## Yorkshire Water 2024
Environment Act -STORM OVERFLOW REGULATORY ANNUAL RETURN 2024
Unique ID | Water Company Name | Permit Status | Site Name (EA Consents Database) | Site Name | EA Permit Reference (EA Consents Database) | WaSC Supplementary Permit Ref. [optional] | Activity Reference on Permit (if >1 discharge on permit) | Storm Discharge Asset Type | Outlet Discharge NGR (EA Consents Database) | Easting of Discharge | Northing of Discharge | WFD Waterbody ID (Cycle 3) (discharge outlet) | WFD Waterbody Catchment Name (Cycle 3) (discharge outlet) | Waterbody Type | Operational catchment ID | Operational catchment name | Management Catchment ID | Management Catchment Name | Receiving Water / Environment (common name) (EA Consents Database) | Shellfish Water (only populate for storm overflow with a Shellfish Water EDM requirement) | Bathing Water (only populate for storm overflow with a Bathing Water EDM requirement) | Treatment Method (over & above Storm Tank settlement / screening) | Total Duration (hrs) all discharges prior to processing through 12-24h count method | Counted discharges using 12-24h count method | Long-term average discharge count | Data start - calendar year | EDM Operation - % of reporting period EDM operational | EDM Operation - Reporting % - Primary Reason <90% | EDM Operation - Action taken / planned - Status & timeframe | High Spill Frequency - Operational Review - Single year reason | High Spill Frequency - Operational Review - Long-term average reason | Investigation activity for the reporting period | Improvement activity for the reporting period | UWWTR (SOAF) investigation status | Old format Unique ID - pre-2024 Annual Return
YWS00001 | Yorkshire Water | Live | PUDSEY VALLEY ROAD CSO | PUDSEY VALLEY ROAD/CSO | 1008 | 1008 | A1 | SO on sewer network | SE2360032653 | 423600 | 432653 | GB104027062830 | Low/Wortley/Pudsey Bks | River | 3265 | Lower Aire | 3001 | Aire and Calder | TRIBUTARY OF PUDSEY BECK | Not Applicable | Not Applicable | Not Applicable | 0:45 | 3 | 3 | 2020 | 55.57 | Comms failure / issue | Scheduled | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00001
YWS00002 | Yorkshire Water | Live | ROCHESTER ROAD SEWAGE PUMPING STN | ROCHESTER ROAD/CSO | 1019 | 1019 | A2 | Storm discharge at pumping station | SK2936086400 | 429360 | 386400 | GB104027057340 | Rivelin from Source to River Loxley | River | 3490 | Upper Don | 3029 | Don and Rother | UNNAMED TRIB OF BLACK BROOK | Not Applicable | Not Applicable | Not Applicable | 45:45 | 13 | 14.8 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00002
YWS00003 | Yorkshire Water | Live | HALTON DEAN TIP CSO | HALTON DEAN TIP/CSO | 1032 | 1032 | A1 | SO on sewer network | SE3512034140 | 435130 | 434148 | GB104027062880 | Wyke Beck from Source to River Aire | River | 3265 | Lower Aire | 3001 | Aire and Calder | DEAN DYKE | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00003
YWS00004 | Yorkshire Water | Live | LUCY AVENUE CSO | LUCY AVENUE/CSO | 1033 | 1033 | A1 | SO on sewer network | SE3446033870 | 434468 | 433872 | GB104027062880 | Wyke Beck from Source to River Aire | River | 3265 | Lower Aire | 3001 | Aire and Calder | DEANE DIKE | Not Applicable | Not Applicable | Not Applicable | 6:15 | 10 | 3.2 | 2020 | 99.93 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00004
YWS00005 | Yorkshire Water | Live | SOWERBY NEW ROAD CSO | SOWERBY NEW ROAD/CSO | 1061 | 1061 | A1 | SO on sewer network | SE0548723826 | 405487 | 423826 | GB104027062641 | Calder from Colden Water to Ryburn Confluence | River | 3310 | Middle Calder | 3001 | Aire and Calder | RIVER CALDER | Not Applicable | Not Applicable | Not Applicable | 95:36 | 74 | 74 | 2020 | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | Operational investigation completed | No improvement action in reporting period | SOAF investigation completed - No work required | YWS00005
YWS00006 | Yorkshire Water | Live | DEVONSHIRE CRESCENT CSO | DEVONSHIRE CRESCENT/CSO | 1068 | 1068 | A1 | SO on sewer network | SE3255738196 | 432557 | 438196 | GB104027062880 | Wyke Beck from Source to River Aire | River | 3265 | Lower Aire | 3001 | Aire and Calder | FOX WOOD BECK | Not Applicable | Not Applicable | Not Applicable | 12:10 | 18 | 15.8 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00006
YWS00007 | Yorkshire Water | Live | POCKLINGTON SCHOOL CSO | WEST GREEN/CSO | 1088 | 1088 | 1 | SO on sewer network | SE8005048660 | 480055 | 448662 | GB104027063480 | Pocklington Beck from Source to Bielby beck | River | 3271 | Lower Derwent Yorkshire | 3027 | Derwent Humber | TRIB OF DERWENT | Not Applicable | Not Applicable | Not Applicable | 2:00 | 2 | 1.6 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00007
YWS00008 | Yorkshire Water | Live | ADEL CHURCH LANE CSO | ADEL CHURCH LANE/CSO | 1108 | 1108 | A1 | SO on sewer network | SE2763540686 | 427635 | 440686 | GB104027062900 | Meanwood Beck from Source to River Aire | River | 3265 | Lower Aire | 3001 | Aire and Calder | ADEL BECK | Not Applicable | Not Applicable | Not Applicable | 176:15 | 46 | 43 | 2020 | 99.99 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00008
YWS00009 | Yorkshire Water | Live | RUGBY FIELD RICHMOND CSO | RUGBY FIELD RICHMOND/CSO | 1114 | 1114 | A1 | SO on sewer network | NZ1787800815 | 417878 | 500815 | GB104027069122 | Swale from Clapgate Beck to Bedale Beck | River | 3317 | Middle Swale | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER SWALE | Not Applicable | Not Applicable | Not Applicable | 125:00 | 63 | 59 | 2020 | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00009
YWS00011 | Yorkshire Water | Live | CAWTHORNE WWTW | CAWTHORNE/STW/3XDWF OVERFLOW | 112 | 112 | A2 | Storm tank at WwTW | SE2829008110 | 428290 | 408110 | GB104027063150 | Cawthorne Dyke from Source to River Dearne | River | 3125 | Dearne | 3029 | Don and Rother | TANYARD BECK | Not Applicable | Not Applicable | Not Applicable | 932:00 | 133 | 92.4 | 2020 | 99.94 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation ongoing | Operational improvement ongoing | SOAF investigation ongoing | YWS00011
YWS00012 | Yorkshire Water | Live | BACK HEIGHTS SPS | BACK HEIGHTS/CSO | 1125 | 1125 | 1 | Storm discharge at pumping station | SE0925033950 | 409250 | 433950 | GB104027062861 | Clayton Beck (Source to Bradford Bk) | River | 3307 | Middle Aire | 3001 | Aire and Calder | PITTY BECK (VIA SW SEWER) | Not Applicable | Not Applicable | Not Applicable | 0:45 | 1 | 1.2 | 2020 | 73.9 | Sensor failure / issue | Resolved - May | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00012
YWS00013 | Yorkshire Water | Live | GLENOIT MILL CSO | GLENOIT MILL/CSO | 1126 | 1126 | A1 | SO on sewer network | SE3725228962 | 437252 | 428962 | GB104027063032 | Aire from Gill Beck (Baildon) to River Calder | River | 3265 | Lower Aire | 3001 | Aire and Calder | TRIBUTARY OF THE RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 32:45 | 17 | 17 | 2020 | 94.13 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00013
YWS00014 | Yorkshire Water | Live | CRIDLING STUBBS WWTW | CRIDLING STUBBS/STW | 1158 | 1158 | 2 | Storm tank at WwTW | SE5221021300 | 452210 | 421300 | GB104027063370 | Womersley Beck from Source to Blowell Drain | River | 3272 | Lower Don | 3029 | Don and Rother | BLOWELL DRAIN | Not Applicable | Not Applicable | Not Applicable | 442:45 | 47 | 34.6 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | Operational investigation ongoing | Operational improvement ongoing | No SOAF investigation required | YWS00014
YWS00015 | Yorkshire Water | Live | INGLEBY ARNCLIFFE STW | INGLEBY ARNCLIFFE/STW/3XDWF OVERFLOW | COPA/1207 | 1207 | A2 | Inlet SO at WwTW | NZ4510000900 | 445300 | 500800 | GB104027069550 | Wiske from Source to Trenholme Stell | River | 3541 | Wiske | 3088 | Swale, Ure, Nidd and Upper Ouse | CARR BECK | Not Applicable | Not Applicable | Not Applicable | 194:30 | 86 | 40.2 | 2020 | 80.42 | Comms failure / issue | Resolved - Apr | Performance - Asset configuration (e.g. PS/rising main/storm tanks) | Performance - Asset configuration (e.g. PS/rising main/storm tanks) | UWWTR investigation ongoing, Operational investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00015
YWS00016 | Yorkshire Water | Live | HEMINGBROUGH WPC WORKS | HEMINGBROUGH NORTH/CSO | 1232 | 1232 | 1 | Storm discharge at pumping station | SE6700030000 | 467307 | 431102 | GB104027064270 | Ouse from R Wharfe to Upper Humber | River | 3280 | Lower Ouse Yorkshire | 3115 | Wharfe and Lower Ouse | OLD COURSE OF RIVER OUSE | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 1.6 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00016
YWS00017 | Yorkshire Water | Live | MONKBRIDGE ROAD CSO | MONKBRIDGE ROAD/CSO | 1281 | 1281 | A1 | SO on sewer network | SE2844036830 | 428440 | 436838 | GB104027062900 | Meanwood Beck from Source to River Aire | River | 3265 | Lower Aire | 3001 | Aire and Calder | MEANWOOD BECK | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0 | 2020 | 94.88 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00017
YWS00018 | Yorkshire Water | Live | TRAFALGAR STREET CSO | TRAFALGAR STREET/CSO | 1282 | 1282 | A1 | SO on sewer network | SE6022750108 | 460227 | 450108 | GB104027069593 | Ouse from River Nidd to Stillingfleet Beck | River | 3499 | Upper Ouse Yorkshire | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER OUSE | Not Applicable | Not Applicable | Not Applicable | 689:08 | 50 | 112 | 2020 | 100 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement ongoing | SOAF investigation ongoing | YWS00018
YWS00019 | Yorkshire Water | Live | THORPE ROAD CSO | THORPE ROAD/CSO | 1298 | 1298 | A1 | SO on sewer network | SE3099027457 | 430990 | 427457 | GB104027062680 | Oulton Beck from Source to River Aire | River | 3265 | Lower Aire | 3001 | Aire and Calder | THROSTLE CARR BECK | Not Applicable | Not Applicable | Not Applicable | 1:00 | 3 | 4.2 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00019
YWS00020 | Yorkshire Water | Live | HUNSWORTH LANE NO 2 CSO | HUNSWORTH LANE/NO 2 CSO | 1323 | 1323 | A1 | SO on sewer network | SE1941928477 | 419419 | 428477 | GB104027062710 | Spen Beck from Source to River Calder | River | 3268 | Lower Calder | 3001 | Aire and Calder | HUNSWORTH UPPER LANE BECK | Not Applicable | Not Applicable | Not Applicable | 100:00 | 30 | 17.8 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00020
YWS00021 | Yorkshire Water | Live | BARDSEY CSO | BARDSEY/CSO | 1364 | 1364 | A1 | SO on sewer network | SE3653643052 | 436536 | 443052 | GB104027063970 | Collingham Bk Catchment (trib of Wharfe) | River | 3318 | Middle Wharfe and Washburn | 3115 | Wharfe and Lower Ouse | GILL BECK | Not Applicable | Not Applicable | Not Applicable | 9:30 | 7 | 3.8 | 2020 | 99.93 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00021
YWS00022 | Yorkshire Water | Live | HALL INGS CSO | HALL INGS/CSO | 1374 | 1374 | A1 | SO on sewer network | SE1638032810 | 416380 | 432810 | GB104027062862 | Bradford Beck (Clayton Bk to R Aire) | River | 3307 | Middle Aire | 3001 | Aire and Calder | BOWLING BECK | Not Applicable | Not Applicable | Not Applicable | 0:15 | 1 | 0.6 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00022
YWS00023 | Yorkshire Water | Live | DALTON ICI SOUTH CSO | DALTON ICI SOUTH/CSO | 1375 | 1375 | A1 | SO on sewer network | SE1704217595 | 417042 | 417595 | GB104027063340 | Fenay beck from Source to River Colne | River | 3097 | Colne and Holme | 3001 | Aire and Calder | LEES HD BECK TRIB COLNE/CALDER | Not Applicable | Not Applicable | Not Applicable | 115:00 | 17 | 28 | 2020 | 74.43 | Sensor failure / issue | Resolved - Apr | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00023
YWS00024 | Yorkshire Water | Live | HOLME LANE 313 CSO | HOLME LANE 313/CSO | 1420 | 1420 | A1 | SO on sewer network | SE1967031250 | 419670 | 431250 | GB104027062830 | Low/Wortley/Pudsey Bks | River | 3265 | Lower Aire | 3001 | Aire and Calder | HOLME BECK | Not Applicable | Not Applicable | Not Applicable | 8:00 | 11 | 11.6 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00024
YWS00025 | Yorkshire Water | Live | BARSEY GREEN STW | BARSEY GREEN/STW | 1433 | 1433 | 2 | Storm tank at WwTW | SE0640020600 | 406400 | 420600 | GB104027062570 | Black Brook from Source to River Calder | River | 3310 | Middle Calder | 3001 | Aire and Calder | BARSEY CLOUGH | Not Applicable | Not Applicable | Not Applicable | 180:00 | 31 | 23.8 | 2020 | 99.82 |  |  | High spill threshold not met | High spill threshold not met | Operational investigation completed | No improvement action in reporting period | No SOAF investigation required | YWS00025
YWS00026 | Yorkshire Water | Permit Application Submitted | TBC When Permit Issued | BLACKBURN/CSO | Permit applied for | 1434 | TBC | SO on sewer network | SK3889092820 | 438890 | 392820 | GB104027057440 | Blackburn Brook from Source to River Don | River | 3312 | Middle Don | 3029 | Don and Rother | BLACKBURN BROOK | Not Applicable | Not Applicable | Not Applicable | 28:45 | 24 | 51.25 | 2020 | 99.64 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement completed | SOAF investigation ongoing | YWS00026
YWS00028 | Yorkshire Water | Live | DALTON WAKEFIELD ROAD CSO | DALTON WAKEFIELD ROAD/CSO | 1485 | 1485 | A1 | SO on sewer network | SE1741617069 | 417416 | 417069 | GB104027063340 | Fenay beck from Source to River Colne | River | 3097 | Colne and Holme | 3001 | Aire and Calder | ROUND WOOD BECK | Not Applicable | Not Applicable | Not Applicable | 37:00 | 18 | 4 | 2020 | 99.82 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00028
YWS00029 | Yorkshire Water | Live | ROUNDWOOD GLEN NO 2 CSO | ROUNDWOOD GLEN/NO 2 CSO | 1501 | 1501 | A1 | SO on sewer network | SE1941937002 | 419419 | 437002 | GB104027063032 | Aire from Gill Beck (Baildon) to River Calder | River | 3265 | Lower Aire | 3001 | Aire and Calder | CARR BECK | Not Applicable | Not Applicable | Not Applicable | 240:00 | 80 | 38.8 | 2020 | 97.79 |  |  | Not asset maintenance - Hydraulic capacity | High spill threshold not met | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS00029
YWS00030 | Yorkshire Water | Live | EAST BIERLEY NO2 CSO | EAST BIERLEY/NO 2 CSO | 1503 | 1503 | A1 | SO on sewer network | SE2015028730 | 420154 | 428721 | GB104027062710 | Spen Beck from Source to River Calder | River | 3268 | Lower Calder | 3001 | Aire and Calder | LODGE BECK | Not Applicable | Not Applicable | Not Applicable | 59:00 | 30 | 27 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00030
YWS00031 | Yorkshire Water | Live | WEST HANDLEY CSO | WEST HANDLEY/NO 2 CSO | 1549 | 1549 | A1 | SO on sewer network | SK3790577250 | 439705 | 377250 | GB104027057771 | Rother, Spittal Brook to Doe Lea | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | TRIBUTARY OF THE RIVER ROTHER | Not Applicable | Not Applicable | Not Applicable | 64:15 | 7 | 9.8 | 2020 | 34.64 | Comms failure / issue | Resolved - January after reporting year | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00031
YWS00032 | Yorkshire Water | Live | VICAR ROAD CSO | VICAR ROAD DARFIELD/CSO | 1550 | 1550 | 1 | SO on sewer network | SE4178003820 | 441794 | 403820 | GB104027057510 | Dove from Source to River Dearne | River | 3125 | Dearne | 3029 | Don and Rother | DOVE | Not Applicable | Not Applicable | Not Applicable | 15:45 | 13 | 32.6 | 2020 | 99.88 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00032
YWS00033 | Yorkshire Water | Live | WEATHERBY HIGH STREET CSO | WETHERBY HIGH STREET/CSO | 1553 | 1553 | A1 | SO on sewer network | SE4045447994 | 440454 | 447994 | GB104027064255 | Wharfe from Collingham Beck to Tadcaster Weir | River | 3287 | Lower Wharfe | 3115 | Wharfe and Lower Ouse | RIVER WHARFE | Not Applicable | Wharfe at Wilderness Carpark | Not Applicable | 0:15 | 1 | 0.4 | 2020 | 99.58 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00033
YWS00034 | Yorkshire Water | Live | HOWDEN STW | HOWDEN/STW | 1569 | 1569 | 2 | Inlet SO at WwTW | SE7542026790 | 475420 | 426790 | GB530402609203 | HUMBER UPPER | Transitional Water | 3228 | Humber Estuary TraC | 3040 | Humber TraC | RIVER OUSE (TIDAL) | Not Applicable | Not Applicable | Not Applicable | 828:00 | 120 | 89 | 2020 | 99.96 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement completed | SOAF investigation ongoing | YWS00034
YWS00035 | Yorkshire Water | Live | LOWER MILL CSO | LOWER MILL/CSO | 1587 | 1587 | A1 | SO on sewer network | SD9924028786 | 399240 | 428786 | GB104027062731 | Hebden Water from Widdop Beck to R Calder | River | 3487 | Upper Calder | 3001 | Aire and Calder | HEBDEN WATER | Not Applicable | Not Applicable | Not Applicable | 4:00 | 5 | 3.8 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00035
YWS00036 | Yorkshire Water | Live | ABBEYDALE MOUNT CSO | ABBEYDALE MOUNT/CSO | 1588 | 1588 | A1 | SO on sewer network | SE2533036380 | 425330 | 436380 | GB104027063032 | Aire from Gill Beck (Baildon) to River Calder | River | 3265 | Lower Aire | 3001 | Aire and Calder | RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 245:00 | 81 | 64.2 | 2020 | 100 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation completed | No improvement action in reporting period | SOAF investigation completed - No work required | YWS00036
YWS00037 | Yorkshire Water | Permit Application Submitted | TBC When Permit Issued | WEST BURTON/STW | Permit applied for | 1605 | TBC | Inlet SO at WwTW | SE0130087500 | 401400 | 487700 | GB104027069360 | Bishopdale Bk from Source to R Ure | River | 3505 | Upper Ure | 3088 | Swale, Ure, Nidd and Upper Ouse | BISHOPDALE BECK | Not Applicable | Not Applicable | Not Applicable | 721:15 | 129 | 113.4 | 2020 | 100 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation ongoing | Operational improvement ongoing | SOAF investigation ongoing | YWS00037
YWS00038 | Yorkshire Water | Live | HUNLOKE ROAD CSO | HUNLOKE ROAD/CSO | 1606 | 1606 | A1 | SO on sewer network | SK4303666393 | 443036 | 366393 | GB104027057640 | Spital/Calow/Muster Brook | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | TRIB OF MUSTER BROOK | Not Applicable | Not Applicable | Not Applicable | 7:30 | 6 | 4.6 | 2020 | 72.85 | Installation set-up/design issue | Resolved - Apr | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00038
YWS00039 | Yorkshire Water | Live | CROW EDGE STW | CROW EDGE/STW | 1614 | 1614 | A2 | Storm tank at WwTW | SE1935403986 | 419350 | 403980 | GB104027057500 | Don from Source to Scout Dyke | River | 3490 | Upper Don | 3029 | Don and Rother | SLEDBROOK DYKE | Not Applicable | Not Applicable | Not Applicable | 285:30 | 47 | 42.8 | 2020 | 99.94 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS00039
YWS00041 | Yorkshire Water | Live | SHEEPSCAR LANE NO 2 CSO | SHEEPSCAR LANE/NO 2 CSO | 1645 | 1645 | A1 | SO on sewer network | SE3068634701 | 430686 | 434701 | GB104027062900 | Meanwood Beck from Source to River Aire | River | 3265 | Lower Aire | 3001 | Aire and Calder | SHEEPSCAR BECK | Not Applicable | Not Applicable | Not Applicable | 139:30 | 48 | 40 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00041
YWS00042 | Yorkshire Water | Live | EGGBOROUGH STW | EGGBOROUGH/STW | 1653 | 1653 | A2 | Storm tank at WwTW | SE5857524533 | 458575 | 424533 | GB104027062760 | Aire from River Calder to River Ouse | River | 3265 | Lower Aire | 3001 | Aire and Calder | INGS AND TETHERINGS DRAIN | Not Applicable | Not Applicable | Not Applicable | 116:45 | 15 | 25.4 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00042
YWS00043 | Yorkshire Water | Permit Application Submitted | TBC When Permit Issued | BOTTON/STW | Permit applied for | 1655 | TBC | Inlet SO at WwTW | NZ6930004400 | 469300 | 504400 | GB104027068110 | Danby Beck catchement (trib of Esk) | River | 3177 | Esk | 3037 | Esk and Coast | DANBY BECK | Not Applicable | Not Applicable | Not Applicable | 297:15 | 44 | 27.8 | 2020 | 99.82 |  |  | High spill threshold not met | High spill threshold not met | Operational investigation ongoing | No improvement action in reporting period | No SOAF investigation required | YWS00043
YWS00044 | Yorkshire Water | Permit Application Submitted | TBC When Permit Issued | COMMONDALE/STW | Permit applied for | 1656 | TBC | Inlet SO at WwTW | NZ6630010300 | 466300 | 510300 | GB104027068170 | Sleddale Beck from Source to River Esk | River | 3177 | Esk | 3037 | Esk and Coast | COMMONDALE BECK | Not Applicable | Not Applicable | Not Applicable | 5:00 | 8 | 4 | 2023 | 99.58 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00044
YWS00045 | Yorkshire Water | Permit Application Submitted | TBC When Permit Issued | MICKLEBY/STW | Permit applied for | 1659 | TBC | Inlet SO at WwTW | NZ8070012800 | 480900 | 512500 | GB104027068720 | Sandsend Beck/Mickley Bk from Source to North Sea | River | 3390 | Sandsend and Staithes | 3037 | Esk and Coast | TRIB OF MICKELBY BECK | Not Applicable | Not Applicable | Not Applicable | 113:45 | 36 | 33.4 | 2020 | 82.1 | Comms failure / issue | Resolved - Mar | High spill threshold not met | High spill threshold not met | Operational investigation ongoing | No improvement action in reporting period | No SOAF investigation required | YWS00045
YWS00046 | Yorkshire Water | Permit Application Submitted | TBC When Permit Issued | THORALBY/STW | Permit applied for | 1685 | TBC | Inlet SO at WwTW | SE0030086700 | 400400 | 486600 | GB104027069360 | Bishopdale Bk from Source to R Ure | River | 3505 | Upper Ure | 3088 | Swale, Ure, Nidd and Upper Ouse | BISHOPDALE BECK | Not Applicable | Not Applicable | Not Applicable | 384:45 | 59 | 79 | 2020 | 97.47 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00046
YWS00047 | Yorkshire Water | Live | BARLOW WWTW | BARLOW/STW | 1694 | 1694 | A2 | Inlet SO at WwTW | SK3386075680 | 433860 | 375679 | GB104027057700 | Barlow Brook from Source to River Drone | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | BARLOW BROOK | Not Applicable | Not Applicable | Not Applicable | 195:15 | 53 | 56.4 | 2020 | 99.99 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement ongoing | SOAF investigation ongoing | YWS00047
YWS00049 | Yorkshire Water | Live | PROPOSED SSO NO 14 MANHOLE | FIELD 0064 DARLEY RD/CSO | 1716 | 1716 | 1 | SO on sewer network | SE2530057800 | 428598 | 450500 | GB104027063741 | Crimple Beck from Source to Park Beck | River | 3308 | Middle and Lower Nidd | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER NIDD | Not Applicable | Not Applicable | Not Applicable | 1:00 | 2 | 1 | 2020 | 37.97 | Comms failure / issue | Scheduled | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00049
YWS00050 | Yorkshire Water | Live | COWICK & SNAITH CSO'S | EAST COWICK/CSO | 1732(T) | 1732(T) | 2 | Storm discharge at pumping station | SE6622021000 | 466220 | 421000 | GB104027064243 | Don from Mill Dyke to River Ouse | River | 3272 | Lower Don | 3029 | Don and Rother | AIRE | Not Applicable | Not Applicable | Not Applicable | 16:00 | 14 | 8.8 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00050
YWS00051 | Yorkshire Water | Live | COWICK & SNAITH CSO'S | WEST COWICK/CSO | 1732(T) | 1732(T) | 3 | Storm discharge at pumping station | SE6489021520 | 464890 | 421520 | GB104027064243 | Don from Mill Dyke to River Ouse | River | 3272 | Lower Don | 3029 | Don and Rother | AIRE | Not Applicable | Not Applicable | Not Applicable | 202:15 | 53 | 66.6 | 2020 | 99.99 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement ongoing | SOAF investigation ongoing | YWS00051
YWS00052 | Yorkshire Water | Live | SNAITH MARSH SEWAGE PUMPING STATION | SNAITH MARSH/SPS | EPRQB3697RY | EPR/QB3697RY | A1 | Storm discharge at pumping station | SE6432922472 | 464329 | 422472 | GB104027062760 | Aire from River Calder to River Ouse | River | 3265 | Lower Aire | 3001 | Aire and Calder | TRIBUTARY OF RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 84:45 | 51 | 14.6 | 2020 | 99.94 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00052
YWS00053 | Yorkshire Water | Live | COWICK & SNAITH CSO'S | SNAITH MARSH/CSO | 1732(T) | 1732(T) | 6 | SO on sewer network | SE6438022340 | 464380 | 422340 | GB104027062760 | Aire from River Calder to River Ouse | River | 3265 | Lower Aire | 3001 | Aire and Calder | AIRE | Not Applicable | Not Applicable | Not Applicable | 19:00 | 16 | 16 | 2020 | 99.98 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00053
YWS00054 | Yorkshire Water | Live | SNAITH SOUTH PUMPING STATION CSO | SNAITH SOUTH/CSO | EPRQB3697NW | EPR/QB3697NW | A1 | Storm discharge at pumping station | SE6353522349 | 463535 | 422349 | GB104027062760 | Aire from River Calder to River Ouse | River | 3265 | Lower Aire | 3001 | Aire and Calder | TIDAL RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 4:00 | 2 | 0.6 | 2020 | 99.96 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00054
YWS00055 | Yorkshire Water | Live | GOWDALL PUMPING STATION CSO | GOWDALL/CSO | EPRQB3697VB | EPR/QB3697VB | A1 | Storm discharge at pumping station | SE6254522713 | 462545 | 422713 | GB104027062760 | Aire from River Calder to River Ouse | River | 3265 | Lower Aire | 3001 | Aire and Calder | TIDAL RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 130:30 | 58 | 16.2 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS00055
YWS00056 | Yorkshire Water | Live | BROOMHILL EMLEY CSO | BROOMHALL EMLEY/CSO | 1811 | 1811 | A1 | SO on sewer network | SE2537213220 | 425372 | 413220 | GB104027063310 | Bentley Brook from Source to River Dearne | River | 3125 | Dearne | 3029 | Don and Rother | LITTLE DIKE | Not Applicable | Not Applicable | Not Applicable | 132:00 | 32 | 28.8 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00056
YWS00057 | Yorkshire Water | Live | PORTOBELLO SPS | PORTOBELLO/CSO | 1814 | 1814 | A1 | Storm discharge at pumping station | SE3329018420 | 433290 | 418420 | GB104027062530 | Owler Beck from Source to River Calder | River | 3268 | Lower Calder | 3001 | Aire and Calder | PUGNEY'S DRAIN | Not Applicable | Not Applicable | Not Applicable | 205:00 | 33 | 16.6 | 2020 | 99.89 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00057
YWS00058 | Yorkshire Water | Live | YWS UNKNOWN SITES DEFAULT | LEA ROAD MANSE/CSO | 1828 | 1828 | 1 | SO on sewer network | SE3537078360 | 435371 | 378361 | GB104027057710 | Drone/Whitting from Source to River Rother | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | RIVER ROTHER | Not Applicable | Not Applicable | Not Applicable | 290:30 | 64 | 28.8 | 2020 | 99.72 |  |  | Not asset maintenance - Hydraulic capacity | High spill threshold not met | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS00058
YWS00059 | Yorkshire Water | Live | TEMPLE AVENUE CSO | TEMPLE AVENUE/CSO | 1855 | 1855 | A1 | SO on sewer network | SE3506032680 | 435088 | 432732 | GB104027062880 | Wyke Beck from Source to River Aire | River | 3265 | Lower Aire | 3001 | Aire and Calder | TRIB OF WYKE BECK | Not Applicable | Not Applicable | Not Applicable | 47:45 | 29 | 34.8 | 2020 | 99.76 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00059
YWS00060 | Yorkshire Water | Live | STOCK HILL FOLD NO 2 CSO | STOCK HILL FOLD/NO 2 CSO | 1862 | 1862 | A1 | SO on sewer network | SE1886337573 | 418863 | 437573 | GB104027063032 | Aire from Gill Beck (Baildon) to River Calder | River | 3265 | Lower Aire | 3001 | Aire and Calder | HAIGH BECK | Not Applicable | Not Applicable | Not Applicable | 159:15 | 55 | 49.2 | 2020 | 99.99 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00060
YWS00061 | Yorkshire Water | Live | DRONFIELD WWTW | DRONFIELD/STW | 1863 | 1863 | A2 | Storm tank at WwTW | SK3667677888 | 436750 | 377820 | GB104027057710 | Drone/Whitting from Source to River Rother | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | RIVER DRONE | Not Applicable | Not Applicable | Not Applicable | 244:43 | 43 | 49.2 | 2020 | 99.92 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00061
YWS00062 | Yorkshire Water | Live | BOLSOVER WWTW | BOLSOVER/STW | 1866 | 1866 | A2 | Storm tank at WwTW | SK4591070150 | 445910 | 370150 | GB104027057290 | Doe Lea from Source to Hawke Brook | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | RIVER DOE LEA | Not Applicable | Not Applicable | Not Applicable | 785:45 | 91 | 81.2 | 2020 | 99.66 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS00062
YWS00063 | Yorkshire Water | Live | BOLSOVER WWTW | BOLSOVER/STW | 1866 | 1866 | A3 | Inlet SO at WwTW | SK4591070150 | 445910 | 370150 | GB104027057290 | Doe Lea from Source to Hawke Brook | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | RIVER DOE LEA | Not Applicable | Not Applicable | Not Applicable | 160:45 | 51 | 55.4 | 2020 | 99.65 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00063
YWS00064 | Yorkshire Water | Live | WIDE LANE WOODLANDS NO 2 CSO | WIDE LANE WOODLANDS/2 CSO | 187 | 187 | A1 | SO on sewer network | SE2874227950 | 428742 | 427950 | GB104027062750 | Milshaw Beck from Source to Low/Wortley/Pudsey Bks | River | 3265 | Lower Aire | 3001 | Aire and Calder | MILL SHAW BECK | Not Applicable | Not Applicable | Not Applicable | 206:15 | 68 | 77 | 2020 | 99.85 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS00064
YWS00065 | Yorkshire Water | Live | SLAYLEIGH LANE CSO | SLAYLEIGH LANE/CSO | 1885 | 1885 | A1 | SO on sewer network | SK3083285104 | 430832 | 385104 | GB104027057760 | Porter from Source to River Sheaf | River | 3312 | Middle Don | 3029 | Don and Rother | PORTER BROOK | Not Applicable | Not Applicable | Not Applicable | 52:45 | 31 | 34.6 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00065
YWS00067 | Yorkshire Water | Live | BURN ROAD CSO | BURN ROAD/CSO | 1896 | 1896 | A1 | SO on sewer network | SE1203018890 | 412003 | 418895 | GB104027062550 | Colne from River Holme to River Calder | River | 3097 | Colne and Holme | 3001 | Aire and Calder | GRIMESCAR DIKE | Not Applicable | Not Applicable | Not Applicable | 48:45 | 30 | 25.2 | 2020 | 99.93 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00067
YWS00068 | Yorkshire Water | Live | JACK HILL CSO | JACK BRIDGE WEST/CSO | 1897 | 1897 | 1 | SO on sewer network | SE1520017530 | 415207 | 417533 | GB104027062550 | Colne from River Holme to River Calder | River | 3097 | Colne and Holme | 3001 | Aire and Calder | COLNE | Not Applicable | Not Applicable | Not Applicable | 8:15 | 14 | 13.2 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00068
YWS00069 | Yorkshire Water | Live | BEN SHAWS CSO | BEN SHAWS/CSO | 1898 | 1898 | A1 | SO on sewer network | SE1520717533 | 415207 | 417533 | GB104027062550 | Colne from River Holme to River Calder | River | 3097 | Colne and Holme | 3001 | Aire and Calder | RIVER COLNE | Not Applicable | Not Applicable | Not Applicable | 69:15 | 37 | 26.6 | 2020 | 95.58 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00069
YWS00070 | Yorkshire Water | Live | HORBURY ROAD M1 CSO | HORBURY ROAD M1/CSO | 1921 | 1921 | A1 | SO on sewer network | SE3056118796 | 430561 | 418796 | GB104027062631 | Calder from River Colne to River Chald | River | 3268 | Lower Calder | 3001 | Aire and Calder | LUPSET BECK | Not Applicable | Not Applicable | Not Applicable | 1:45 | 4 | 3.4 | 2020 | 75.28 | Comms failure / issue | Scheduled | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00070
YWS00071 | Yorkshire Water | Live | SNAITH STW | SNAITH/STW | 1943 | 1943 | A2 | Storm tank at WwTW | SE6353022350 | 463530 | 422350 | GB104027062760 | Aire from River Calder to River Ouse | River | 3265 | Lower Aire | 3001 | Aire and Calder | RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 12:15 | 2 | 2 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00071
YWS00072 | Yorkshire Water | Live | ELMETE LANE CSO | ELMETE LANE/NO 2 CSO | 1944 | 1944 | 1 | SO on sewer network | SE3371036940 | 433717 | 436940 | GB104027062880 | Wyke Beck from Source to River Aire | River | 3265 | Lower Aire | 3001 | Aire and Calder | WYKE BECK | Not Applicable | Not Applicable | Not Applicable | 59:30 | 16 | 15.4 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00072
YWS00073 | Yorkshire Water | Live | BENTLEY SEWAGE TREATMENT WORKS | BENTLEY/STW | 1978 | 1978 | A2 | Storm tank at WwTW | SE5713005720 | 457130 | 405720 | GB104027057541 | Bentley Mill Stream | River | 3272 | Lower Don | 3029 | Don and Rother | BENTLEY MILL STREAM | Not Applicable | Not Applicable | Not Applicable | 300:05 | 82 | 27 | 2020 | 99.9 |  |  | Not asset maintenance - Hydraulic capacity | High spill threshold not met | UWWTR investigation ongoing, Operational investigation ongoing | Operational improvement ongoing | SOAF investigation ongoing | YWS00073
YWS00074 | Yorkshire Water | Live | ST PETERS STREET CSO | ST PETERS STREET/CSO | 1997 | 1997 | A1 | SO on sewer network | SE7908271056 | 479082 | 471056 | GB104027068313 | Derwent from River Rye to Kirkham | River | 3311 | Middle Derwent Yorkshire | 3027 | Derwent Humber | MILL BECK | Not Applicable | Not Applicable | Not Applicable | 6:42 | 11 | 28.2 | 2020 | 99.98 |  |  | High spill threshold not met | High spill threshold not met | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00074
YWS00075 | Yorkshire Water | Live | SPRINGVALE CSO | SPRINGVALE/CSO | 2002 | 2002 | A1 | SO on sewer network | SE2574403213 | 425744 | 403213 | GB104027057490 | Don from Scout Dyke to the Little Don | River | 3490 | Upper Don | 3029 | Don and Rother | RIVER DON | Not Applicable | Not Applicable | Not Applicable | 303:45 | 52 | 55 | 2020 | 94.13 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | No investigation activity in reporting period | No improvement action in reporting period | SOAF investigation completed - No work required | YWS00075
YWS00076 | Yorkshire Water | Live | DARTON STW | DARTON/STW/3XDWF OVERFLOW | 2026 | 2026 | A2 | Storm tank at WwTW | SE3251008970 | 432510 | 408970 | GB104027063171 | Dearne from Cawthorne Dyke to Lundwood STW | River | 3125 | Dearne | 3029 | Don and Rother | RIVER DEARNE | Not Applicable | Not Applicable | Not Applicable | 367:15 | 53 | 68.8 | 2020 | 99.55 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation ongoing | Operational improvement ongoing | SOAF investigation ongoing | YWS00076
YWS00077 | Yorkshire Water | Live | SOWGATE LANE CSO | SOWGATE LANE/CSO | 2060 | 2060 | A2 | Storm discharge at pumping station | SE4718022950 | 447180 | 422950 | GB104027062760 | Aire from River Calder to River Ouse | River | 3265 | Lower Aire | 3001 | Aire and Calder | WASH DIKE | Not Applicable | Not Applicable | Not Applicable | 587:30 | 61 | 59.2 | 2020 | 99.97 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS00077
YWS00078 | Yorkshire Water | Live | SOWGATE LANE CSO | SOWGATE LANE/CSO | 2060 | 2060 | A3 | Storm discharge at pumping station | SE4718022950 | 447140 | 422920 | GB104027062760 | Aire from River Calder to River Ouse | River | 3265 | Lower Aire | 3001 | Aire and Calder | WASH DIKE | Not Applicable | Not Applicable | Not Applicable | 233:30 | 42 | 45.4 | 2020 | 99.97 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS00078
YWS00079 | Yorkshire Water | Live | RED LION A58 CSO | RED LION A58/CSO | 2068 | 2068 | A1 | SO on sewer network | SE1469026050 | 414690 | 426050 | GB104027062700 | Clifton Beck from Source to River Calder | River | 3310 | Middle Calder | 3001 | Aire and Calder | WYKE BECK | Not Applicable | Not Applicable | Not Applicable | 181:00 | 60 | 37.6 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00079
YWS00080 | Yorkshire Water | Live | SHIPTON ROAD SEWAGE PUMPING STATION | SHIPTON ROAD/NO 2 CSO | 2075 | 2075 | A1 | Storm discharge at pumping station | SE5800054400 | 458002 | 454403 | GB104027069593 | Ouse from River Nidd to Stillingfleet Beck | River | 3499 | Upper Ouse Yorkshire | 3088 | Swale, Ure, Nidd and Upper Ouse | BLUE BECK, TRIBUTARY OF OUSE | Not Applicable | Not Applicable | Not Applicable | 26:15 | 10 | 2.4 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00080
YWS00081 | Yorkshire Water | Live | LONG LANE STW | LONG LANE/STW | 2081 | 2081 | 2 | Storm tank at WwTW | SK4368089200 | 443680 | 389200 | GB104027057772 | Rother, Doe Lea to Don | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | RIVER ROTHER | Not Applicable | Not Applicable | Not Applicable | 463:00 | 72 | 35.2 | 2020 | 99.5 |  |  | Not asset maintenance - Hydraulic capacity | High spill threshold not met | UWWTR investigation ongoing, Operational investigation ongoing | Operational improvement ongoing | SOAF investigation ongoing | YWS00081
YWS00082 | Yorkshire Water | Live | BROAD LANE SPS | HOWDEN BROAD LN/CSO | 2086 | 2086 | A1 | Storm discharge at pumping station | SE7514027840 | 475173 | 427897 | Not part of a WFD catchment | Not part of a WFD catchment | River | N/A | N/A | N/A | N/A | HOWDEN DIKE DRAIN | Not Applicable | Not Applicable | Not Applicable | 183:00 | 66 | 86.6 | 2020 | 99.9 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00082
YWS00083 | Yorkshire Water | Live | THORNHILL ROAD CSO | THORNHILL ROAD/CSO | 2094 | 2094 | 1 | SO on sewer network | SE2671017940 | 426174 | 417946 | GB104027062510 | Smithy Brook from Source to River Calder | River | 3268 | Lower Calder | 3001 | Aire and Calder | SMITHY BROOK | Not Applicable | Not Applicable | Not Applicable | 26:00 | 14 | 10.6 | 2020 | 89.96 | Comms failure / issue | Resolved - Feb | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00083
YWS00084 | Yorkshire Water | Live | AMPLEFORTH VILLAGE STW | AMPLEFORTH VILLAGE/STW | 213 | 213 | A2 | Storm tank at WwTW | SE5830077700 | 458300 | 477700 | GB104027068420 | Holbeck from Source to Wath Beck | River | 3387 | Rye | 3027 | Derwent Humber | HOLBECK | Not Applicable | Not Applicable | Not Applicable | 2964:00 | 160 | 148.6 | 2020 | 99.96 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement ongoing | SOAF investigation ongoing | YWS00084
YWS00085 | Yorkshire Water | Live | NORTH FERRIBY STW | NORTH FERRIBY/STW | 2137 | 2137(T) | 2 | Inlet SO at WwTW | SE9913025150 | 499130 | 425150 | GB530402609202 | HUMBER MIDDLE | Transitional Water | 3228 | Humber Estuary TraC | 3040 | Humber TraC | RIVER HUMBER | Not Applicable | Not Applicable | Not Applicable | 669:30 | 126 | 141.4 | 2020 | 100 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS00085
YWS00086 | Yorkshire Water | Live | DANESMOOR WWTW | DANESMOOR/STW | 2138 | 2138 | A2 | Storm tank at WwTW | SK4076063000 | 440760 | 363000 | GB104027052280 | Rother from Source to Redleadmill Brook | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | RIVER ROTHER | Not Applicable | Not Applicable | Not Applicable | 910:00 | 77 | 93.4 | 2020 | 76.34 | Sensor failure / issue | Resolved - Mar | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00086
YWS00087 | Yorkshire Water | Live | DANESMOOR WWTW | DANESMOOR/STW | 2138 | 2138 | A3 | Inlet SO at WwTW | SK4076063000 | 440760 | 363000 | GB104027052280 | Rother from Source to Redleadmill Brook | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | RIVER ROTHER | Not Applicable | Not Applicable | Not Applicable | 89:00 | 37 | 63 | 2020 | 76.33 | Sensor failure / issue | Resolved - Mar | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00087
YWS00088 | Yorkshire Water | Live | SWINTON SEWAGE TREATMENT WORKS | MEXBORO SWINTON/STW | 2160 | 2160 | A2 | Storm tank at WwTW | SK4694099190 | 446940 | 399190 | GB104027057452 | Don from River Rother to River Dearne | River | 3312 | Middle Don | 3029 | Don and Rother | RIVER DON | Not Applicable | Not Applicable | Not Applicable | 1108:53 | 119 | 107.2 | 2020 | 92.33 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS00088
YWS00089 | Yorkshire Water | Live | COPLEY VILLAGE SPS | COPLEY VILLAGE/NO 2 SPS | 2170 | 2170 | A2 | Storm discharge at pumping station | SE0846622376 | 408466 | 422376 | GB104027062642 | Calder from Ryburn Confluence to River Colne | River | 3310 | Middle Calder | 3001 | Aire and Calder | RIVER CALDER | Not Applicable | Not Applicable | Not Applicable | 0:15 | 1 | 1.4 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00089
YWS00090 | Yorkshire Water | Live | DARNALL ROAD CSO | DARNALL ROAD/CSO | 2171 | 2171 | A1 | SO on sewer network | SK3813488975 | 438134 | 388975 | GB104027057412 | Don from River Loxley confl to River Don Works | River | 3312 | Middle Don | 3029 | Don and Rother | KIRKBRIDGE DIKE | Not Applicable | Not Applicable | Not Applicable | 56:00 | 27 | 26.8 | 2020 | 50.6 | Comms failure / issue | Scheduled | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00090
YWS00091 | Yorkshire Water | Live | WATH UPON DEARNE WWTW | WATH ON DEARNE/STW | 2172 | 2172 | 3 | Storm tank at WwTW | SE4449001120 | 444470 | 401120 | GB104027063173 | Dearne Darfield STW to River Don | River | 3125 | Dearne | 3029 | Don and Rother | BROOK DIKE/RIVER DEARNE | Not Applicable | Not Applicable | Not Applicable | 1194:00 | 86 | 58.6 | 2020 | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00091
YWS00092 | Yorkshire Water | Live | HASTILAR ROAD SOUTH CSO | HASTILAR ROAD SOUTH/CSO | 218 | 218 | A1 | SO on sewer network | SK3999884944 | 439998 | 384944 | GB104027057773 | Shire Brook | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | TRIB OF SHIRE BROOK | Not Applicable | Not Applicable | Not Applicable | 11:30 | 16 | 19.8 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00092
YWS00093 | Yorkshire Water | Live | CROFTON STW | CROFTON/STW | 2207 | 2207 | A2 | Storm tank at WwTW | SE3629018470 | 436290 | 418470 | GB104027062560 | Oakenshaw Beck from Source to River Calder | River | 3268 | Lower Calder | 3001 | Aire and Calder | OAKENSHAW BECK | Not Applicable | Not Applicable | Not Applicable | 143:30 | 16 | 44.2 | 2020 | 91.84 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00093
YWS00094 | Yorkshire Water | Live | CROFTON STW | CROFTON/STW | 2207 | 2207 | A3 | Inlet SO at WwTW | SE3629018470 | 436290 | 418470 | GB104027062560 | Oakenshaw Beck from Source to River Calder | River | 3268 | Lower Calder | 3001 | Aire and Calder | OAKENSHAW BECK | Not Applicable | Not Applicable | Not Applicable | 22:00 | 13 | 10.6 | 2020 | 99.45 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00094
YWS00095 | Yorkshire Water | Live | GOOGLE CARR LANE SPS | GOOLE CARR LANE/SPS/6XDWF OVERFLOW | 2213(T) | 2213(T) | A1 | Storm discharge at pumping station | SE7490025630 | 474900 | 425630 | GB530402609203 | HUMBER UPPER | Transitional Water | 3228 | Humber Estuary TraC | 3040 | Humber TraC | RIVER OUSE | Not Applicable | Not Applicable | Not Applicable | 251:45 | 55 | 68.6 | 2020 | 99.99 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS00095
YWS00096 | Yorkshire Water | Live | CONSTABLE BURTON STW | CONSTABLE BURTON/STW | 2216 | 2216 | A2 | Inlet SO at WwTW | SE1718390702 | 417183 | 490702 | GB104027068940 | Bedale/Newton/Burton Bk from Source to Brompton Bk | River | 3317 | Middle Swale | 3088 | Swale, Ure, Nidd and Upper Ouse | BURTON BECK | Not Applicable | Not Applicable | Not Applicable | 455:15 | 49 | 42.4 | 2020 | 99.95 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00096
YWS00097 | Yorkshire Water | Live | YWS UNKNOWN SITES DEFAULT | WATER END/CSO | 2218 | 2218 | 1 | Storm discharge at pumping station | SE3774096520 | 437740 | 496520 | GB104027069540 | Willow Beck Catchment (trib of Wiske) | River | 3541 | Wiske | 3088 | Swale, Ure, Nidd and Upper Ouse | TRIB WISKE/SWALE | Not Applicable | Not Applicable | Not Applicable | 103:00 | 36 | 12.8 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00097
YWS00098 | Yorkshire Water | Live | YWS UNKNOWN SITES DEFAULT | LODGE LANE/CSO | 2218 | 2218 | 2 | SO on sewer network | SE3708096260 | 437087 | 496261 | GB104027069540 | Willow Beck Catchment (trib of Wiske) | River | 3541 | Wiske | 3088 | Swale, Ure, Nidd and Upper Ouse | TRIB WISKE/SWALE | Not Applicable | Not Applicable | Not Applicable | 131:30 | 44 | 32.2 | 2020 | 99.93 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00098
YWS00099 | Yorkshire Water | Live | YWS UNKNOWN SITES DEFAULT | THE GREEN/CSO | 2218 | 2218 | 3 | SO on sewer network | SE3581093540 | 435813 | 493544 | GB104027069540 | Willow Beck Catchment (trib of Wiske) | River | 3541 | Wiske | 3088 | Swale, Ure, Nidd and Upper Ouse | TRIB WISKE/SWALE | Not Applicable | Not Applicable | Not Applicable | 51:45 | 25 | 27 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00099
YWS00100 | Yorkshire Water | Live | GARFORTH STW | GARFORTH/STW | 2225 | 2225 | A2 | Storm tank at WwTW | SE4175028790 | 441750 | 428790 | GB104027062810 | Lin Dike from Source to River Aire | River | 3265 | Lower Aire | 3001 | Aire and Calder | SHEFFIELD BECK | Not Applicable | Not Applicable | Not Applicable | 536:30 | 46 | 55.6 | 2020 | 99.95 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00100
YWS00101 | Yorkshire Water | Live | WHITECOTE HILL CSO | WHITECOTE HILL/CSO | 2226 | 2226 | A1 | SO on sewer network | SE2373936344 | 423739 | 436344 | GB104027063032 | Aire from Gill Beck (Baildon) to River Calder | River | 3265 | Lower Aire | 3001 | Aire and Calder | RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 6:30 | 8 | 5.2 | 2020 | 96.85 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00101
YWS00102 | Yorkshire Water | Live | FOULRIDGE CSO | FOULRIDGE/CSO | 2240 | 2240 | A1 | SO on sewer network | SD8886242637 | 388863 | 442637 | GB104027062980 | Earby Beck from source to River Aire | River | 3484 | Upper Aire | 3001 | Aire and Calder | COUNTY DYKE | Not Applicable | Not Applicable | Not Applicable | 176:30 | 75 | 89.6 | 2020 | 100 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS00102
YWS00103 | Yorkshire Water | Live | GRIMETHORPE STW | GRIMETHORPE/STW/3XDWF OVERFLOW | 2246 | 2246 | A2 | Storm tank at WwTW | SE4025009630 | 440258 | 409623 | GB104027063180 | Grimethorpe Dike from Source to River Dearne | River | 3125 | Dearne | 3029 | Don and Rother | SHAFTON BECK | Not Applicable | Not Applicable | Not Applicable | 588:15 | 62 | 63.8 | 2020 | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00103
YWS00104 | Yorkshire Water | Live | GRIMETHORPE STW | GRIMETHORPE/STW/6XDWF OVERFLOW | 2246 | 2246 | A3 | Inlet SO at WwTW | SE4025009630 | 440258 | 409623 | GB104027063180 | Grimethorpe Dike from Source to River Dearne | River | 3125 | Dearne | 3029 | Don and Rother | SHAFTON BECK | Not Applicable | Not Applicable | Not Applicable | 8:45 | 5 | 6.4 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00104
YWS00105 | Yorkshire Water | Live | YWS UNKNOWN SITES DEFAULT | TREETON LANE/CSO | 2250 | 2250 | 2 | Storm discharge at pumping station | SK3889092820 | 442570 | 388450 | GB104027057772 | Rother, Doe Lea to Don | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | TRIBUTARY OF THE RIVER ROTHER | Not Applicable | Not Applicable | Not Applicable | 18:30 | 13 | 29.4 | 2020 | 99.97 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00105
YWS00106 | Yorkshire Water | Live | YWS UNKNOWN SITES DEFAULT | TREETON/CSO | 2250 | 2250 | 3 | Storm discharge at pumping station | SK3889092820 | 443250 | 388530 | GB104027057772 | Rother, Doe Lea to Don | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | TRIBUTARY OF THE RIVER ROTHER | Not Applicable | Not Applicable | Not Applicable | 56:30 | 19 | 23.8 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00106
YWS00107 | Yorkshire Water | Live | YWS UNKNOWN SITES DEFAULT | WHISTON VALE/CSO | 2250 | 2250 | 4 | Storm discharge at pumping station | SK3889092820 | 444390 | 389900 | GB104027057772 | Rother, Doe Lea to Don | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | TRIBUTARY OF THE RIVER ROTHER | Not Applicable | Not Applicable | Not Applicable | 35:30 | 19 | 22 | 2020 | 99.91 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00107
YWS00108 | Yorkshire Water | Live | DENHOLME (DOE PARK) WWTW | DENHOLME/NO 2 STW/3XDWF OVERFLOW | 2251 | 2251 | A2 | Storm tank at WwTW | SE0763334250 | 407633 | 434250 | GB104027062870 | Harden Beck from Source to River Aire | River | 3307 | Middle Aire | 3001 | Aire and Calder | DENHOLME BECK | Not Applicable | Not Applicable | Not Applicable | 1086:00 | 99 | 115 | 2020 | 98.75 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS00108
YWS00109 | Yorkshire Water | Live | NEILEY NO. 2 STW | NEILEY/NO 2 STW | 2255 | 2255 | A2 | Storm tank at WwTW | SE1463011560 | 414670 | 411530 | GB104027063301 | Holme from New Mill Dike to R Colne | River | 3097 | Colne and Holme | 3001 | Aire and Calder | RIVER HOLME | Not Applicable | Not Applicable | Not Applicable | 886:00 | 68 | 77.8 | 2020 | 100 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00109
YWS00110 | Yorkshire Water | Live | OLD MAIN STREET CSO | OLD MAIN STREET XXX/CSO | 2279 | 2279 | 6 | SO on sewer network | SE1053039380 | 410539 | 439383 | GB104027063034 | Aire (R Worth to Gill Beck) | River | 3307 | Middle Aire | 3001 | Aire and Calder | VARIOUS | Not Applicable | Not Applicable | Not Applicable | 379:30 | 33 | 25.8 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00110
YWS00111 | Yorkshire Water | Live | ST PEG LANE CSO | ST PEG LANE/NO 2 CSO | 2281 | 2281 | 1 | SO on sewer network | SE1953025130 | 419533 | 425133 | GB104027062710 | Spen Beck from Source to River Calder | River | 3268 | Lower Calder | 3001 | Aire and Calder | RIVER SPEN | Not Applicable | Not Applicable | Not Applicable | 214:30 | 37 | 36 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00111
YWS00113 | Yorkshire Water | Live | TIGLEY CSO, TINGLEY | TINGLEY/CSO | 2294 | 2294 | A1 | Storm discharge at pumping station | SE2875226361 | 428752 | 426361 | GB104027062750 | Milshaw Beck from Source to Low/Wortley/Pudsey Bks | River | 3265 | Lower Aire | 3001 | Aire and Calder | DENSHAW BECK | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0 | 2020 | 99.85 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00113
YWS00114 | Yorkshire Water | Live | THE GRANARY CSO | THE GRANARY/CSO | 2299 | 2299 | A1 | SO on sewer network | SE2720059100 | 426020 | 459090 | GB104027068296 | Nidd from Burstwith to Oak Beck | River | 3308 | Middle and Lower Nidd | 3088 | Swale, Ure, Nidd and Upper Ouse | NIDD AND TRIBS | Not Applicable | Not Applicable | Not Applicable | 442:15 | 82 | 72 | 2020 | 94.42 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00114
YWS00115 | Yorkshire Water | Live | THE GRANARY CSO | HOLLINS CLOSE/CSO | 2299 | EPR/UB3896EN | A1 | SO on sewer network | SE2720059100 | 426164 | 458712 | GB104027068296 | Nidd from Burstwith to Oak Beck | River | 3308 | Middle and Lower Nidd | 3088 | Swale, Ure, Nidd and Upper Ouse | NIDD AND TRIBS | Not Applicable | Not Applicable | Not Applicable | 175:45 | 38 | 36 | 2020 | 98.13 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00115
YWS00116 | Yorkshire Water | Live | SPRINGWELL LANE NORTH CSO | SPRINGWELL LANE NORTH/CSO | 2300 | 2300 | A1 | SO on sewer network | SE3637993805 | 436379 | 493805 | GB104027069540 | Willow Beck Catchment (trib of Wiske) | River | 3541 | Wiske | 3088 | Swale, Ure, Nidd and Upper Ouse | WILLOW BECK | Not Applicable | Not Applicable | Not Applicable | 203:15 | 70 | 81.4 | 2020 | 99.11 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement completed | SOAF investigation ongoing | YWS00116
YWS00117 | Yorkshire Water | Live | Not matched in EA Consents Database | UPWELL STREET/CSO | 2301 | 2301 | 1 | SO on sewer network | SK3851890505 | 438518 | 390505 | GB104027057412 | Don from River Loxley confl to River Don Works | River | 3312 | Middle Don | 3029 | Don and Rother | Not matched in EA Consents Database | Not Applicable | Not Applicable | Not Applicable | 46:15 | 25 | 22.2 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00117
YWS00118 | Yorkshire Water | Live | SILKSTONE STW | SILKSTONE/STW/3XDWF OVERFLOW | 2313 | 2313 | A2 | Storm tank at WwTW | SE2948006430 | 429480 | 406430 | GB104027057560 | Silkstone Beck from Source to Cawthorne Dyke | River | 3125 | Dearne | 3029 | Don and Rother | SILKSTONE BECK | Not Applicable | Not Applicable | Not Applicable | 471:30 | 65 | 46 | 2020 | 100 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00118
YWS00119 | Yorkshire Water | Live | DAWSONS CORNER CSO | DAWSONS CORNER/CSO | 2314 | 2314 | A1 | SO on sewer network | SE2094334467 | 420943 | 434467 | GB104027062830 | Low/Wortley/Pudsey Bks | River | 3265 | Lower Aire | 3001 | Aire and Calder | TRIBUTARY OF BAGLEY BECK | Not Applicable | Not Applicable | Not Applicable | 128:45 | 48 | 43.4 | 2020 | 56.27 | Comms failure / issue | Scheduled | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00119
YWS00120 | Yorkshire Water | Live | KINGS MILL LANE NO 2 CSO | KINGS MILL LANE/NO 2 CSO | 2325 | 2325 | A1 | SO on sewer network | SE1512216255 | 415122 | 416255 | GB104027062550 | Colne from River Holme to River Calder | River | 3097 | Colne and Holme | 3001 | Aire and Calder | RIVER COLNE | Not Applicable | Not Applicable | Not Applicable | 15:45 | 9 | 5 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00120
YWS00121 | Yorkshire Water | Live | STONEBRIDGE LANE CSO | STONEBRIDGE LANE/CSO | 2329 | 2329 | 1 | SO on sewer network | SE2547032860 | 425471 | 432864 | GB104027062830 | Low/Wortley/Pudsey Bks | River | 3265 | Lower Aire | 3001 | Aire and Calder | FARNLEY BECK | Not Applicable | Not Applicable | Not Applicable | 4:30 | 9 | 11 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00121
YWS00122 | Yorkshire Water | Live | CHURCH HILL CSO | CHURCH HILL/CSO | 2332 | 2332 | 1 | SO on sewer network | SE3661011030 | 436617 | 411039 | GB104027063230 | Cudworth Dyke from Source to River Dearne | River | 3125 | Dearne | 3029 | Don and Rother | ROYSTON SCOTT DIKE | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 1.2 | 2020 | 99.73 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00122
YWS00123 | Yorkshire Water | Live | HOYLANDSWAINE STW | HOYLANDSWAINE/STW/3XDWF OVERFLOW | 2344 | 2344 | 2 | Storm tank at WwTW | SE2690005700 | 426900 | 405700 | GB104027057560 | Silkstone Beck from Source to Cawthorne Dyke | River | 3125 | Dearne | 3029 | Don and Rother | ELLHIRST BECK | Not Applicable | Not Applicable | Not Applicable | 1437:45 | 146 | 121.8 | 2020 | 99.98 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement ongoing | SOAF investigation ongoing | YWS00123
YWS00124 | Yorkshire Water | Live | HOYLANDSWAINE STW | HOYLANDSWAINE/STW/6XDWF OVERFLOW | 2344 | 2344 | 3 | Inlet SO at WwTW | SE2690005700 | 426900 | 405700 | GB104027057560 | Silkstone Beck from Source to Cawthorne Dyke | River | 3125 | Dearne | 3029 | Don and Rother | ELLHIRST BECK | Not Applicable | Not Applicable | Not Applicable | 126:30 | 31 | 118.33 | 2020 | 61.44 | Installation set-up/design issue | Resolved - May | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement ongoing | SOAF investigation ongoing | YWS00124
YWS00125 | Yorkshire Water | Live | MALHAM WWTW | MALHAM/NO 2 STW | 2346 | 2346 | 2 | Inlet SO at WwTW | SD9023062190 | 390200 | 462200 | GB104027063110 | Aire from Malham Tarn to Malham Beck | River | 3484 | Upper Aire | 3001 | Aire and Calder | MALHAM BECK | Not Applicable | Not Applicable | Not Applicable | 940:30 | 77 | 84.6 | 2020 | 100 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation ongoing | Operational improvement ongoing | SOAF investigation ongoing | YWS00125
YWS00126 | Yorkshire Water | Live | CLAYTON STW | CLAYTON/STW | 2352 | 2352 | A2 | Storm tank at WwTW | SE4570008000 | 445700 | 408000 | GB104027063140 | Frickley Beck from Source to Ea Beck | River | 3272 | Lower Don | 3029 | Don and Rother | FRICKLEY BECK | Not Applicable | Not Applicable | Not Applicable | 33:30 | 9 | 15.4 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00126
YWS00127 | Yorkshire Water | Live | STAPLETON PARK WWTW | STAPLETON PARK/STW | 2363 | 2363 | A2 | Inlet SO at WwTW | SE5150018980 | 451500 | 418980 | GB104027063370 | Womersley Beck from Source to Blowell Drain | River | 3272 | Lower Don | 3029 | Don and Rother | TRIB OF WOMERSLEY BECK | Not Applicable | Not Applicable | Not Applicable | 90:00 | 31 | 55.4 | 2020 | 99.64 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00127
YWS00128 | Yorkshire Water | Live | YWS UNKNOWN SITES DEFAULT | LAWNS LANE/CSO | 2365 | 2365 | 1 | SO on sewer network | SE2508031150 | 425083 | 431155 | GB104027062830 | Low/Wortley/Pudsey Bks | River | 3265 | Lower Aire | 3001 | Aire and Calder | TRIB OF WORTLEY BECK | Not Applicable | Not Applicable | Not Applicable | 3:15 | 7 | 7 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00128
YWS00129 | Yorkshire Water | Live | MELTHAM CSO | MELTHAM/CSO | 2378 | 2378 | A1 | SO on sewer network | SE1090511160 | 410905 | 411160 | GB104027063590 | Mag Brook from Source to River Holme | River | 3097 | Colne and Holme | 3001 | Aire and Calder | MELTHAM DIKE | Not Applicable | Not Applicable | Not Applicable | 29:45 | 10 | 10.67 | 2020 | 51.63 | Comms failure / issue | Resolved - Dec | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00129
YWS00130 | Yorkshire Water | Live | CHAPEL LANE NO 2 CSO | CHAPEL LANE/NO 2 CSO | 2396 | 2396 | A1 | SO on sewer network | SE2199123854 | 421991 | 423854 | GB104027062710 | Spen Beck from Source to River Calder | River | 3268 | Lower Calder | 3001 | Aire and Calder | TRIB OF RIVER SPEN | Not Applicable | Not Applicable | Not Applicable | 20:45 | 15 | 24.2 | 2020 | 95.63 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00130
YWS00131 | Yorkshire Water | Live | EAST ARDSLEY NO 2 CSO | EAST ARDSLEY/NO 2 CSO | 2397 | 2397 | A1 | SO on sewer network | SE2992026115 | 429920 | 426115 | GB104027062680 | Oulton Beck from Source to River Aire | River | 3265 | Lower Aire | 3001 | Aire and Calder | C. TRIB OF LINGWELL GATE BECK | Not Applicable | Not Applicable | Not Applicable | 2:45 | 6 | 6.2 | 2020 | 97.13 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00131
YWS00132 | Yorkshire Water | Live | YWS UNKNOWN SITES DEFAULT | BEESTON RING ROAD/CSO | 2408 | 2408 | 1 | SO on sewer network | SE2823029570 | 428232 | 429573 | GB104027062750 | Milshaw Beck from Source to Low/Wortley/Pudsey Bks | River | 3265 | Lower Aire | 3001 | Aire and Calder | MILLSHAW BECK | Not Applicable | Not Applicable | Not Applicable | 6:30 | 8 | 5.6 | 2020 | 56.93 | Comms failure / issue | Resolved - Jun | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00132
YWS00133 | Yorkshire Water | Live | DENBY DALE ROAD CSO | DENBY DALE ROAD/CSO | 2411 | 2411 | A1 | SO on sewer network | SE3216417743 | 432164 | 417743 | GB104027062631 | Calder from River Colne to River Chald | River | 3268 | Lower Calder | 3001 | Aire and Calder | TRIBUTARY OF THE RIVER CALDER | Not Applicable | Not Applicable | Not Applicable | 1:45 | 1 | 1.2 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00133
YWS00134 | Yorkshire Water | Live | NETHERTON CSO | NETHERTON/CSO | 2412 | 2412 | A1 | SO on sewer network | SE2803116495 | 428031 | 416495 | GB104027062631 | Calder from River Colne to River Chald | River | 3268 | Lower Calder | 3001 | Aire and Calder | PITS BECK CULVERTED | Not Applicable | Not Applicable | Not Applicable | 20:15 | 20 | 22 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00134
YWS00135 | Yorkshire Water | Live | GREAT CLIFF PS & STORM TANK | GREAT CLIFF/SPS | 2413 | 2413 | 2 | Storm discharge at pumping station | SE3031015610 | 430310 | 415610 | GB104027062631 | Calder from River Colne to River Chald | River | 3268 | Lower Calder | 3001 | Aire and Calder | DENNINGTON BECK | Not Applicable | Not Applicable | Not Applicable | 368:15 | 53 | 44.4 | 2020 | 99.86 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00135
YWS00137 | Yorkshire Water | Live | REGENT DRIVE CSO | REGENT DRIVE/NO 2 CSO | 2438 | 2438 | 1 | SO on sewer network | SD9996052110 | 399964 | 452111 | GB104027063020 | Eller Beck from Haw Beck to River Aire | River | 3484 | Upper Aire | 3001 | Aire and Calder | TRIB OF SKIBEDEN BECK | Not Applicable | Not Applicable | Not Applicable | 18:30 | 9 | 2.8 | 2020 | 98.24 |  |  | High spill threshold not met | High spill threshold not met | Operational investigation completed | Operational improvement completed | No SOAF investigation required | YWS00137
YWS00138 | Yorkshire Water | Permit Application Submitted | TBC When Permit Issued | HOOTON PAGNELL/STW | Permit applied for | 2455 | TBC | Inlet SO at WwTW | SE4820008300 | 448200 | 408300 | GB104027063140 | Frickley Beck from Source to Ea Beck | River | 3272 | Lower Don | 3029 | Don and Rother | HOOTON PAGNELL BECK | Not Applicable | Not Applicable | Not Applicable | 65:15 | 45 | 56.4 | 2020 | 99.99 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement ongoing | SOAF investigation ongoing | YWS00138
YWS00139 | Yorkshire Water | Live | SWINNOW VIEW CSO | SWINNOW VIEW/CSO | 2467 | 2467 | A1 | SO on sewer network | SE2455433606 | 424554 | 433606 | GB104027062830 | Low/Wortley/Pudsey Bks | River | 3265 | Lower Aire | 3001 | Aire and Calder | FARNLEY BECK | Not Applicable | Not Applicable | Not Applicable | 0:15 | 1 | 0.2 | 2020 | 99.91 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00139
YWS00140 | Yorkshire Water | Live | RENISHAW STW | RENISHAW/STW | 2469 | 2469 | A2 | Storm tank at WwTW | SK4483078200 | 444830 | 378200 | GB104027057772 | Rother, Doe Lea to Don | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | SMITHY BROOK | Not Applicable | Not Applicable | Not Applicable | 1667:00 | 124 | 87 | 2020 | 99.87 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00140
YWS00141 | Yorkshire Water | Live | WOODHOUSE LANE CSO | WOODHOUSE LANE/CSO | 2479 | 2479 | A1 | SO on sewer network | SE1588321823 | 415883 | 421823 | GB104027062642 | Calder from Ryburn Confluence to River Colne | River | 3310 | Middle Calder | 3001 | Aire and Calder | RIVER CALDER | Not Applicable | Not Applicable | Not Applicable | 104:15 | 71 | 30.6 | 2020 | 99.93 |  |  | Not asset maintenance - Hydraulic capacity | High spill threshold not met | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS00141
YWS00144 | Yorkshire Water | Live | ADDINGHAM NO.1 STORM TANKS | ADDINGHAM/NO 1 SPS/PRELIMINARY TREATMENT-STW/3XDWF OVERFLOW | 2482 | 2482 | A1 | Storm discharge at pumping station | SE0900049000 | 409000 | 449000 | GB104027064257 | Wharfe from Barben Beck/River Dibb to Hundwith Beck | River | 3318 | Middle Wharfe and Washburn | 3115 | Wharfe and Lower Ouse | RIVER WHARFE | Not Applicable | Wharfe at Cromwheel, Ilkley | Not Applicable | 653:15 | 66 | 57.8 | 2020 | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00144
YWS00145 | Yorkshire Water | Live | ADDINGHAM NO.1 STORM TANKS | ADDINGHAM/NO 1 SPS/PRELIMINARY TREATMENT-STW/6XDWF OVERFLOW | 2482 | 2482 | A2 | Storm discharge at pumping station | SE0900049000 | 409000 | 449000 | GB104027064257 | Wharfe from Barben Beck/River Dibb to Hundwith Beck | River | 3318 | Middle Wharfe and Washburn | 3115 | Wharfe and Lower Ouse | RIVER WHARFE | Not Applicable | Wharfe at Cromwheel, Ilkley | Not Applicable | 42:45 | 23 | 51.6 | 2020 | 99.97 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00145
YWS00146 | Yorkshire Water | Live | WOODFALL SHELF EAST 2 CSO | WOODFALL SHELF EAST/2 CSO | 2490 | 2490 | A1 | SO on sewer network | SE1290028090 | 412900 | 428000 | GB104027062700 | Clifton Beck from Source to River Calder | River | 3310 | Middle Calder | 3001 | Aire and Calder | BROW LANE SEWER | Not Applicable | Not Applicable | Not Applicable | 46:45 | 35 | 33.67 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00146
YWS00147 | Yorkshire Water | Live | DOWLEY GAP (BINGLEY) WWTW | DOWLEY GAP/STW | 2502 | 2502 | A2 | Storm tank at WwTW | SE1230338141 | 412303 | 438141 | GB104027063034 | Aire (R Worth to Gill Beck) | River | 3307 | Middle Aire | 3001 | Aire and Calder | RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 475:50 | 77 | 77.4 | 2020 | 99.93 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00147
YWS00148 | Yorkshire Water | Live | DOWLEY GAP (BINGLEY) WWTW | DOWLEY GAP/STW | 2502 | 2502 | A3 | Inlet SO at WwTW | SE1230338141 | 412303 | 438141 | GB104027063034 | Aire (R Worth to Gill Beck) | River | 3307 | Middle Aire | 3001 | Aire and Calder | RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 56:22 | 27 | 20.4 | 2020 | 99.94 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00148
YWS00149 | Yorkshire Water | Live | NEW HEY ROAD CSO | NEW HEY ROAD/CSO | 2504 | 2504 | A1 | SO on sewer network | SE0890818023 | 408908 | 418023 | GB104027062570 | Black Brook from Source to River Calder | River | 3310 | Middle Calder | 3001 | Aire and Calder | CULVERTED TRIB LONGWOOD BROOK | Not Applicable | Not Applicable | Not Applicable | 20:45 | 13 | 18.6 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00149
YWS00150 | Yorkshire Water | Live | WORTLEY VALLEY CSO | WORTLEY VALLEY/CSO | 2506 | 2506 | A1 | SO on sewer network | SE2785631380 | 427856 | 431380 | GB104027062830 | Low/Wortley/Pudsey Bks | River | 3265 | Lower Aire | 3001 | Aire and Calder | WORTLEY BECK PUMPED OUTLET | Not Applicable | Not Applicable | Not Applicable | 24:45 | 17 | 38.5 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | Operational investigation completed | No improvement action in reporting period | No SOAF investigation required | YWS00150
YWS00151 | Yorkshire Water | Live | SADDLEWORTH ROAD CSO | SADDLEWORTH ROAD/CSO | EPRSB3590RG | EPR/SB3590RG | A1 | SO on sewer network | SE0857420785 | 408574 | 420785 | GB104027062570 | Black Brook from Source to River Calder | River | 3310 | Middle Calder | 3001 | Aire and Calder | BLACK BROOK | Not Applicable | Not Applicable | Not Applicable | 129:30 | 37 | 24.6 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00151
YWS00152 | Yorkshire Water | Live | YWS UNKNOWN SITES DEFAULT | CARR HALL LANE/CSO | 2515 | 2515 | A1 | SO on sewer network | SE0942021120 | 408854 | 419485 | GB104027062570 | Black Brook from Source to River Calder | River | 3310 | Middle Calder | 3001 | Aire and Calder | CALDER AND TRIBS | Not Applicable | Not Applicable | Not Applicable | 0:15 | 1 | 4.4 | 2020 | 99.89 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00152
YWS00153 | Yorkshire Water | Live | WEST VALE CSO | WEST VALE/CSO | EPRSB3590WC | EPR/SB3590WC | A1 | SO on sewer network | SE0942421127 | 409424 | 421127 | GB104027062570 | Black Brook from Source to River Calder | River | 3310 | Middle Calder | 3001 | Aire and Calder | BLACK BROOK | Not Applicable | Not Applicable | Not Applicable | 2082:15 | 177 | 133.8 | 2020 | 99.98 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | Operational investigation completed | Operational improvement ongoing | SOAF investigation completed - No work required | YWS00153
YWS00154 | Yorkshire Water | Live | YWS UNKNOWN SITES DEFAULT | WADLANDS CLOSE/CSO | 2516 | 2516 | 1 | SO on sewer network | SE2155035560 | 421550 | 435560 | GB104027063032 | Aire from Gill Beck (Baildon) to River Calder | River | 3265 | Lower Aire | 3001 | Aire and Calder | TRIB OF BAGLEY BECK | Not Applicable | Not Applicable | Not Applicable | 1:15 | 3 | 1 | 2020 | 91.88 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00154
YWS00155 | Yorkshire Water | Live | MANCHESTER ROAD CSO | MANCHESTER ROAD/CSO | 2537 | 2537 | A1 | SO on sewer network | SE1647032210 | 416510 | 432210 | GB104027062862 | Bradford Beck (Clayton Bk to R Aire) | River | 3307 | Middle Aire | 3001 | Aire and Calder | BOWLING BECK | Not Applicable | Not Applicable | Not Applicable | 15:00 | 22 | 4.8 | 2020 | 99.77 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00155
YWS00156 | Yorkshire Water | Live | LYON ROAD NO 2 CSO | LYON ROAD/NO 2 CSO | 2541 | 2541 | A1 | SO on sewer network | SE0180044950 | 401810 | 444950 | GB104027062960 | Eastburn Beck from Lothersdale Beck to River Aire | River | 3484 | Upper Aire | 3001 | Aire and Calder | MILL STREAM TRIB EASTBURN BECK | Not Applicable | Not Applicable | Not Applicable | 26:30 | 17 | 10.6 | 2020 | 99.94 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00156
YWS00157 | Yorkshire Water | Live | CHEESEBOTTOM STW | CHEESEBOTTOM/STW | 2556 | 2556 | A2 | Inlet SO at WwTW | SE2801000980 | 427990 | 401280 | GB104027057490 | Don from Scout Dyke to the Little Don | River | 3490 | Upper Don | 3029 | Don and Rother | RIVER DON | Not Applicable | Not Applicable | Not Applicable | 25:45 | 18 | 9.6 | 2020 | 99.98 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00157
YWS00158 | Yorkshire Water | Live | ELLERKER WWTW | ELLERKER/NO 2 STW | 2562 | 2562(T) | A2 | Inlet SO at WwTW | SE9051027140 | 490520 | 427127 | GB530402609202 | HUMBER MIDDLE | Transitional Water | 3228 | Humber Estuary TraC | 3040 | Humber TraC | CRABLEY CREEK | Not Applicable | Not Applicable | Not Applicable | 1182:00 | 115 | 112.8 | 2020 | 100 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS00158
YWS00159 | Yorkshire Water | Live | FARTOWN BRADFORD ROAD CSO | FARTOWN BRADFORD RD/CSO | 2579 | 2579 | A1 | SO on sewer network | SE1520717533 | 415207 | 417533 | GB104027062550 | Colne from River Holme to River Calder | River | 3097 | Colne and Holme | 3001 | Aire and Calder | RIVER COLNE VIA BIRKBY RELIEF | Not Applicable | Not Applicable | Not Applicable | 9:45 | 15 | 13.4 | 2020 | 99.78 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00159
YWS00160 | Yorkshire Water | Live | EMBSAY WWTW | EMBSAY/STW/3XDWF OVERFLOW | 2583 | 2583 | A2 | Storm tank at WwTW | SD9988353009 | 399982 | 453069 | GB104027063060 | Haw Beck from Source to Eller beck | River | 3484 | Upper Aire | 3001 | Aire and Calder | TRIB OF HAW BECK | Not Applicable | Not Applicable | Not Applicable | 1682:00 | 127 | 86.6 | 2020 | 99.96 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement completed | SOAF investigation ongoing | YWS00160
YWS00162 | Yorkshire Water | Live | FIELD 4751 MELMERBY CSO | FIELD 4751 MELMERBY/CSO | 2601 | 2601 | A1 | SO on sewer network | SE3362576527 | 433625 | 476527 | GB104027069461 | Ure from Thornton Steward Beck to River Skell | River | 3309 | Middle and Lower Ure | 3088 | Swale, Ure, Nidd and Upper Ouse | TRIB NORTON BK/NUNWICK BK/ | Not Applicable | Not Applicable | Not Applicable | 20:00 | 18 | 15.6 | 2020 | 99.91 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00162
YWS00163 | Yorkshire Water | Live | ALMA VILLAS | ALMA VILLAS/CSO | 2619 | 2619 | A1 | SO on sewer network | SE3661329444 | 436613 | 429444 | GB104027063032 | Aire from Gill Beck (Baildon) to River Calder | River | 3265 | Lower Aire | 3001 | Aire and Calder | RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 1:00 | 4 | 5.2 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00163
YWS00164 | Yorkshire Water | Live | RED DOLES ROAD CSO | RED DOLES ROAD/CSO | 2623 | 2623 | A1 | SO on sewer network | SE1580618021 | 415806 | 418021 | GB104027062550 | Colne from River Holme to River Calder | River | 3097 | Colne and Holme | 3001 | Aire and Calder | RIVER COLNE | Not Applicable | Not Applicable | Not Applicable | 114:45 | 51 | 43.6 | 2020 | 100 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00164
YWS00165 | Yorkshire Water | Revoke Application Submitted | YWS UNKNOWN SITES DEFAULT | LADY ANN ROAD/CSO | 2634 | 2634 | 1 | SO on sewer network | SE2497024320 | 424972 | 424323 | GB104027062670 | Batley Beck from Source to River Calder | River | 3268 | Lower Calder | 3001 | Aire and Calder | BATLEY BECK TO RIVER CALDER | Not Applicable | Not Applicable | Not Applicable | [5 empty] | No longer operational as an overflow - permit revoked or to be revoked | Overflow no longer spilling to environment - from Jan | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00165
YWS00166 | Yorkshire Water | Live | STANNARY CSO | STANNARY HALIFAX/CSO | 2641 | 2641 | A1 | SO on sewer network | SE0912025730 | 409122 | 425732 | GB104027062780 | Hebble Brook from Source to River Calder | River | 3310 | Middle Calder | 3001 | Aire and Calder | HEBBLE BROOK | Not Applicable | Not Applicable | Not Applicable | 1:15 | 3 | 1.4 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00166
YWS00167 | Yorkshire Water | Permit Application Submitted | TBC When Permit Issued | APPLETON LE MOOR/STW | Permit applied for | 2643 | TBC | Inlet SO at WwTW | SE7350087400 | 473300 | 487300 | GB104027068490 | Seven from Little Beck to Catter Beck | River | 3387 | Rye | 3027 | Derwent Humber | TRIB OF RIVER SEVEN | Not Applicable | Not Applicable | Not Applicable | 3:30 | 4 | 9.4 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00167
YWS00168 | Yorkshire Water | Live | CUDWORTH STW | CUDWORTH/NO 2 STW/3XDWF OVERFLOW | 2655 | 2655 | A2 | Storm tank at WwTW | SE3931007110 | 439310 | 407110 | GB104027063230 | Cudworth Dyke from Source to River Dearne | River | 3125 | Dearne | 3029 | Don and Rother | RIVER DEARNE | Not Applicable | Not Applicable | Not Applicable | 268:15 | 30 | 60 | 2020 | 99.99 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | No investigation activity in reporting period | No improvement action in reporting period | SOAF investigation completed - No work required | YWS00168
YWS00170 | Yorkshire Water | Live | SOUTH STATION ROAD CSO | SOUTH STATION ROAD/CSO | 2688 | 2688 | 1 | SO on sewer network | SE1568039160 | 415680 | 439160 | GB104027063034 | Aire (R Worth to Gill Beck) | River | 3307 | Middle Aire | 3001 | Aire and Calder | BARNSLEY BEACK TO RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 75:15 | 44 | 50.6 | 2020 | 99.99 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00170
YWS00171 | Yorkshire Water | Live | WYVIL CRESCENT CSO | WYVIL CRESCENT/CSO | 27/19/0019 | 27/19/0019 | A1 | SO on sewer network | SE1360848128 | 413608 | 448128 | GB104027064257 | Wharfe from Barben Beck/River Dibb to Hundwith Beck | River | 3318 | Middle Wharfe and Washburn | 3115 | Wharfe and Lower Ouse | RIVER WHARFE | Not Applicable | Not Applicable | Not Applicable | 569:45 | 87 | 89.2 | 2020 | 100 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement completed | SOAF investigation ongoing | YWS00171
YWS00172 | Yorkshire Water | Live | LEEDS ROAD ILKLEY NO2 CSO | LEEDS ROAD ILKLEY/2 CSO | QC.27/19/0024 | 27/19/0024 | A1 | SO on sewer network | SE1284348265 | 412843 | 448265 | GB104027064257 | Wharfe from Barben Beck/River Dibb to Hundwith Beck | River | 3318 | Middle Wharfe and Washburn | 3115 | Wharfe and Lower Ouse | THE RIVER WHARFE | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 1.4 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00172
YWS00173 | Yorkshire Water | Live | BEN RHYDDING (ILKLEY) WPC WORKS, ST | BEN RHYDDING/STW | 27/19/0044 | 27/19/0044 | 2 | Storm tank at WwTW | SE1474047310 | 414740 | 447310 | GB104027064257 | Wharfe from Barben Beck/River Dibb to Hundwith Beck | River | 3318 | Middle Wharfe and Washburn | 3115 | Wharfe and Lower Ouse | RIVER WHARFE | Not Applicable | Not Applicable | Not Applicable | 2504:45 | 158 | 122 | 2020 | 99.98 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement completed | SOAF investigation ongoing | YWS00173
YWS00174 | Yorkshire Water | Live | ILKLEY SEWAGE TREATMENT WORKS | ILKLEY/STW/3XDWF OVERFLOW | 27/19/0045 | 27/19/0045 | A2 | Storm tank at WwTW | SE1240048430 | 412400 | 448430 | GB104027064257 | Wharfe from Barben Beck/River Dibb to Hundwith Beck | River | 3318 | Middle Wharfe and Washburn | 3115 | Wharfe and Lower Ouse | RIVER WHARFE | Not Applicable | Not Applicable | Not Applicable | 589:21 | 63 | 79.4 | 2020 | 100 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00174
YWS00175 | Yorkshire Water | Live | ILKLEY SEWAGE TREATMENT WORKS | ILKLEY/STW/6XDWF OVERFLOW | 27/19/0045 | 27/19/0045 | A3 | Inlet SO at WwTW | SE1240048430 | 412400 | 448430 | GB104027064257 | Wharfe from Barben Beck/River Dibb to Hundwith Beck | River | 3318 | Middle Wharfe and Washburn | 3115 | Wharfe and Lower Ouse | RIVER WHARFE | Not Applicable | Not Applicable | Not Applicable | 386:00 | 74 | 83.2 | 2020 | 100 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00175
YWS00176 | Yorkshire Water | Live | MIDDLETON (ILKLEY) PUMPING STATION | ILKLEY MIDDLETON/CSO | 27/19/0052 | 27/19/0052 | 1 | Storm discharge at pumping station | SE1215048470 | 412150 | 448470 | GB104027064257 | Wharfe from Barben Beck/River Dibb to Hundwith Beck | River | 3318 | Middle Wharfe and Washburn | 3115 | Wharfe and Lower Ouse | RIVER WHARFE | Not Applicable | Wharfe at Cromwheel, Ilkley | Not Applicable | 281:30 | 38 | 38.4 | 2020 | 99.98 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00176
YWS00177 | Yorkshire Water | Live | BURNSALL CAR PARK SPS | BURNSALL CAR PK/CSO | 27/19/0054 | 27/19/0054 | 1 | Storm discharge at pumping station | SE0319461039 | 403180 | 461020 | GB104027064253 | Wharfe from Park Gill Bk to Barben Beck/River Dibb | River | 3507 | Upper Wharfe | 3115 | Wharfe and Lower Ouse | RIVER WHARFE | Not Applicable | Wharfe at Cromwheel, Ilkley | Not Applicable | 192:42 | 35 | 46.4 | 2020 | 100 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00177
YWS00178 | Yorkshire Water | Live | ASKWITH SPS | ASKWITH/CSO | 27/19/0056 | 27/19/0056 | A2 | SO on sewer network | SE1641048060 | 416410 | 448060 | GB104027064258 | Wharfe from Hundwith Beck to River Washburn | River | 3318 | Middle Wharfe and Washburn | 3115 | Wharfe and Lower Ouse | WEST BECK | Not Applicable | Not Applicable | Not Applicable | 188:30 | 44 | 40.8 | 2020 | 100 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00178
YWS00179 | Yorkshire Water | Live | BRIDGE LANE SEWAGE PUMPING STATION | BRIDGE LANE/CSO | 27/19/0058 | 27/19/0058 | 1 | Storm discharge at pumping station | SE1128048060 | 411280 | 448060 | GB104027064257 | Wharfe from Barben Beck/River Dibb to Hundwith Beck | River | 3318 | Middle Wharfe and Washburn | 3115 | Wharfe and Lower Ouse | SPICEY GILL | Not Applicable | Wharfe at Cromwheel, Ilkley | Not Applicable | 0:00 | 0 | 5 | 2020 | 99.72 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00179
YWS00180 | Yorkshire Water | Live | STATION ROAD NO. 2 CSO | MENSTON CEMETERY/CSO | 27/19/0064 | EPR/ZB3390WE | A1 | SO on sewer network | SE1716044880 | 417154 | 444965 | GB104027064258 | Wharfe from Hundwith Beck to River Washburn | River | 3318 | Middle Wharfe and Washburn | 3115 | Wharfe and Lower Ouse | MICKLE ING BECK | Not Applicable | Not Applicable | Not Applicable | 158:30 | 55 | 35 | 2020 | 96.92 |  |  | High spill threshold not met | High spill threshold not met | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00180
YWS00181 | Yorkshire Water | Live | STATION ROAD NO. 2 CSO | STATION ROAD/NO 1 CSO | 27/19/0064 | EPR/ZB3391EQ | A1 | SO on sewer network | SE1716044880 | 417154 | 444965 | GB104027064258 | Wharfe from Hundwith Beck to River Washburn | River | 3318 | Middle Wharfe and Washburn | 3115 | Wharfe and Lower Ouse | MICKLE ING BECK | Not Applicable | Not Applicable | Not Applicable | 9:00 | 10 | 8 | 2020 | 88.12 | Comms failure / issue | Resolved - Nov | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00181
YWS00182 | Yorkshire Water | Live | STATION ROAD NO. 2 CSO | STATION ROAD/NO 2 CSO | 27/19/0064 | 27/19/0064 | A1 | SO on sewer network | SE1716044880 | 417154 | 444965 | GB104027064258 | Wharfe from Hundwith Beck to River Washburn | River | 3318 | Middle Wharfe and Washburn | 3115 | Wharfe and Lower Ouse | MICKLE ING BECK | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0.33 | 2020 | 72.76 | Comms failure / issue | Resolved - Apr | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00182
YWS00183 | Yorkshire Water | Live | STATION ROAD NO. 2 CSO | WESTBOURNE DRIVE/NO 1 CSO | 27/19/0064 | EPR/ZB3390VN | A1 | SO on sewer network | SE1716044880 | 417154 | 444965 | GB104027064258 | Wharfe from Hundwith Beck to River Washburn | River | 3318 | Middle Wharfe and Washburn | 3115 | Wharfe and Lower Ouse | MICKLE ING BECK | Not Applicable | Not Applicable | Not Applicable | 30:15 | 28 | 48.33 | 2022 | 98.54 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00183
YWS00184 | Yorkshire Water | Live | STATION ROAD NO. 2 CSO | WESTBOURNE DRIVE/NO 2 CSO | 27/19/0064 | EPR/ZB3390EY | A1 | SO on sewer network | SE1716044880 | 417154 | 444965 | GB104027064258 | Wharfe from Hundwith Beck to River Washburn | River | 3318 | Middle Wharfe and Washburn | 3115 | Wharfe and Lower Ouse | MICKLE ING BECK | Not Applicable | Not Applicable | Not Applicable | 18:30 | 17 | 10.8 | 2020 | 99.91 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00184
YWS00185 | Yorkshire Water | Live | GRASSINGTON SEWAGE TREATMENT WORKS | GRASSINGTON/STW | 27/19/0075 | 27/19/0075 | A2 | Inlet SO at WwTW | SE0063962941 | 400639 | 462941 | GB104027064253 | Wharfe from Park Gill Bk to Barben Beck/River Dibb | River | 3507 | Upper Wharfe | 3115 | Wharfe and Lower Ouse | RIVER WHARFE | Not Applicable | Wharfe at Cromwheel, Ilkley | Not Applicable | 54:45 | 36 | 69.2 | 2020 | 99.97 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00185
YWS00186 | Yorkshire Water | Live | KETTLEWELL STW | KETTLEWELL/STW | 27/19/0078 | 27/19/0078 | A2 | Storm tank at WwTW | SD9691071980 | 396910 | 471980 | GB104027064253 | Wharfe from Park Gill Bk to Barben Beck/River Dibb | River | 3507 | Upper Wharfe | 3115 | Wharfe and Lower Ouse | RIVER WHARFE | Not Applicable | Wharfe at Cromwheel, Ilkley | Not Applicable | 148:45 | 20 | 31.2 | 2020 | 99.97 |  |  | High spill threshold not met | High spill threshold not met | UWWTR investigation ongoing, Operational investigation completed | Operational improvement ongoing | SOAF investigation ongoing | YWS00186
YWS00187 | Yorkshire Water | Live | KETTLEWELL STW | KETTLEWELL/STW | 27/19/0078 | 27/19/0078 | A3 | Inlet SO at WwTW | SD9689072050 | 396890 | 472050 | GB104027064253 | Wharfe from Park Gill Bk to Barben Beck/River Dibb | River | 3507 | Upper Wharfe | 3115 | Wharfe and Lower Ouse | RIVER WHARFE | Not Applicable | Wharfe at Cromwheel, Ilkley | Not Applicable | 153:45 | 77 | 60.2 | 2020 | 99.96 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement ongoing | SOAF investigation ongoing | YWS00187
YWS00188 | Yorkshire Water | Live | DRAUGHTON WPC WORKS | DRAUGHTON PRIORS LANE/CSO | 27/19/0082 | 27/19/0082 | A2 | SO on sewer network | SE0460053100 | 404610 | 453102 | GB104027064030 | Hambleton Beck/Ings Bk Catch (trib of Wharfe) | River | 3318 | Middle Wharfe and Washburn | 3115 | Wharfe and Lower Ouse | INGS BECK | Not Applicable | Wharfe at Cromwheel, Ilkley | Not Applicable | 24:00 | 15 | 5.8 | 2020 | 99.63 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | SOAF investigation completed - Work required | YWS00188
YWS00189 | Yorkshire Water | Live | DRAUGHTON WPC WORKS | DRAUGHTON/STW/6XDWF OVERFLOW | 27/19/0082 | 27/19/0082 | A3 | Inlet SO at WwTW | SE0460053100 | 404610 | 453102 | GB104027064030 | Hambleton Beck/Ings Bk Catch (trib of Wharfe) | River | 3318 | Middle Wharfe and Washburn | 3115 | Wharfe and Lower Ouse | INGS BECK | Not Applicable | Wharfe at Cromwheel, Ilkley | Not Applicable | 325:30 | 47 | 15.75 | 2021 | 99.72 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00189
YWS00190 | Yorkshire Water | Live | HEBDEN WASTEWATER TREATMENT WORKS | HEBDEN/STW | 27/19/0083 | 27/19/0083 | A2 | Storm tank at WwTW | SE0269162177 | 402691 | 462177 | GB104027064253 | Wharfe from Park Gill Bk to Barben Beck/River Dibb | River | 3507 | Upper Wharfe | 3115 | Wharfe and Lower Ouse | RIVER WHARFE | Not Applicable | Wharfe at Cromwheel, Ilkley | Not Applicable | 367:40 | 50 | 35.4 | 2020 | 99.91 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00190
YWS00191 | Yorkshire Water | Live | LOW MILL LANE 179 CSO | LOW MILL LANE 179/CSO | 27/19/0092 | 27/19/0092 | 1 | SO on sewer network | SE0871049560 | 408718 | 449567 | GB104027064257 | Wharfe from Barben Beck/River Dibb to Hundwith Beck | River | 3318 | Middle Wharfe and Washburn | 3115 | Wharfe and Lower Ouse | TOWN BECK | Not Applicable | Wharfe at Cromwheel, Ilkley | Not Applicable | 5:30 | 5 | 7.6 | 2020 | 67.83 | Comms failure / issue | Resolved - Dec | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00191
YWS00192 | Yorkshire Water | Live | OTLEY SEWAGE TREATMENT WORKS | OTLEY/STW | 27/20/0046 | 27/20/0046 | A2 | Storm tank at WwTW | SE2103446058 | 421034 | 446058 | GB104027064258 | Wharfe from Hundwith Beck to River Washburn | River | 3318 | Middle Wharfe and Washburn | 3115 | Wharfe and Lower Ouse | RIVER WHARFE | Not Applicable | Not Applicable | Not Applicable | 661:30 | 85 | 70.6 | 2020 | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation ongoing | Operational improvement ongoing | SOAF investigation ongoing | YWS00192
YWS00193 | Yorkshire Water | Live | OTLEY SEWAGE TREATMENT WORKS | OTLEY/STW | 27/20/0046 | 27/20/0046 | A3 | Inlet SO at WwTW | SE2095046070 | 420950 | 446070 | GB104027064258 | Wharfe from Hundwith Beck to River Washburn | River | 3318 | Middle Wharfe and Washburn | 3115 | Wharfe and Lower Ouse | RIVER WHARFE | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 23.8 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00193
YWS00194 | Yorkshire Water | Live | CSO AT MILNER LANE | MILNER LANE/NO 2 CSO | 27/20/0051 | 27/20/0051 | 1 | SO on sewer network | SE3784041000 | 437841 | 440991 | GB104027063950 | Thorner Beck Catchment (trib of Wharfe) | River | 3287 | Lower Wharfe | 3115 | Wharfe and Lower Ouse | MILL BECK (WHARFE CATCHMENT) | Not Applicable | Not Applicable | Not Applicable | 1230:15 | 103 | 63.4 | 2020 | 99.98 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS00194
YWS00195 | Yorkshire Water | Live | WETHERBY SEWAGE TREATMENT WORKS | WETHERBY/STW | 27/20/0054 | 27/20/0054 | A2 | Storm tank at WwTW | SE4182047048 | 441747 | 446950 | GB104027064255 | Wharfe from Collingham Beck to Tadcaster Weir | River | 3287 | Lower Wharfe | 3115 | Wharfe and Lower Ouse | RIVER WHARFE | Not Applicable | Wharfe at Wilderness Carpark | Not Applicable | 230:15 | 46 | 58.6 | 2020 | 99.93 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00195
YWS00197 | Yorkshire Water | Live | WIGTON MOOR SEWAGE PUMPING STATION | ALWOODLEY/CSO | 27/20/0066 | 27/20/0066 | 2 | SO on sewer network | SE3180041350 | 431800 | 441350 | GB104027063960 | Stank Beck catchment (trib of Wharfe) | River | 3318 | Middle Wharfe and Washburn | 3115 | Wharfe and Lower Ouse | STURDY BECK | Not Applicable | Not Applicable | Not Applicable | 119:45 | 37 | 36.4 | 2020 | 93.04 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00197
YWS00198 | Yorkshire Water | Live | THORP ARCH SEWAGE TREATMENT WORKS | THORP ARCH/STW | 27/20/0068 | 27/20/0068 | A2 | Storm tank at WwTW | SE4511045840 | 445110 | 445840 | GB104027064255 | Wharfe from Collingham Beck to Tadcaster Weir | River | 3287 | Lower Wharfe | 3115 | Wharfe and Lower Ouse | ST HELENS DIKE | Not Applicable | Not Applicable | Not Applicable | 1291:30 | 156 | 56.6 | 2020 | 99.95 |  |  | Performance - Asset configuration (e.g. PS/rising main/storm tanks) | Performance - Asset configuration (e.g. PS/rising main/storm tanks) | UWWTR investigation ongoing, Operational investigation ongoing | Operational improvement ongoing | SOAF investigation ongoing | YWS00198
YWS00199 | Yorkshire Water | Live | POOL WPC WORKS | POOL/STW/3XDWF OVERFLOW | 27/20/0069 | 27/20/0069 | A2 | Storm tank at WwTW | SE2636045420 | 426360 | 445420 | GB104027064254 | Wharfe from R Washburn to Collingham Beck | River | 3318 | Middle Wharfe and Washburn | 3115 | Wharfe and Lower Ouse | RIVER WHARFE | Not Applicable | Not Applicable | Not Applicable | 647:45 | 100 | 114.4 | 2020 | 90.6 |  |  | Performance - Infiltration | Performance - Infiltration | UWWTR investigation ongoing, Operational investigation completed | Operational improvement completed | SOAF investigation ongoing | YWS00199
YWS00200 | Yorkshire Water | Live | POOL WPC WORKS | POOL/STW/6XDWF OVERFLOW | 27/20/0069 | 27/20/0069 | A3 | Inlet SO at WwTW | SE2636045420 | 426360 | 445420 | GB104027064254 | Wharfe from R Washburn to Collingham Beck | River | 3318 | Middle Wharfe and Washburn | 3115 | Wharfe and Lower Ouse | RIVER WHARFE | Not Applicable | Not Applicable | Not Applicable | 429:00 | 54 | 34.4 | 2020 | 99.98 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00200
YWS00201 | Yorkshire Water | Live | TADCASTER WPC WORKS | TADCASTER/DOMESTIC STW | 27/20/0073 | 27/20/0073 | 2 | Storm tank at WwTW | SE4949042450 | 449490 | 442450 | GB104027064256 | Wharfe from Tadcaster Weir to River Ouse | River | 3287 | Lower Wharfe | 3115 | Wharfe and Lower Ouse | RIVER WHARFE | Not Applicable | Not Applicable | Not Applicable | 266:45 | 29 | 14 | 2020 | 99.92 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00201
YWS00202 | Yorkshire Water | Live | WARREN LANE SPS | WARREN LANE OTLEY/CSO | 27/20/0079 | 27/20/0079 | 2 | SO on sewer network | SE2621044980 | 426210 | 444980 | GB104027064254 | Wharfe from R Washburn to Collingham Beck | River | 3318 | Middle Wharfe and Washburn | 3115 | Wharfe and Lower Ouse | TRIB OF THE WHARFE | Not Applicable | Not Applicable | Not Applicable | 23:45 | 10 | 19.2 | 2020 | 94.53 |  |  | High spill threshold not met | High spill threshold not met | Operational investigation completed | Operational improvement completed | No SOAF investigation required | YWS00202
YWS00203 | Yorkshire Water | Live | SHADWELL SEWAGE PUMPING STATION | SHADWELL/CSO | 27/20/0082 | 27/20/0082 | A2 | Storm discharge at pumping station | SE3531239811 | 435312 | 439811 | GB104027063970 | Collingham Bk Catchment (trib of Wharfe) | River | 3318 | Middle Wharfe and Washburn | 3115 | Wharfe and Lower Ouse | CULVERTED TRIB SCARCROFT BECK | Not Applicable | Not Applicable | Not Applicable | 116:30 | 64 | 54.2 | 2020 | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00203
YWS00204 | Yorkshire Water | Live | LANGWITH VALLEY SPS | LANGWITH VALLEY/CSO | 27/20/0083 | 27/20/0083 | 2 | Storm discharge at pumping station | SE3732045940 | 437320 | 445940 | GB104027064254 | Wharfe from R Washburn to Collingham Beck | River | 3318 | Middle Wharfe and Washburn | 3115 | Wharfe and Lower Ouse | WHARFE | Not Applicable | Wharfe at Wilderness Carpark | Not Applicable | 6:30 | 9 | 3.4 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00204
YWS00205 | Yorkshire Water | Live | BRIDGE HOUSE FARM CSO | BRIDGE HOUSE FARM/CSO | 27/20/0100 | 27/20/0100 | A1 | SO on sewer network | SE2919046770 | 429196 | 446766 | GB104027063990 | Weeton Beck catchment (trib of Wharfe) | River | 3318 | Middle Wharfe and Washburn | 3115 | Wharfe and Lower Ouse | WEETON BECK | Not Applicable | Not Applicable | Not Applicable | 353:45 | 50 | 51.8 | 2020 | 100 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00205
YWS00206 | Yorkshire Water | Live | WEST BUSK LANE NO 2 CSO | WEST BUSK LANE/NO 2 CSO | 27/20/0101 | 27/20/0101 | A1 | SO on sewer network | SE1902745345 | 419027 | 445345 | GB104027064258 | Wharfe from Hundwith Beck to River Washburn | River | 3318 | Middle Wharfe and Washburn | 3115 | Wharfe and Lower Ouse | RIVER WHARFE VIA PUBLIC SEWER | Not Applicable | Not Applicable | Not Applicable | 17:15 | 21 | 29.2 | 2020 | 98.25 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00206
YWS00207 | Yorkshire Water | Live | TADCASTER WEST CSO | TADCASTER WEST/CSO | 27/20/0112 | 27/20/0112 | A1 | SO on sewer network | SE4874443422 | 448744 | 443422 | GB104027064255 | Wharfe from Collingham Beck to Tadcaster Weir | River | 3287 | Lower Wharfe | 3115 | Wharfe and Lower Ouse | RIVER WHARFE | Not Applicable | Not Applicable | Not Applicable | 104:45 | 54 | 55.4 | 2020 | 100 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | Operational investigation completed | No improvement action in reporting period | SOAF investigation completed - No work required | YWS00207
YWS00208 | Yorkshire Water | Live | BRITANNIA INN CSO | TADCASTER EAST/CSO | 27/20/0113 | 27/20/0113 | A1 | SO on sewer network | SE4884043370 | 448772 | 443454 | GB104027064255 | Wharfe from Collingham Beck to Tadcaster Weir | River | 3287 | Lower Wharfe | 3115 | Wharfe and Lower Ouse | RIVER WHARFE | Not Applicable | Not Applicable | Not Applicable | 238:00 | 31 | 71.6 | 2020 | 100 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | Operational investigation completed | No improvement action in reporting period | SOAF investigation completed - Work required | YWS00208
YWS00209 | Yorkshire Water | Live | TADCASTER BRITTANIA CSO | TADCASTER BRITTANIA/CSO | 27/20/0114 | 27/20/0114 | A1 | SO on sewer network | SE4884943375 | 448849 | 443375 | GB104027064255 | Wharfe from Collingham Beck to Tadcaster Weir | River | 3287 | Lower Wharfe | 3115 | Wharfe and Lower Ouse | RIVER WHARFE | Not Applicable | Not Applicable | Not Applicable | 267:45 | 33 | 76.2 | 2020 | 99.87 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | Operational investigation completed | Operational improvement ongoing | SOAF investigation completed - Work required | YWS00209
YWS00210 | Yorkshire Water | Live | BARDSEY THE DRIVE CSO | BARDSEY THE DRIVE/CSO | 27/20/0115 | 27/20/0115 | A1 | SO on sewer network | SE3668744144 | 436687 | 444144 | GB104027063970 | Collingham Bk Catchment (trib of Wharfe) | River | 3318 | Middle Wharfe and Washburn | 3115 | Wharfe and Lower Ouse | BARDSEY BECK | Not Applicable | Not Applicable | Not Applicable | 38:00 | 15 | 12.4 | 2020 | 98.58 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00210
YWS00211 | Yorkshire Water | Live | HETCHELL VIEW CSO | HETCHELL VIEW/NO 2 CSO | 27/20/0117 | 27/20/0117 | 1 | SO on sewer network | SE3693042990 | 436932 | 442994 | GB104027063970 | Collingham Bk Catchment (trib of Wharfe) | River | 3318 | Middle Wharfe and Washburn | 3115 | Wharfe and Lower Ouse | BARDSEY BECK | Not Applicable | Not Applicable | Not Applicable | 1087:45 | 65 | 86.8 | 2020 | 100 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS00211
YWS00212 | Yorkshire Water | Live | MEADOW CLOSE CSO | MEADOW CLOSE/CSO | 27/20/0118 | 27/20/0118 | A1 | SO on sewer network | SE3696044720 | 436963 | 444719 | GB104027063970 | Collingham Bk Catchment (trib of Wharfe) | River | 3318 | Middle Wharfe and Washburn | 3115 | Wharfe and Lower Ouse | KESWICK BECK | Not Applicable | Not Applicable | Not Applicable | 124:15 | 30 | 52 | 2020 | 42.42 | Comms failure / issue | Resolved - Nov | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement ongoing | SOAF investigation ongoing | YWS00212
YWS00213 | Yorkshire Water | Live | KEARBY SEWAGE TREATMENT WORKS | KEARBY/STW | 27/20/0128 | 27/20/0128 | A2 | Storm tank at WwTW | SE3334246699 | 433342 | 446699 | GB104027064254 | Wharfe from R Washburn to Collingham Beck | River | 3318 | Middle Wharfe and Washburn | 3115 | Wharfe and Lower Ouse | RIVER WHARFE | Not Applicable | Not Applicable | Not Applicable | 305:15 | 38 | 42.8 | 2020 | 99.97 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00213
YWS00214 | Yorkshire Water | Live | WEETON SEWAGE TREATMENT WORKS | WEETON/STW | 27/20/0129 | 27/20/0129 | 2 | Storm tank at WwTW | SE2966046120 | 429660 | 446120 | GB104027064254 | Wharfe from R Washburn to Collingham Beck | River | 3318 | Middle Wharfe and Washburn | 3115 | Wharfe and Lower Ouse | RIVER WHARFE | Not Applicable | Not Applicable | Not Applicable | 2442:30 | 164 | 136 | 2020 | 99.98 |  |  | Performance - Infiltration | Performance - Infiltration | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS00214
YWS00215 | Yorkshire Water | Live | ARTHINGTON LANE CSO | ARTHINGTON LANE/CSO | 27/20/0130 | 27/20/0130 | A1 | SO on sewer network | SE2480045330 | 424810 | 445332 | GB104027064254 | Wharfe from R Washburn to Collingham Beck | River | 3318 | Middle Wharfe and Washburn | 3115 | Wharfe and Lower Ouse | RIVER WHARFE | Not Applicable | Not Applicable | Not Applicable | 51:00 | 20 | 24.6 | 2020 | 94.87 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00215
YWS00216 | Yorkshire Water | Live | ABERFORD SEWAGE TREATMENT WORKS | ABERFORD/STW | 27/20/0134 | 27/20/0134 | A2 | Inlet SO at WwTW | SE4366037780 | 443664 | 437781 | GB104027063940 | Cock Beck Catchment (trib of Wharfe) | River | 3287 | Lower Wharfe | 3115 | Wharfe and Lower Ouse | TRIBUTARY OF COCK BECK | Not Applicable | Not Applicable | Not Applicable | 6:30 | 16 | 16.8 | 2020 | 99.97 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00216
YWS00218 | Yorkshire Water | Live | WATTLE SYKE CSO | WATTLE SYKE/CSO | 27/20/0161 | 27/20/0161 | 1 | SO on sewer network | SE3944046420 | 439446 | 446425 | GB104027064255 | Wharfe from Collingham Beck to Tadcaster Weir | River | 3287 | Lower Wharfe | 3115 | Wharfe and Lower Ouse | RIVER WHARFE | Not Applicable | Wharfe at Wilderness Carpark | Not Applicable | 0:00 | 0 | 1.4 | 2020 | 86.45 | Comms failure / issue | Resolved - Apr | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00218
YWS00219 | Yorkshire Water | Live | WEDDERBURN SCHOOL CSO | WEDDERBURN SCHOOL/CSO | 27/21/0011 | 27/21/0011 | 1 | SO on sewer network | SE3216055270 | 432166 | 455275 | GB104027063741 | Crimple Beck from Source to Park Beck | River | 3308 | Middle and Lower Nidd | 3088 | Swale, Ure, Nidd and Upper Ouse | RUD BECK VIA A PUBLIC SEWER | Not Applicable | Not Applicable | Not Applicable | 12:30 | 11 | 5.2 | 2020 | 92.2 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00219
YWS00220 | Yorkshire Water | Live | SHERWOOD DRIVE CSO | SHERWOOD DRIVE/CSO | 27/21/0015 | 27/21/0015 | A1 | SO on sewer network | SE3333254976 | 433332 | 454976 | GB104027063741 | Crimple Beck from Source to Park Beck | River | 3308 | Middle and Lower Nidd | 3088 | Swale, Ure, Nidd and Upper Ouse | RUD BECK | Not Applicable | Not Applicable | Not Applicable | 288:45 | 60 | 29.5 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS00220
YWS00221 | Yorkshire Water | Live | HOOKSTONE ROAD CSO | HOOKSTONE ROAD/CSO | 27/21/0025 | 27/21/0025 | A1 | SO on sewer network | SE3149654091 | 431496 | 454091 | GB104027063741 | Crimple Beck from Source to Park Beck | River | 3308 | Middle and Lower Nidd | 3088 | Swale, Ure, Nidd and Upper Ouse | HOOKSTONE BECK | Not Applicable | Not Applicable | Not Applicable | 150:00 | 28 | 47 | 2020 | 100 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS00221
YWS00222 | Yorkshire Water | Live | BILTON LANE BECK CSO | BILTON LANE BECK/CSO | 27/21/0043 | 27/21/0043 | A1 | SO on sewer network | SE3129057770 | 431300 | 457772 | GB104027068297 | Nidd from Oak Beck to Low Bridge on Briggate (Knaresborough) | River | 3308 | Middle and Lower Nidd | 3088 | Swale, Ure, Nidd and Upper Ouse | BILTON BECK | Not Applicable | Not Applicable | Not Applicable | 67:45 | 32 | 31.2 | 2020 | 97 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00222
YWS00223 | Yorkshire Water | Live | HIRST BRIDGE - KILLINGHALL NO.1 | HIRST LANE/CSO | 27/21/0078 | 27/21/0078 | 2 | Storm discharge at pumping station | SE2459058610 | 424590 | 458610 | GB104027068296 | Nidd from Burstwith to Oak Beck | River | 3308 | Middle and Lower Nidd | 3088 | Swale, Ure, Nidd and Upper Ouse | TANG BECK | Not Applicable | Not Applicable | Not Applicable | 1369:00 | 95 | 92.8 | 2020 | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement completed | SOAF investigation ongoing | YWS00223
YWS00224 | Yorkshire Water | Live | BIRSTWITH NO2 SPS | BIRSTWITH/NO 2 CSO | 27/21/0083 | 27/21/0083 | A2 | Storm discharge at pumping station | SE2446459675 | 424464 | 459675 | GB104027068296 | Nidd from Burstwith to Oak Beck | River | 3308 | Middle and Lower Nidd | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER NIDD | Not Applicable | Not Applicable | Not Applicable | 84:15 | 20 | 41.4 | 2020 | 95.49 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation completed | No improvement action in reporting period | SOAF investigation completed - No work required | YWS00224
YWS00225 | Yorkshire Water | Live | PATELEY BRIDGE STW | PATELEY BRIDGE/STW | 27/21/0088 | 27/21/0088 | A2 | Storm tank at WwTW | SE1771064060 | 417710 | 464060 | GB104027068295 | Nidd from Ashfoldside Beck to Birstwith | River | 3497 | Upper Nidd | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER NIDD | Not Applicable | Not Applicable | Not Applicable | 2331:45 | 132 | 116.6 | 2020 | 100 |  |  | Performance - GW inundation | Performance - GW inundation | UWWTR investigation completed, Operational investigation completed | No improvement action in reporting period | SOAF investigation completed - No work required | YWS00225
YWS00226 | Yorkshire Water | Live | PATELEY BRIDGE STW | PATELEY BRIDGE/STW | 27/21/0088 | 27/21/0088 | A3 | Inlet SO at WwTW | SE1768064070 | 417680 | 464070 | GB104027068295 | Nidd from Ashfoldside Beck to Birstwith | River | 3497 | Upper Nidd | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER NIDD | Not Applicable | Not Applicable | Not Applicable | 16:45 | 7 | 45.33 | 2020 | 99.93 |  |  | High spill threshold not met | Performance - GW inundation | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00226
YWS00227 | Yorkshire Water | Live | SHAW MILLS SEWAGE TREATMENT WORKS | SHAW MILLS/STW | 27/21/0091 | 27/21/0091 | A2 | Storm tank at WwTW | SE2586062390 | 425860 | 462390 | GB104027063850 | Thornton Beck Catch (Trib of Nidd) | River | 3308 | Middle and Lower Nidd | 3088 | Swale, Ure, Nidd and Upper Ouse | THORNTON BECK | Not Applicable | Not Applicable | Not Applicable | 980:19 | 105 | 102.8 | 2020 | 99.96 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS00227
YWS00228 | Yorkshire Water | Live | SHAW MILLS SEWAGE TREATMENT WORKS | SHAW MILLS/STW | 27/21/0091 | 27/21/0091 | A3 | Inlet SO at WwTW | SE2586062410 | 425860 | 462410 | GB104027063850 | Thornton Beck Catch (Trib of Nidd) | River | 3308 | Middle and Lower Nidd | 3088 | Swale, Ure, Nidd and Upper Ouse | THORNTON BECK | Not Applicable | Not Applicable | Not Applicable | 421:30 | 74 | 96.6 | 2020 | 99.64 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS00228
YWS00229 | Yorkshire Water | Live | MARKINGTON STW | MARKINGTON/STW | 27/21/0114 | 27/21/0114 | A2 | Inlet SO at WwTW | SE2965065600 | 429630 | 465610 | GB104027064110 | Holbeck Catchment | River | 3309 | Middle and Lower Ure | 3088 | Swale, Ure, Nidd and Upper Ouse | A TRIBUTARY OF THE RIVER URE | Not Applicable | Not Applicable | Not Applicable | 535:45 | 56 | 58 | 2020 | 99.97 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00229
YWS00230 | Yorkshire Water | Live | SSO AT GOLDSBOROUGH | GOLDSBOROUGH/CSO | 27/21/0119 | 27/21/0119 | 1 | Storm discharge at pumping station | SE3890056100 | 438890 | 456130 | GB104027063770 | Gundrifs Beck (trib of Nidd) | River | 3308 | Middle and Lower Nidd | 3088 | Swale, Ure, Nidd and Upper Ouse | NEW CUT | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0 | 2020 | 9.72 | Sensor failure / issue | Resolved - Nov | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00230
YWS00231 | Yorkshire Water | Live | ABBEY ROAD NO 2 CSO | ABBEY ROAD/NO 2 CSO | 27/21/0123 | 27/21/0123 | A1 | SO on sewer network | SE3512356374 | 435123 | 456374 | GB104027068297 | Nidd from Oak Beck to Low Bridge on Briggate (Knaresborough) | River | 3308 | Middle and Lower Nidd | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER NIDD | Not Applicable | Nidd at the Lido, Knaresborough | Not Applicable | 25:30 | 20 | 10.4 | 2020 | 99.72 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00231
YWS00232 | Yorkshire Water | Live | ALMSFORD AVENUE CSO | ALMSFORD AVENUE/CSO | 27/21/0127 | 27/21/0127 | A1 | SO on sewer network | SE3166252963 | 431662 | 452963 | GB104027063741 | Crimple Beck from Source to Park Beck | River | 3308 | Middle and Lower Nidd | 3088 | Swale, Ure, Nidd and Upper Ouse | TRIB OF CRIMPLE BECK | Not Applicable | Not Applicable | Not Applicable | 111:30 | 42 | 48.2 | 2020 | 99.89 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00232
YWS00233 | Yorkshire Water | Live | FOLLIFOOT SEWAGE PUMPING STATION | FOLLIFOOT/CSO | 27/21/0136 | 27/21/0136 | A2 | Storm discharge at pumping station | SE3483252592 | 434832 | 452592 | GB104027063741 | Crimple Beck from Source to Park Beck | River | 3308 | Middle and Lower Nidd | 3088 | Swale, Ure, Nidd and Upper Ouse | HORSE POND BECK | Not Applicable | Not Applicable | Not Applicable | 4:45 | 4 | 5.8 | 2020 | 99.8 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00233
YWS00234 | Yorkshire Water | Live | KIRK HAMMERTON STW | KIRK HAMMERTON/STW | 27/21/0139 | 27/21/0139 | A2 | Storm tank at WwTW | SE4759055460 | 447590 | 455460 | GB104027068292 | Nidd from Crimple Beck to River Ouse | River | 3308 | Middle and Lower Nidd | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER NIDD | Not Applicable | Not Applicable | Not Applicable | 606:30 | 67 | 56.8 | 2020 | 99.62 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00234
YWS00235 | Yorkshire Water | Live | KIRK HAMMERTON STW | KIRK HAMMERTON/STW | 27/21/0139 | 27/21/0139 | A3 | Inlet SO at WwTW | SE4759055460 | 447590 | 455460 | GB104027068292 | Nidd from Crimple Beck to River Ouse | River | 3308 | Middle and Lower Nidd | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER NIDD | Not Applicable | Not Applicable | Not Applicable | 112:45 | 32 | 53 | 2020 | 99.34 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00235
YWS00236 | Yorkshire Water | Live | MOOR MONKTON EAST SPS | MOOR MONKTON EAST/CSO | 27/21/0141 | 27/21/0141 | A2 | Storm discharge at pumping station | SE5119657007 | 451196 | 457007 | GB104027068292 | Nidd from Crimple Beck to River Ouse | River | 3308 | Middle and Lower Nidd | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER NIDD | Not Applicable | Not Applicable | Not Applicable | 1:22 | 7 | 5.8 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00236
YWS00237 | Yorkshire Water | Live | NUN MONKTON SEWAGE TREATMENT WORKS | NUN MONKTON/STW | 27/21/0142 | 27/21/0142 | 2 | Inlet SO at WwTW | SE5119057580 | 451190 | 457580 | GB104027068292 | Nidd from Crimple Beck to River Ouse | River | 3308 | Middle and Lower Nidd | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER NIDD | Not Applicable | Not Applicable | Not Applicable | 569:45 | 71 | 60 | 2020 | 99.95 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00237
YWS00238 | Yorkshire Water | Live | CRIMPLE LANE CSO | CRIMPLE LANE/NO 2 CSO | 27/21/0143 | 27/21/0143 | A1 | SO on sewer network | SE3340954046 | 433409 | 454046 | GB104027063741 | Crimple Beck from Source to Park Beck | River | 3308 | Middle and Lower Nidd | 3088 | Swale, Ure, Nidd and Upper Ouse | CRIMPLE BECK | Not Applicable | Not Applicable | Not Applicable | 324:30 | 56 | 54.2 | 2020 | 96.19 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00238
YWS00239 | Yorkshire Water | Live | FULWITHMILL FARM N0 2 CSO | FULWITHMILL FARM/NO 2 CSO | 27/21/0144 | 27/21/0144 | A1 | SO on sewer network | SE3176652688 | 431766 | 452688 | GB104027063741 | Crimple Beck from Source to Park Beck | River | 3308 | Middle and Lower Nidd | 3088 | Swale, Ure, Nidd and Upper Ouse | CRIMPLE BECK | Not Applicable | Not Applicable | Not Applicable | 136:30 | 29 | 5.8 | 2020 | 99.91 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00239
YWS00240 | Yorkshire Water | Live | HOOKSTONE DRIVE NO 2 CSO | HOOKSTONE DRIVE/NO 2 CSO | 27/21/0145 | 27/21/0145 | A1 | SO on sewer network | SE3333154973 | 433331 | 454973 | GB104027063741 | Crimple Beck from Source to Park Beck | River | 3308 | Middle and Lower Nidd | 3088 | Swale, Ure, Nidd and Upper Ouse | CULVERTED RUD BECK/PUBLICSEWER | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0.2 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00240
YWS00241 | Yorkshire Water | Live | FOREST LANE CSO | FOREST LANE/NO 2 CSO | 27/21/0149 | 27/21/0149 | 1 | SO on sewer network | SE3353055270 | 433532 | 455267 | GB104027063741 | Crimple Beck from Source to Park Beck | River | 3308 | Middle and Lower Nidd | 3088 | Swale, Ure, Nidd and Upper Ouse | CULVERTED STAR BECK | Not Applicable | Not Applicable | Not Applicable | 26:45 | 18 | 9 | 2020 | 99.98 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00241
YWS00242 | Yorkshire Water | Live | HOOKSTONE GRANGE WAY CSO | HOOKSTONE GRANGE WAY/CSO | 27/21/0151 | 27/21/0151 | A1 | SO on sewer network | SE3301155120 | 433331 | 454973 | GB104027063741 | Crimple Beck from Source to Park Beck | River | 3308 | Middle and Lower Nidd | 3088 | Swale, Ure, Nidd and Upper Ouse | RUD BECK VIA PUBLIC SEWER | Not Applicable | Not Applicable | Not Applicable | 3:00 | 6 | 3.2 | 2020 | 96.28 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00242
YWS00243 | Yorkshire Water | Live | GREENFIELDS ROAD NO3 CSO | GREENFIELDS ROAD/NO 3 CSO | 27/21/0152 | 27/21/0152 | A1 | SO on sewer network | SE3333154973 | 433331 | 454973 | GB104027063741 | Crimple Beck from Source to Park Beck | River | 3308 | Middle and Lower Nidd | 3088 | Swale, Ure, Nidd and Upper Ouse | RUD BECK VIA A PUBLIC SEWER | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0.6 | 2020 | 99.93 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00243
YWS00244 | Yorkshire Water | Live | TOCKWITH TREATMENT WORKS | TOCKWITH/STW | 27/21/0159 | 27/21/0159 | 2 | Storm tank at WwTW | SE4657053630 | 446570 | 453620 | GB104027068292 | Nidd from Crimple Beck to River Ouse | River | 3308 | Middle and Lower Nidd | 3088 | Swale, Ure, Nidd and Upper Ouse | FLEET BECK | Not Applicable | Not Applicable | Not Applicable | 656:30 | 51 | 44.2 | 2020 | 99.99 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00244
YWS00245 | Yorkshire Water | Live | CATTAL SEWAGE TREATMENT WORKS | CATTAL/STW | 27/21/0166 | 27/21/0166 | 2 | Inlet SO at WwTW | SE4465053990 | 444650 | 453990 | GB104027068292 | Nidd from Crimple Beck to River Ouse | River | 3308 | Middle and Lower Nidd | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER NIDD | Not Applicable | Not Applicable | Not Applicable | 202:00 | 32 | 30.6 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00245
YWS00246 | Yorkshire Water | Live | NORTH DEIGHTON STW | NORTH DEIGHTON/STW | 27/21/0169 | 27/21/0169 | A2 | Storm tank at WwTW | SE3977053250 | 439772 | 453250 | GB104027068298 | Nidd from Low Bridge on Briggate (Knaresborough) to Crimple Beck | River | 3308 | Middle and Lower Nidd | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER NIDD | Not Applicable | Not Applicable | Not Applicable | 2861:45 | 153 | 104.4 | 2020 | 99.99 |  |  | Performance - Infiltration | Performance - Infiltration | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS00246
YWS00247 | Yorkshire Water | Live | RIPLEY NO2 CSO | RIPLEY/NO 2 CSO | 27/21/0170 | 27/21/0170 | A1 | SO on sewer network | SE2825059975 | 428250 | 459975 | GB104027063850 | Thornton Beck Catch (Trib of Nidd) | River | 3308 | Middle and Lower Nidd | 3088 | Swale, Ure, Nidd and Upper Ouse | RIPLEY BECK | Not Applicable | Not Applicable | Not Applicable | 7:30 | 11 | 2.6 | 2020 | 97.78 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00247
YWS00248 | Yorkshire Water | Live | KILLINGHALL NO 2 CSO | KILLINGHALL/NO 2 CSO | 27/21/0173 | 27/21/0173 | A1 | SO on sewer network | SE2852059160 | 428520 | 459160 | GB104027068296 | Nidd from Burstwith to Oak Beck | River | 3308 | Middle and Lower Nidd | 3088 | Swale, Ure, Nidd and Upper Ouse | UNNAMED TRIB OF NIDD | Not Applicable | Not Applicable | Not Applicable | 62:30 | 19 | 19.4 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00248
YWS00249 | Yorkshire Water | Live | DARLEY SEWAGE TREATMENT WORKS | DARLEY/STW | 27/21/0205 | 27/21/0205 | A2 | Storm tank at WwTW | SE2118259656 | 421182 | 459656 | GB104027068295 | Nidd from Ashfoldside Beck to Birstwith | River | 3497 | Upper Nidd | 3088 | Swale, Ure, Nidd and Upper Ouse | TRIB OF RIVER NIDD | Not Applicable | Not Applicable | Not Applicable | 2260:00 | 146 | 112.2 | 2020 | 99.97 |  |  | Performance - GW inundation | Performance - GW inundation | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS00249
YWS00250 | Yorkshire Water | Live | DARLEY SEWAGE TREATMENT WORKS | DARLEY/STW | 27/21/0205 | 27/21/0205 | A3 | Inlet SO at WwTW | SE2118259656 | 421182 | 459656 | GB104027068295 | Nidd from Ashfoldside Beck to Birstwith | River | 3497 | Upper Nidd | 3088 | Swale, Ure, Nidd and Upper Ouse | TRIB OF RIVER NIDD | Not Applicable | Not Applicable | Not Applicable | 926:00 | 86 | 63.8 | 2020 | 99.89 |  |  | Performance - GW inundation | Performance - GW inundation | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00250
YWS00251 | Yorkshire Water | Live | 35 SKIPTON ROAD CSO | SKIPTON ROAD 179/CSO | 27/21/0207 | 27/21/0207 | 1 | SO on sewer network | SE2943056901 | 429433 | 456908 | GB104027063760 | Oak Beck Catchment (Trib of Nidd) | River | 3308 | Middle and Lower Nidd | 3088 | Swale, Ure, Nidd and Upper Ouse | OAK BECK VIA PUBLIC SEWER | Not Applicable | Not Applicable | Not Applicable | 3:15 | 7 | 4.75 | 2020 | 99.82 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00251
YWS00252 | Yorkshire Water | Live | UNITY GROVE CSO | UNITY GROVE/CSO | 27/21/0208 | 27/21/0208 | A1 | SO on sewer network | SE2943356908 | 429433 | 456908 | GB104027063760 | Oak Beck Catchment (Trib of Nidd) | River | 3308 | Middle and Lower Nidd | 3088 | Swale, Ure, Nidd and Upper Ouse | OAK BECK VIA PUBLIC SEWER | Not Applicable | Not Applicable | Not Applicable | 3:45 | 8 | 4.6 | 2020 | 87.38 | Comms failure / issue | Resolved - Jul | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00252
YWS00253 | Yorkshire Water | Live | 33 SKIPTON ROAD CSO | SKIPTON ROAD 33/CSO | 27/21/0209 | 27/21/0209 | 1 | SO on sewer network | SE2943056903 | 429433 | 456908 | GB104027063760 | Oak Beck Catchment (Trib of Nidd) | River | 3308 | Middle and Lower Nidd | 3088 | Swale, Ure, Nidd and Upper Ouse | OAK BECK VIA A PUBLIC SEWER | Not Applicable | Not Applicable | Not Applicable | 2:30 | 6 | 1.4 | 2020 | 43.94 | Comms failure / issue | Resolved - Oct | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00253
YWS00254 | Yorkshire Water | Live | 83 SKIPTON ROAD CSO | SKIPTON ROAD 83/CSO | 27/21/0210 | 27/21/0210 | A1 | SO on sewer network | SE2943356908 | 429433 | 456908 | GB104027063760 | Oak Beck Catchment (Trib of Nidd) | River | 3308 | Middle and Lower Nidd | 3088 | Swale, Ure, Nidd and Upper Ouse | OAK BECK VIA A PUBLIC SEWER | Not Applicable | Not Applicable | Not Applicable | 0:15 | 1 | 0.6 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00254
YWS00255 | Yorkshire Water | Live | SKIPTON ROAD 109 CSP | SKIPTON ROAD 109/CSO | 27/21/0211 | 27/21/0211 | A1 | SO on sewer network | SE2943056905 | 429433 | 456908 | GB104027063760 | Oak Beck Catchment (Trib of Nidd) | River | 3308 | Middle and Lower Nidd | 3088 | Swale, Ure, Nidd and Upper Ouse | OAK BECK VIA A PUBLIC SEWER | Not Applicable | Not Applicable | Not Applicable | 6:00 | 11 | 10.8 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00255
YWS00256 | Yorkshire Water | Live | HARROGATE HYDRO CSOS | JENNY PLAIN BRIDGE/CSO | 27/21/0216 | 27/21/0216 | 10 | SO on sewer network | SE2968056430 | 429680 | 456430 | GB104027063760 | Oak Beck Catchment (Trib of Nidd) | River | 3308 | Middle and Lower Nidd | 3088 | Swale, Ure, Nidd and Upper Ouse | OAK BECK AND COPPICE BECK | Not Applicable | Not Applicable | Not Applicable | 30:15 | 21 | 24.2 | 2020 | 80.36 | Comms failure / issue | Resolved - Mar | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00256
YWS00257 | Yorkshire Water | Live | HARROGATE HYDRO CSOS | ST MARYS WALK 30/CSO | 27/21/0216 | 27/21/0216 | 11 | SO on sewer network | SE2995055070 | 429952 | 455077 | GB104027063741 | Crimple Beck from Source to Park Beck | River | 3308 | Middle and Lower Nidd | 3088 | Swale, Ure, Nidd and Upper Ouse | OAK BECK AND COPPICE BECK | Not Applicable | Not Applicable | Not Applicable | 39:45 | 20 | 21.4 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00257
YWS00258 | Yorkshire Water | Live | HARROGATE HYDRO CSOS | ST MARYS WALK 29/CSO | 27/21/0216 | 27/21/0216 | 12 | SO on sewer network | SE2995055110 | 429950 | 455111 | GB104027063760 | Oak Beck Catchment (Trib of Nidd) | River | 3308 | Middle and Lower Nidd | 3088 | Swale, Ure, Nidd and Upper Ouse | OAK BECK AND COPPICE BECK | Not Applicable | Not Applicable | Not Applicable | 93:45 | 40 | 55.8 | 2020 | 99.96 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00258
YWS00259 | Yorkshire Water | Live | HARROGATE HYDRO CSOS | ST MARYS WALK XXX/CSO | 27/21/0216 | 27/21/0216 | 13 | SO on sewer network | SE2995055220 | 429957 | 455221 | GB104027063760 | Oak Beck Catchment (Trib of Nidd) | River | 3308 | Middle and Lower Nidd | 3088 | Swale, Ure, Nidd and Upper Ouse | OAK BECK AND COPPICE BECK | Not Applicable | Not Applicable | Not Applicable | 202:45 | 86 | 100.4 | 2020 | 100 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00259
YWS00260 | Yorkshire Water | Live | HARROGATE HYDRO CSOS | HOTEL MAJESTIC/CSO | 27/21/0216 | 27/21/0216 | 14 | SO on sewer network | SE3007055660 | 430070 | 455660 | GB104027063760 | Oak Beck Catchment (Trib of Nidd) | River | 3308 | Middle and Lower Nidd | 3088 | Swale, Ure, Nidd and Upper Ouse | OAK BECK AND COPPICE BECK | Not Applicable | Not Applicable | Not Applicable | 85:15 | 31 | 9.8 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00260
YWS00261 | Yorkshire Water | Live | HARROGATE HYDRO CSOS | ST MARYS WALK 7/CSO | 27/21/0216 | 27/21/0216 | 15 | SO on sewer network | SE2995055220 | 429882 | 454897 | GB104027063741 | Crimple Beck from Source to Park Beck | River | 3308 | Middle and Lower Nidd | 3088 | Swale, Ure, Nidd and Upper Ouse | OAK BECK AND COPPICE BECK | Not Applicable | Not Applicable | Not Applicable | 18:30 | 17 | 15.2 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00261
YWS00262 | Yorkshire Water | Live | HARROGATE HYDRO CSOS | COLD BATH ROAD/CSO | 27/21/0216 | 27/21/0216 | 16 | SO on sewer network | SE2995055220 | 429956 | 455222 | GB104027063760 | Oak Beck Catchment (Trib of Nidd) | River | 3308 | Middle and Lower Nidd | 3088 | Swale, Ure, Nidd and Upper Ouse | OAK BECK AND COPPICE BECK | Not Applicable | Not Applicable | Not Applicable | 0:15 | 1 | 0.6 | 2020 | 91.64 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00262
YWS00263 | Yorkshire Water | Live | HARROGATE HYDRO CSOS | KINGS ROAD/CSO | 27/21/0216 | 27/21/0216 | 2 | SO on sewer network | SE2995055220 | 430014 | 455637 | GB104027063760 | Oak Beck Catchment (Trib of Nidd) | River | 3308 | Middle and Lower Nidd | 3088 | Swale, Ure, Nidd and Upper Ouse | OAK BECK AND COPPICE BECK | Not Applicable | Not Applicable | Not Applicable | 0:45 | 3 | 1.6 | 2020 | 99.76 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00263
YWS00264 | Yorkshire Water | Live | HARROGATE HYDRO CSOS | MONTPELLIER RD27/CSO | 27/21/0216 | 27/21/0216 | 3 | SO on sewer network | SE2995055270 | 429953 | 455272 | GB104027063760 | Oak Beck Catchment (Trib of Nidd) | River | 3308 | Middle and Lower Nidd | 3088 | Swale, Ure, Nidd and Upper Ouse | OAK BECK AND COPPICE BECK | Not Applicable | Not Applicable | Not Applicable |  |  | 4.5 | 2020 | 0 | Sensor failure / issue | Scheduled | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00264
YWS00265 | Yorkshire Water | Live | HARROGATE HYDRO CSOS | CHUDLEIGH ROAD/CSO | 27/21/0216 | 27/21/0216 | 4 | SO on sewer network | SE3039055650 | 430392 | 455659 | GB104027063760 | Oak Beck Catchment (Trib of Nidd) | River | 3308 | Middle and Lower Nidd | 3088 | Swale, Ure, Nidd and Upper Ouse | OAK BECK AND COPPICE BECK | Not Applicable | Not Applicable | Not Applicable | 5:15 | 13 | 6.8 | 2020 | 93.33 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00265
YWS00266 | Yorkshire Water | Live | HARROGATE HYDRO CSOS | CAMBRIDGE STREET/CSO | 27/21/0216 | 27/21/0216 | 5 | SO on sewer network | SE2995055550 | 429956 | 455559 | GB104027063760 | Oak Beck Catchment (Trib of Nidd) | River | 3308 | Middle and Lower Nidd | 3088 | Swale, Ure, Nidd and Upper Ouse | OAK BECK AND COPPICE BECK | Not Applicable | Not Applicable | Not Applicable | 16:30 | 24 | 33.4 | 2020 | 99.9 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00266
YWS00267 | Yorkshire Water | Live | HARROGATE HYDRO CSOS | WEST PARK/CSO | 27/21/0216 | 27/21/0216 | 6 | SO on sewer network | SE2995055240 | 429954 | 455248 | GB104027063760 | Oak Beck Catchment (Trib of Nidd) | River | 3308 | Middle and Lower Nidd | 3088 | Swale, Ure, Nidd and Upper Ouse | OAK BECK AND COPPICE BECK | Not Applicable | Not Applicable | Not Applicable | 2:30 | 6 | 4.6 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00267
YWS00268 | Yorkshire Water | Live | HARROGATE HYDRO CSOS | ALBERT STREET/CSO | 27/21/0216 | 27/21/0216 | 7 | SO on sewer network | SE2995055240 | 429954 | 455248 | GB104027063760 | Oak Beck Catchment (Trib of Nidd) | River | 3308 | Middle and Lower Nidd | 3088 | Swale, Ure, Nidd and Upper Ouse | OAK BECK AND COPPICE BECK | Not Applicable | Not Applicable | Not Applicable | 57:15 | 41 | 50 | 2020 | 99.94 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00268
YWS00269 | Yorkshire Water | Live | HARROGATE HYDRO CSOS | STRAWBERRY DALE/CSO | 27/21/0216 | 27/21/0216 | 8 | SO on sewer network | SE3013055730 | 430130 | 455733 | GB104027063760 | Oak Beck Catchment (Trib of Nidd) | River | 3308 | Middle and Lower Nidd | 3088 | Swale, Ure, Nidd and Upper Ouse | OAK BECK AND COPPICE BECK | Not Applicable | Not Applicable | Not Applicable | 53:30 | 43 | 48.4 | 2020 | 100 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00269
YWS00270 | Yorkshire Water | Live | HARROGATE HYDRO CSOS | HYDE PARK ROAD/CSO | 27/21/0216 | 27/21/0216 | 9 | SO on sewer network | SE2995055220 | 430392 | 455659 | GB104027063760 | Oak Beck Catchment (Trib of Nidd) | River | 3308 | Middle and Lower Nidd | 3088 | Swale, Ure, Nidd and Upper Ouse | OAK BECK AND COPPICE BECK | Not Applicable | Not Applicable | Not Applicable | 9:00 | 15 | 5.8 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00270
YWS00271 | Yorkshire Water | Live | FIELD 4200 CSO | FIELD 4200 WHIXLEY/CSO | 27/21/0255 | 27/21/0255 | 1 | SO on sewer network | SE4443057980 | 444430 | 457980 | GB104027068292 | Nidd from Crimple Beck to River Ouse | River | 3308 | Middle and Lower Nidd | 3088 | Swale, Ure, Nidd and Upper Ouse | WHIXLEY CUT | Not Applicable | Not Applicable | Not Applicable | 20:45 | 20 | 17.8 | 2020 | 92.93 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00271
YWS00272 | Yorkshire Water | Live | EASTFIELD FARM CSO | EASTFIELD FARM/CSO | 27/21/0256 | 27/21/0256 | A1 | SO on sewer network | SE3658851114 | 436588 | 451114 | GB104027063742 | Crimple Beck from Park Beck to River Nidd | River | 3308 | Middle and Lower Nidd | 3088 | Swale, Ure, Nidd and Upper Ouse | CRIMPLE BECK OR RIVER CRIMPLE | Not Applicable | Not Applicable | Not Applicable | 7:30 | 11 | 8.2 | 2020 | 95.94 |  |  | High spill threshold not met | High spill threshold not met | Operational investigation ongoing | Operational improvement ongoing | No SOAF investigation required | YWS00272
YWS00273 | Yorkshire Water | Live | WATERSIDE 47 CSO | WATERSIDE 47/CSO | 27/21/0259 | 27/21/0259 | A1 | SO on sewer network | SE3474156787 | 434741 | 456787 | GB104027068297 | Nidd from Oak Beck to Low Bridge on Briggate (Knaresborough) | River | 3308 | Middle and Lower Nidd | 3088 | Swale, Ure, Nidd and Upper Ouse | MILL STREAM | Not Applicable | Nidd at the Lido, Knaresborough | Not Applicable | 46:15 | 23 | 20 | 2020 | 99.74 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00273
YWS00274 | Yorkshire Water | Live | WATERSIDE 48 CSO | WATERSIDE 48/CSO | 27/21/0260 | 27/21/0260 | A1 | SO on sewer network | SE3470756706 | 434707 | 456706 | GB104027068297 | Nidd from Oak Beck to Low Bridge on Briggate (Knaresborough) | River | 3308 | Middle and Lower Nidd | 3088 | Swale, Ure, Nidd and Upper Ouse | MILL STREAM | Not Applicable | Nidd at the Lido, Knaresborough | Not Applicable | 138:00 | 43 | 37 | 2020 | 78.4 | Sensor failure / issue | Resolved - Nov | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00274
YWS00275 | Yorkshire Water | Live | WATERSIDE 49 CSO | WATERSIDE 49/CSO | 27/21/0261 | 27/21/0261 | A1 | SO on sewer network | SE3457557131 | 434575 | 457131 | GB104027068297 | Nidd from Oak Beck to Low Bridge on Briggate (Knaresborough) | River | 3308 | Middle and Lower Nidd | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER NIDD | Not Applicable | Nidd at the Lido, Knaresborough | Not Applicable | 27:15 | 17 | 13.2 | 2020 | 99.54 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00275
YWS00276 | Yorkshire Water | Live | BOROUGHBRIDGE ROAD CSO | BOROUGHBRIDGE ROAD/CSO | 27/21/0262 | 27/21/0262 | 1 | SO on sewer network | SE3483057400 | 434838 | 457409 | GB104027068297 | Nidd from Oak Beck to Low Bridge on Briggate (Knaresborough) | River | 3308 | Middle and Lower Nidd | 3088 | Swale, Ure, Nidd and Upper Ouse | FROGMIRE DYKE | Not Applicable | Nidd at the Lido, Knaresborough | Not Applicable | 3:15 | 10 | 8.6 | 2020 | 99.63 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00276
YWS00277 | Yorkshire Water | Live | CRAGG TOP COMBINED SEWER OVERFLOW | CRAGG TOP/CSO | 27/21/0263 | 27/21/0263 | 1 | SO on sewer network | SE3513056250 | 435134 | 456258 | GB104027068297 | Nidd from Oak Beck to Low Bridge on Briggate (Knaresborough) | River | 3308 | Middle and Lower Nidd | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER NIDD | Not Applicable | Nidd at the Lido, Knaresborough | Not Applicable | 5:00 | 13 | 13.8 | 2020 | 98.32 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00277
YWS00278 | Yorkshire Water | Live | ABBEY MILL CSO | ABBEY MILL/CSO | 27/21/0264 | 27/21/0264 | A1 | SO on sewer network | SE3601055960 | 436015 | 455962 | GB104027068298 | Nidd from Low Bridge on Briggate (Knaresborough) to Crimple Beck | River | 3308 | Middle and Lower Nidd | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER NIDD | Not Applicable | Nidd at the Lido, Knaresborough | Not Applicable | 0:00 | 0 | 1.4 | 2020 | 97.01 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00278
YWS00279 | Yorkshire Water | Live | SPITAL CROFT CSO | SPITAL CROFT/CSO | 27/21/0265 | 27/21/0265 | A1 | SO on sewer network | SE3511656231 | 435116 | 456231 | GB104027068298 | Nidd from Low Bridge on Briggate (Knaresborough) to Crimple Beck | River | 3308 | Middle and Lower Nidd | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER NIDD | Not Applicable | Nidd at the Lido, Knaresborough | Not Applicable | 167:00 | 26 | 28.2 | 2020 | 93.71 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00279
YWS00280 | Yorkshire Water | Live | KIRKBY MALZEARD STW | KIRKBY MALZEARD/STW | 27/22/0048 | 27/22/0048 | A2 | Storm tank at WwTW | SE2470074200 | 424702 | 474147 | GB104027069260 | Kex Beck and the Laver | River | 3309 | Middle and Lower Ure | 3088 | Swale, Ure, Nidd and Upper Ouse | KEX BECK | Not Applicable | Not Applicable | Not Applicable | 168:30 | 54 | 58.8 | 2020 | 100 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS00280
YWS00281 | Yorkshire Water | Live | RIPON WPC WORKS | RIPON/STW | 27/22/0052 | 27/22/0052 | A2 | Storm tank at WwTW | SE3241570792 | 432415 | 470792 | GB104027064140 | Skell from River Laver to River Ure | River | 3309 | Middle and Lower Ure | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER URE | Not Applicable | Not Applicable | Not Applicable | 601:24 | 58 | 62.4 | 2020 | 99.95 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00281
YWS00282 | Yorkshire Water | Live | RIPON WPC WORKS | RIPON/STW | 27/22/0052 | 27/22/0052 | A3 | Inlet SO at WwTW | SE3237070810 | 432378 | 470818 | GB104027064140 | Skell from River Laver to River Ure | River | 3309 | Middle and Lower Ure | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER URE | Not Applicable | Not Applicable | Not Applicable | 152:04 | 46 | 14.75 | 2020 | 99.95 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00282
YWS00283 | Yorkshire Water | Live | GREWELTHORPE/GALPHAY/LAVERTON SCH | GREWELTHORPE/CSO | 27/22/0059 | 27/22/0059 | 2 | SO on sewer network | SE2310076100 | 423780 | 475850 | GB104027069260 | Kex Beck and the Laver | River | 3309 | Middle and Lower Ure | 3088 | Swale, Ure, Nidd and Upper Ouse | TRANMIRE GOIT | Not Applicable | Not Applicable | Not Applicable | 247:30 | 74 | 58.6 | 2020 | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS00283
YWS00284 | Yorkshire Water | Live | SKELTON ON URE WPC WORKS | SKELTON/STW/3XDWF OVERFLOW | 27/22/0060 | 27/22/0060 | A2 | Storm tank at WwTW | SE3550068600 | 435730 | 468450 | GB104027064161 | Ure from River Skell to River Tutt | River | 3309 | Middle and Lower Ure | 3088 | Swale, Ure, Nidd and Upper Ouse | SCOUR GUTTER | Not Applicable | Not Applicable | Not Applicable | 1910:00 | 146 | 132.4 | 2020 | 99.93 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS00284
YWS00285 | Yorkshire Water | Live | SKELTON ON URE WPC WORKS | SKELTON/STW/6XDWF OVERFLOW | 27/22/0060 | 27/22/0060 | A3 | Inlet SO at WwTW | SE3550068600 | 435560 | 468550 | GB104027064161 | Ure from River Skell to River Tutt | River | 3309 | Middle and Lower Ure | 3088 | Swale, Ure, Nidd and Upper Ouse | SCOUR GUTTER | Not Applicable | Not Applicable | Not Applicable | 1146:30 | 106 | 78.6 | 2020 | 98.99 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS00285
YWS00286 | Yorkshire Water | Live | ASKRIGG SEWAGE TREATMENT WORKS | ASKRIGG/STW | 27/22/0062 | 27/22/0062 | 2 | Inlet SO at WwTW | SD9460090470 | 394600 | 490470 | GB104027069480 | Coghill Beck Catch (trib of Ure) | River | 3505 | Upper Ure | 3088 | Swale, Ure, Nidd and Upper Ouse | PADDOCK BECK | Not Applicable | Not Applicable | Not Applicable | 55:00 | 24 | 15.8 | 2020 | 99.98 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00286
YWS00287 | Yorkshire Water | Live | MASHAM SEWAGE TREATMENT WORKS | MASHAM/STW | 27/22/0063 | 27/22/0063 | 2 | Storm tank at WwTW | SE2308080630 | 423080 | 480630 | GB104027069461 | Ure from Thornton Steward Beck to River Skell | River | 3309 | Middle and Lower Ure | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER URE | Not Applicable | Not Applicable | Not Applicable | 874:45 | 67 | 47.6 | 2020 | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00287
YWS00288 | Yorkshire Water | Live | MIDDLEHAM SEWAGE PUMPING STATION | MIDDLEHAM/CSO | 27/22/0066 | 27/22/0066 | A2 | Storm discharge at pumping station | SE1354188107 | 413541 | 488107 | GB104027069464 | Ure from Mill Beck to Thornton Steward Beck | River | 3505 | Upper Ure | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER URE | Not Applicable | Not Applicable | Not Applicable | 82:00 | 36 | 18 | 2020 | 99.77 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00288
YWS00289 | Yorkshire Water | Live | SOUTH STAINLEY SPS | SOUTH STAINLEY/CSO | 27/22/0069 | 27/22/0069 | A1 | Storm discharge at pumping station | SE3057063060 | 430570 | 463060 | GB104027064110 | Holbeck Catchment | River | 3309 | Middle and Lower Ure | 3088 | Swale, Ure, Nidd and Upper Ouse | STAINLEY BECK | Not Applicable | Not Applicable | Not Applicable | 696:15 | 39 | 52.6 | 2020 | 67.29 | Sensor failure / issue | Resolved - May | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement completed | SOAF investigation ongoing | YWS00289
YWS00290 | Yorkshire Water | Live | SKELL BRIDGE SPS | SKELL BRIDGE/CSO | 27/22/0071 | 27/22/0071 | 2 | Storm discharge at pumping station | SE3192070930 | 431920 | 470930 | GB104027064140 | Skell from River Laver to River Ure | River | 3309 | Middle and Lower Ure | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER SKELL | Not Applicable | Not Applicable | Not Applicable | 2:30 | 5 | 5.4 | 2020 | 99.96 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00290
YWS00291 | Yorkshire Water | Live | SWINTON MASHAM STW | SWINTON MASHAM/NO 2 STW | 27/22/0075 | 27/22/0075 | A2 | Inlet SO at WwTW | SE2163080160 | 421640 | 480172 | GB104027069310 | Burn from Leighton Beck to River Ure | River | 3309 | Middle and Lower Ure | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER BURN | Not Applicable | Not Applicable | Not Applicable | 2125:00 | 229 | 130.2 | 2020 | 99.94 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS00291
YWS00292 | Yorkshire Water | Live | BISHOP MONKTON STW | BISHOP MONKTON/NO 2 STW/3XDWF OVERFLOW | 27/22/0077 | 27/22/0077 | 2 | Storm tank at WwTW | SE3373066930 | 433730 | 466930 | GB104027064161 | Ure from River Skell to River Tutt | River | 3309 | Middle and Lower Ure | 3088 | Swale, Ure, Nidd and Upper Ouse | BISHOP MONKTON BECK | Not Applicable | Not Applicable | Not Applicable | 1513:45 | 138 | 78.4 | 2020 | 99.66 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation ongoing | Operational improvement ongoing | SOAF investigation ongoing | YWS00292
YWS00293 | Yorkshire Water | Live | BISHOP MONKTON STW | BISHOP MONKTON/NO 2 STW/6XDWF OVERFLOW | 27/22/0077 | 27/22/0077 | 3 | Inlet SO at WwTW | SE3370066800 | 433730 | 466850 | GB104027064161 | Ure from River Skell to River Tutt | River | 3309 | Middle and Lower Ure | 3088 | Swale, Ure, Nidd and Upper Ouse | BISHOP MONKTON BECK | Not Applicable | Not Applicable | Not Applicable | 110:00 | 46 | 19 | 2020 | 99.68 |  |  | High spill threshold not met | High spill threshold not met | Operational investigation ongoing | Operational improvement ongoing | No SOAF investigation required | YWS00293
YWS00294 | Yorkshire Water | Live | WATH (RIPON) SEWAGE WORKS | WATH RIPON/STW/3XDWF OVERFLOW | 27/22/0079 | 27/22/0079 | A2 | Storm tank at WwTW | SE3253076630 | 432533 | 476637 | GB104027069461 | Ure from Thornton Steward Beck to River Skell | River | 3309 | Middle and Lower Ure | 3088 | Swale, Ure, Nidd and Upper Ouse | NORTON BECK | Not Applicable | Not Applicable | Not Applicable | 354:45 | 58 | 57 | 2020 | 100 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00294
YWS00295 | Yorkshire Water | Live | BLOSSOMGATE CSO | BLOSSOMGATE/CSO | 27/22/0080 | 27/22/0080 | A1 | SO on sewer network | SE3102570990 | 431025 | 470990 | GB104027064140 | Skell from River Laver to River Ure | River | 3309 | Middle and Lower Ure | 3088 | Swale, Ure, Nidd and Upper Ouse | SKELL | Not Applicable | Not Applicable | Not Applicable | 117:30 | 34 | 38.4 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS00295
YWS00296 | Yorkshire Water | Live | CLOTHERHOLME CSO | CLOTHERHOLME/CSO | 27/22/0081 | 27/22/0081 | A1 | SO on sewer network | SE3102070990 | 431025 | 470990 | GB104027064140 | Skell from River Laver to River Ure | River | 3309 | Middle and Lower Ure | 3088 | Swale, Ure, Nidd and Upper Ouse | SKELL | Not Applicable | Not Applicable | Not Applicable | 62:45 | 30 | 20 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00296
YWS00297 | Yorkshire Water | Live | KIRKBY ROAD CSO | KIRKBY ROAD/CSO | 27/22/0082 | 27/22/0082 | A1 | SO on sewer network | SE3102570990 | 431025 | 470990 | GB104027064140 | Skell from River Laver to River Ure | River | 3309 | Middle and Lower Ure | 3088 | Swale, Ure, Nidd and Upper Ouse | SKELL | Not Applicable | Not Applicable | Not Applicable | 4:15 | 4 | 2.6 | 2020 | 91.68 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00297
YWS00298 | Yorkshire Water | Live | MALLORIE PARK CSO | MALLORIE PARK/CSO | 27/22/0083 | 27/22/0083 | A1 | SO on sewer network | SE3102770990 | 431027 | 470990 | GB104027064140 | Skell from River Laver to River Ure | River | 3309 | Middle and Lower Ure | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER SKELL VIA SURFACE WTR SW | Not Applicable | Not Applicable | Not Applicable | 4:30 | 8 | 6 | 2020 | 99.74 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00298
YWS00299 | Yorkshire Water | Live | PARK STREET CSO | PARK STREET/CSO | 27/22/0084 | 27/22/0084 | 1 | SO on sewer network | SE3102270990 | 431025 | 470990 | GB104027064140 | Skell from River Laver to River Ure | River | 3309 | Middle and Lower Ure | 3088 | Swale, Ure, Nidd and Upper Ouse | SKELL | Not Applicable | Not Applicable | Not Applicable | 158:15 | 47 | 37.6 | 2020 | 99.79 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00299
YWS00300 | Yorkshire Water | Live | HAWES SEWAGE TREATMENT WORKS | HAWES/STW | 27/22/0090 | 27/22/0090 | 2 | Inlet SO at WwTW | SD8761090250 | 387610 | 490250 | GB104027069463 | Ure from Duerley Beck to Mill Beck | River | 3505 | Upper Ure | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER URE | Not Applicable | Not Applicable | Not Applicable | 373:00 | 105 | 96.6 | 2020 | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS00300
YWS00302 | Yorkshire Water | Live | GREAT OUSEBURN SPS | GREAT OUSEBURN/CSO | 27/22/0092 | 27/22/0092 | A2 | Storm discharge at pumping station | SE4450861779 | 444508 | 461779 | GB104027063800 | Ouse from Source to River Ure | River | 3309 | Middle and Lower Ure | 3088 | Swale, Ure, Nidd and Upper Ouse | UNNAMED TRIB OF OUSE GILL BECK | Not Applicable | Not Applicable | Not Applicable | 38:15 | 17 | 7.8 | 2020 | 92.71 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00302
YWS00303 | Yorkshire Water | Live | SHAROW SPS | SHAROW/CSO | 27/22/0094 | 27/22/0094 | A2 | Storm discharge at pumping station | SE3209471922 | 432094 | 471922 | GB104027069461 | Ure from Thornton Steward Beck to River Skell | River | 3309 | Middle and Lower Ure | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER URE | Not Applicable | Not Applicable | Not Applicable | 37:30 | 12 | 2.4 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00303
YWS00304 | Yorkshire Water | Live | BOROUGHBRIDGE STW | BOROUGHBRIDGE/NO 2 STW | 27/22/0095 | 27/22/0095 | A2 | Storm tank at WwTW | SE4080067170 | 440800 | 467170 | GB104027064162 | Ure from River Tutt to River Swale | River | 3309 | Middle and Lower Ure | 3088 | Swale, Ure, Nidd and Upper Ouse | UNNAMED TRIB OF URE | Not Applicable | Not Applicable | Not Applicable | 1907:45 | 130 | 110.8 | 2020 | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS00304
YWS00305 | Yorkshire Water | Live | LOW MOOR LANE SPS | LOW MOOR LANE/CSO | 27/22/0096 | 27/22/0096 | A2 | Storm discharge at pumping station | SE3342760308 | 433427 | 460308 | GB104027064100 | Tutt Catchment (Trib of Ure) | River | 3309 | Middle and Lower Ure | 3088 | Swale, Ure, Nidd and Upper Ouse | JUMWELL BECK | Not Applicable | Not Applicable | Not Applicable | 82:15 | 13 | 40.2 | 2020 | 100 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00305
YWS00306 | Yorkshire Water | Live | DARLEY HEAD SEWAGE PUMPING STATION | DARLEY HEAD/CSO | 27/22/0103 | 27/22/0103 | A2 | Storm discharge at pumping station | SE1939659814 | 419396 | 459814 | GB104027063810 | Darley Beck Catchment (Trib of Nidd) | River | 3497 | Upper Nidd | 3088 | Swale, Ure, Nidd and Upper Ouse | DARLEY BECK | Not Applicable | Not Applicable | Not Applicable | 158:30 | 35 | 34.8 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00306
YWS00307 | Yorkshire Water | Live | HARMBY COMBINED SEWER OVERFLOW | HARMBY/CSO | 27/22/0106 | 27/22/0106 | 1 | SO on sewer network | SE1303089380 | 413040 | 489378 | GB104027069464 | Ure from Mill Beck to Thornton Steward Beck | River | 3505 | Upper Ure | 3088 | Swale, Ure, Nidd and Upper Ouse | HARMBY BECK | Not Applicable | Not Applicable | Not Applicable | 100:00 | 31 | 34.6 | 2020 | 99.98 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00307
YWS00308 | Yorkshire Water | Live | PARK VIEW CSO | PARK VIEW/CSO | 27/22/0108 | 27/22/0108 | A1 | SO on sewer network | SE1126389958 | 411263 | 489958 | GB104027069464 | Ure from Mill Beck to Thornton Steward Beck | River | 3505 | Upper Ure | 3088 | Swale, Ure, Nidd and Upper Ouse | TRIB OF RIVER URE | Not Applicable | Not Applicable | Not Applicable | 268:15 | 55 | 54.6 | 2020 | 99.97 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00308
YWS00309 | Yorkshire Water | Live | EAST WITTON CSO | EAST WITTON/CSO | 27/22/0109 | 27/22/0109 | A1 | SO on sewer network | SE1470386230 | 414703 | 486230 | GB104027069464 | Ure from Mill Beck to Thornton Steward Beck | River | 3505 | Upper Ure | 3088 | Swale, Ure, Nidd and Upper Ouse | TRIB OF RIVER URE | Not Applicable | Not Applicable | Not Applicable | 415:15 | 42 | 27.8 | 2020 | 99.94 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00309
YWS00310 | Yorkshire Water | Live | BORRAGE BRIDGE CSO | BORRAGE BRIDGE/CSO | 27/22/0111 | 27/22/0111 | 1 | SO on sewer network | SE3102170991 | 431025 | 470990 | GB104027064140 | Skell from River Laver to River Ure | River | 3309 | Middle and Lower Ure | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER SKELL VIA A PUBLIC SEWER | Not Applicable | Not Applicable | Not Applicable | 33:00 | 31 | 59.2 | 2020 | 100 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS00310
YWS00311 | Yorkshire Water | Live | BAINBRIDGE STW | BAINBRIDGE/STW | 27/22/0121 | 27/22/0121 | A2 | Inlet SO at WwTW | SD9349090510 | 393490 | 490480 | GB104027069400 | Bain/Raydale Beck Catch (trib of Ure) | River | 3505 | Upper Ure | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER BAIN | Not Applicable | Not Applicable | Not Applicable | 325:15 | 77 | 81 | 2020 | 99.93 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement ongoing | SOAF investigation ongoing | YWS00311
YWS00312 | Yorkshire Water | Live | HETTON GARTH CSO | HETTON GARTH/CSO | 27/22/0128 | 27/22/0128 | A1 | SO on sewer network | SE1131090290 | 411316 | 490289 | GB104027069464 | Ure from Mill Beck to Thornton Steward Beck | River | 3505 | Upper Ure | 3088 | Swale, Ure, Nidd and Upper Ouse | UNNAMED TRIBUTARY OF RIVER URE | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 1.8 | 2020 | 99.98 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00312
YWS00313 | Yorkshire Water | Live | SILVER STREET CSO | SILVER STREET/CSO | 27/22/0132 | 27/22/0132 | A1 | SO on sewer network | SE2253880845 | 422538 | 480845 | GB104027069461 | Ure from Thornton Steward Beck to River Skell | River | 3309 | Middle and Lower Ure | 3088 | Swale, Ure, Nidd and Upper Ouse | TRIBUTARY OF RIVER URE | Not Applicable | Not Applicable | Not Applicable | 12:30 | 16 | 27 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00313
YWS00314 | Yorkshire Water | Live | NORTH STAINLEY STW | NORTH STAINLEY/STW | 27/22/0135 | 27/22/0135 | 2 | Inlet SO at WwTW | SE2876077350 | 428760 | 477350 | GB104027069461 | Ure from Thornton Steward Beck to River Skell | River | 3309 | Middle and Lower Ure | 3088 | Swale, Ure, Nidd and Upper Ouse | NORTH STAINLEY BECK | Not Applicable | Not Applicable | Not Applicable | 51:00 | 7 | 3.4 | 2020 | 99.58 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00314
YWS00315 | Yorkshire Water | Live | AYSGARTH FALLS STW | AYSGARTH FALLS/STW | 27/22/0153 | 27/22/0153 | A2 | Inlet SO at WwTW | SE0120088670 | 401200 | 488670 | GB104027069463 | Ure from Duerley Beck to Mill Beck | River | 3505 | Upper Ure | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER URE | Not Applicable | Not Applicable | Not Applicable | 156:45 | 9 | 2.2 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00315
YWS00316 | Yorkshire Water | Live | THE HOLME BRIDGE CSO | THE HOLME BRIDGE/CSO | 27/22/0160 | 27/22/0160 | 1 | SO on sewer network | SD8741089840 | 387411 | 489844 | GB104027069390 | Duerley Beck from Source to River Ure | River | 3505 | Upper Ure | 3088 | Swale, Ure, Nidd and Upper Ouse | GAYLE BECK | Not Applicable | Not Applicable | Not Applicable | 3:00 | 1 | 0.8 | 2020 | 99.95 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00316
YWS00317 | Yorkshire Water | Live | LEYBURN ROAD CSO | LEYBURN ROAD/CSO | 27/22/0161 | 27/22/0161 | 1 | SO on sewer network | SE2258081010 | 422580 | 481011 | GB104027069461 | Ure from Thornton Steward Beck to River Skell | River | 3309 | Middle and Lower Ure | 3088 | Swale, Ure, Nidd and Upper Ouse | TRIBUTARY OF RIVER URE | Not Applicable | Not Applicable | Not Applicable | 22:15 | 19 | 11 | 2020 | 99.91 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00317
YWS00318 | Yorkshire Water | Live | MILLGATE MASHAM CSO | MILLGATE MASHAM/CSO | 27/22/0162 | 27/22/0162 | A1 | SO on sewer network | SE2271480804 | 422714 | 480804 | GB104027069461 | Ure from Thornton Steward Beck to River Skell | River | 3309 | Middle and Lower Ure | 3088 | Swale, Ure, Nidd and Upper Ouse | TRIBUTARY OF RIVER URE | Not Applicable | Not Applicable | Not Applicable | 915:30 | 139 | 106.6 | 2020 | 96 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | Operational investigation completed | No improvement action in reporting period | SOAF investigation completed - No work required | YWS00318
YWS00319 | Yorkshire Water | Live | NEW ROW COMBINED SEWER OVERFLOW | NEW ROW/CSO | 27/22/0163 | 27/22/0163 | A1 | SO on sewer network | SE3950066505 | 439509 | 466505 | GB104027064100 | Tutt Catchment (Trib of Ure) | River | 3309 | Middle and Lower Ure | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER TUTT | Not Applicable | Not Applicable | Not Applicable | 77:30 | 30 | 6 | 2020 | 50.24 | Sensor failure / issue | Resolved - Nov | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00319
YWS00320 | Yorkshire Water | Live | SWINTON TERRACE CSO | SWINTON TERRACE/CSO | 27/22/0164 | 27/22/0164 | 1 | SO on sewer network | SE2234080460 | 422345 | 480467 | GB104027069310 | Burn from Leighton Beck to River Ure | River | 3309 | Middle and Lower Ure | 3088 | Swale, Ure, Nidd and Upper Ouse | SWINNEY BECK | Not Applicable | Not Applicable | Not Applicable |  |  | 7.25 | 2020 | 0 | Sensor failure / issue | Scheduled | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00320
YWS00321 | Yorkshire Water | Live | WATER SKELLGATE CSO | WATER SKELLGATE/CSO | 27/22/0167 | 27/22/0167 | A1 | SO on sewer network | SE3104571001 | 431045 | 471001 | GB104027064140 | Skell from River Laver to River Ure | River | 3309 | Middle and Lower Ure | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER SKELL | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0.8 | 2020 | 75.61 | Comms failure / issue | Scheduled | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00321
YWS00322 | Yorkshire Water | Live | BONDGATE GREEN CSO | BONDGATE GREEN/CSO | 27/22/0168 | 27/22/0168 | 1 | SO on sewer network | SE3141070950 | 431417 | 470959 | GB104027064140 | Skell from River Laver to River Ure | River | 3309 | Middle and Lower Ure | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER SKELL | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 4.6 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00322
YWS00323 | Yorkshire Water | Live | STONEBRIDGE GATE CSO | STONEBRIDGE GATE/CSO | 27/22/0169 | 27/22/0169 | 1 | Storm discharge at pumping station | SE3158071570 | 431580 | 471570 | GB104027069461 | Ure from Thornton Steward Beck to River Skell | River | 3309 | Middle and Lower Ure | 3088 | Swale, Ure, Nidd and Upper Ouse | SKITTERGATE GUTTER | Not Applicable | Not Applicable | Not Applicable | 95:30 | 24 | 14.4 | 2020 | 90.55 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00323
YWS00324 | Yorkshire Water | Live | NORTHALLERTON & ROMANBY STW | NORTHALLERTON/STW/3XDWF OVERFLOW | QR27/23/0050 | 27/23/0050 | 2 | Storm tank at WwTW | SE3505093010 | 435430 | 492900 | GB104027069540 | Willow Beck Catchment (trib of Wiske) | River | 3541 | Wiske | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER WISKE | Not Applicable | Not Applicable | Not Applicable | 505:30 | 104 | 126 | 2020 | 99.86 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00324
YWS00325 | Yorkshire Water | Live | SHUTE ROAD NO2 SPS | SHUTE ROAD/NO 2 CSO | QR.27/23/0076 | 27/23/0076 | A2 | Storm discharge at pumping station | SE1833797850 | 418337 | 497850 | GB104027069000 | Colburn Beck/Risedale Bk from Source to R Swale | River | 3317 | Middle Swale | 3088 | Swale, Ure, Nidd and Upper Ouse | COTTAGES BECK | Not Applicable | Not Applicable | Not Applicable | 258:45 | 30 | 20.2 | 2020 | 95.78 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00325
YWS00326 | Yorkshire Water | Live | CATTERICK BRIDGE SPS | CATTERICK BRIDGE/CSO | 27/23/0093 | 27/23/0093 | A2 | Storm discharge at pumping station | SE2295599455 | 422955 | 499455 | GB104027069122 | Swale from Clapgate Beck to Bedale Beck | River | 3317 | Middle Swale | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER SWALE | Not Applicable | Not Applicable | Not Applicable | 89:30 | 32 | 36.2 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00326
YWS00327 | Yorkshire Water | Live | THORMANBY SEWAGE TREATMENT WORKS | THORMANBY/NO 2 STW | 27/23/0106 | 27/23/0106 | 2 | Inlet SO at WwTW | SE4898075180 | 448970 | 475180 | GB104027068790 | Birdforth/Green's Bks Catch (trib of Swale) | River | 3283 | Lower Swale | 3088 | Swale, Ure, Nidd and Upper Ouse | UNNAMED TRIB OF BIRDFORTH BECK | Not Applicable | Not Applicable | Not Applicable | 189:15 | 58 | 53.6 | 2020 | 100 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00327
YWS00328 | Yorkshire Water | Live | GUNNERSIDE STW | GUNNERSIDE/NO 2 STW | 27/23/0108 | 27/23/0108 | 2 | Inlet SO at WwTW | SD9498097810 | 394980 | 497810 | GB104027069121 | Swale from Muker Beck to Clapgate Beck | River | 3503 | Upper Swale | 3088 | Swale, Ure, Nidd and Upper Ouse | THE RIVER SWALE | Not Applicable | Not Applicable | Not Applicable |  |  | 57.25 | 2020 | 0 | Installation set-up/design issue | Resolved - January after reporting year | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00328
YWS00329 | Yorkshire Water | Live | COLBURN SEWAGE TREATMENT WORKS | COLBURN/STW | 27/23/0123 | 27/23/0123 | A2 | Storm tank at WwTW | SE2053099680 | 420530 | 499680 | GB104027069122 | Swale from Clapgate Beck to Bedale Beck | River | 3317 | Middle Swale | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER SWALE | Not Applicable | Not Applicable | Not Applicable | 1936:00 | 113 | 125.5 | 2020 | 100 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation ongoing | Operational improvement ongoing | SOAF investigation ongoing | YWS00329
YWS00330 | Yorkshire Water | Live | COLBURN SEWAGE TREATMENT WORKS | COLBURN/STW | 27/23/0123 | 27/23/0123 | A3 | Inlet SO at WwTW | SE2053099680 | 420530 | 499680 | GB104027069122 | Swale from Clapgate Beck to Bedale Beck | River | 3317 | Middle Swale | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER SWALE | Not Applicable | Not Applicable | Not Applicable | 47:30 | 17 | 14.75 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00330
YWS00331 | Yorkshire Water | Live | DANBY WISKE VILL SPS | DANBY WISKE VILL/CSO | 27/23/0127 | 27/23/0127 | A2 | Storm discharge at pumping station | SE3377098700 | 433770 | 498700 | GB104027069530 | Wiske from Trenholme Stell to River Swale | River | 3541 | Wiske | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER WISKE | Not Applicable | Not Applicable | Not Applicable | 0:45 | 1 | 0.2 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00331
YWS00332 | Yorkshire Water | Live | GREAT CRAKEHALL SPS | GREAT CRAKEHALL/CSO | 27/23/0128 | 27/23/0128 | 1 | Storm discharge at pumping station | SE2453090170 | 424530 | 490180 | GB104027068920 | Bedale/Newton/Burton Bk - Brompton Bk to Rand | River | 3317 | Middle Swale | 3088 | Swale, Ure, Nidd and Upper Ouse | BEDALE BECK | Not Applicable | Not Applicable | Not Applicable | 78:30 | 23 | 17.8 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00332
YWS00333 | Yorkshire Water | Live | INGLEBY CROSS SPS | INGLEBY CROSS/CSO | 27/23/0129 | 27/23/0129 | A2 | Storm discharge at pumping station | NZ4514900655 | 445149 | 500655 | GB104027069550 | Wiske from Source to Trenholme Stell | River | 3541 | Wiske | 3088 | Swale, Ure, Nidd and Upper Ouse | CARR BECK | Not Applicable | Not Applicable | Not Applicable | 529:15 | 57 | 63.6 | 2020 | 100 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement ongoing | SOAF investigation ongoing | YWS00333
YWS00334 | Yorkshire Water | Live | MORTON ON SWALE SPS | MORTON ON SWALE VILL/CSO | 27/23/0131 | 27/23/0131 | 2 | Storm discharge at pumping station | SE3236091880 | 432360 | 491880 | GB104027069122 | Swale from Clapgate Beck to Bedale Beck | River | 3317 | Middle Swale | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER SWALE | Not Applicable | Not Applicable | Not Applicable | 38:15 | 11 | 10 | 2020 | 84.58 | Comms failure / issue | Resolved - May | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00334
YWS00336 | Yorkshire Water | Live | THIRSK SEWAGE TREATMENT WORKS | THIRSK/STW | 27/23/0138 | 27/23/0138 | A2 | Storm tank at WwTW | SE4359780297 | 443597 | 480297 | GB104027068820 | Cod Beck from Spital Beck to River Swale | River | 3283 | Lower Swale | 3088 | Swale, Ure, Nidd and Upper Ouse | COD BECK | Not Applicable | Not Applicable | Not Applicable | 440:15 | 68 | 91.2 | 2020 | 99.97 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00336
YWS00337 | Yorkshire Water | Live | GILLING WEST SEWAGE TREATMENT WORKS | GILLING WEST/STW | 27/23/0141 | 27/23/0141 | A2 | Storm tank at WwTW | NZ1876004690 | 418741 | 504733 | GB104027069180 | Skeeby/Holme/Dalton Bk from Source to River Swale | River | 3317 | Middle Swale | 3088 | Swale, Ure, Nidd and Upper Ouse | GILLING BECK | Not Applicable | Not Applicable | Not Applicable | 15:15 | 5 | 56.4 | 2020 | 99.17 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00337
YWS00338 | Yorkshire Water | Live | BEDALE SEWAGE TREATMENT WORKS | BEDALE/STW | 27/23/0144 | 27/23/0144 | A2 | Storm tank at WwTW | SE2738187810 | 427387 | 487814 | GB104027068910 | Bedale/Newton/Burton Bk from Rand Bk to R Swale | River | 3317 | Middle Swale | 3088 | Swale, Ure, Nidd and Upper Ouse | BEDALE BECK | Not Applicable | Not Applicable | Not Applicable | 1515:00 | 122 | 86.2 | 2020 | 100 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation ongoing | Operational improvement ongoing | SOAF investigation ongoing | YWS00338
YWS00339 | Yorkshire Water | Live | BEDALE SEWAGE TREATMENT WORKS | BEDALE/STW | 27/23/0144 | 27/23/0144 | A3 | Inlet SO at WwTW | SE2730087880 | 427279 | 487901 | GB104027068910 | Bedale/Newton/Burton Bk from Rand Bk to R Swale | River | 3317 | Middle Swale | 3088 | Swale, Ure, Nidd and Upper Ouse | BEDALE BECK | Not Applicable | Not Applicable | Not Applicable | 647:15 | 113 | 111.33 | 2020 | 99.95 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS00339
YWS00340 | Yorkshire Water | Live | SINDERBY STW | SINDERBY/STW/3XDWF OVERFLOW | 27/23/0148 | 27/23/0148 | A2 | Storm tank at WwTW | SE3470082200 | 434787 | 482163 | GB104027069591 | Swale from Wiske to River Ure | River | 3283 | Lower Swale | 3088 | Swale, Ure, Nidd and Upper Ouse | HOLME AND AINDERBY BECK | Not Applicable | Not Applicable | Not Applicable | 239:30 | 34 | 41.4 | 2020 | 99.97 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00340
YWS00341 | Yorkshire Water | Live | SKEEBY SEWAGE PUMPING STATION | SKEEBY/CSO | 27/23/0161 | 27/23/0161 | 2 | Storm discharge at pumping station | NZ2047002760 | 420470 | 502760 | GB104027069180 | Skeeby/Holme/Dalton Bk from Source to River Swale | River | 3317 | Middle Swale | 3088 | Swale, Ure, Nidd and Upper Ouse | SKEEBY BECK | Not Applicable | Not Applicable | Not Applicable | 572:15 | 52 | 42.8 | 2020 | 95.28 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00341
YWS00342 | Yorkshire Water | Live | HELPERBY (BRAFFERTON) SPS | HELPERBY/CSO | 27/23/0174 | 27/23/0174 | 2 | Storm discharge at pumping station | SE4371069830 | 443710 | 469830 | GB104027069591 | Swale from Wiske to River Ure | River | 3283 | Lower Swale | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER SWALE | Not Applicable | Not Applicable | Not Applicable | 34:00 | 35 | 32.8 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00342
YWS00344 | Yorkshire Water | Live | MIDDLETON TYAS STW | MIDDLETON TYAS/NO 2 STW | 27/23/0181 | 27/23/0181 | A2 | Storm tank at WwTW | NZ2338006220 | 423368 | 506246 | GB104027069160 | Scorton Beck from Source to River Swale | River | 3317 | Middle Swale | 3088 | Swale, Ure, Nidd and Upper Ouse | UNNAMED TRIB COW LANE BECK | Not Applicable | Not Applicable | Not Applicable | 270:15 | 44 | 49.8 | 2020 | 99.99 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00344
YWS00346 | Yorkshire Water | Live | NORTH COWTON STW | NORTH COWTON/STW | 27/23/0194 | 27/23/0194 | A2 | Storm tank at WwTW | NZ2861003520 | 428610 | 503510 | GB104027069560 | Trenholme Stell from Source to River Wiske | River | 3541 | Wiske | 3088 | Swale, Ure, Nidd and Upper Ouse | THE STELL | Not Applicable | Not Applicable | Not Applicable | 831:45 | 86 | 124.8 | 2020 | 99.4 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement ongoing | SOAF investigation ongoing | YWS00346
YWS00347 | Yorkshire Water | Live | SNAPE SEWAGE TREATMENT WORKS | SNAPE/STW/3XDWF OVERFLOW | 27/23/0201 | 27/23/0201 | A2 | Storm tank at WwTW | SE2734184271 | 427341 | 484271 | GB104027068841 | Old Stell Catchment (trib of Bedale Beck) | River | 3317 | Middle Swale | 3088 | Swale, Ure, Nidd and Upper Ouse | TRIB OF MAIN CUT | Not Applicable | Not Applicable | Not Applicable | 965:15 | 77 | 69.6 | 2020 | 99.97 |  |  | Performance - Infiltration | Performance - Infiltration | UWWTR investigation ongoing, Operational investigation ongoing | Operational improvement ongoing | SOAF investigation ongoing | YWS00347
YWS00348 | Yorkshire Water | Live | RAVENSWORTH SEWAGE PUMPING STATION | RAVENSWORTH VILLAGE/CSO | 27/23/0205 | 27/23/0205 | 1 | Storm discharge at pumping station | NZ1415008130 | 414150 | 508130 | GB104027069180 | Skeeby/Holme/Dalton Bk from Source to River Swale | River | 3317 | Middle Swale | 3088 | Swale, Ure, Nidd and Upper Ouse | HOLME BECK | Not Applicable | Not Applicable | Not Applicable | 314:45 | 66 | 60.6 | 2020 | 99.78 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00348
YWS00349 | Yorkshire Water | Live | MARSKE SEWAGE TREATMENT WORKS | MARSKE/STW | 27/23/0208 | 27/23/0208 | 2 | Inlet SO at WwTW | NZ1041000430 | 410410 | 500430 | GB104027069140 | Marske Beck from Source to River Swale | River | 3503 | Upper Swale | 3088 | Swale, Ure, Nidd and Upper Ouse | MARSKE BECK | Not Applicable | Not Applicable | Not Applicable | 1326:15 | 136 | 149.2 | 2020 | 97.83 |  |  | Performance - Infiltration | Performance - Infiltration | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS00349
YWS00350 | Yorkshire Water | Live | COWESBY SEWAGE TREATMENT WORKS | COWESBY/STW/6XDWF OVERFLOW | 27/23/0215 | 27/23/0215 | 2 | Inlet SO at WwTW | SE4645089550 | 446450 | 489550 | GB104027068950 | Broad Beck from Source to Cod Beck | River | 3283 | Lower Swale | 3088 | Swale, Ure, Nidd and Upper Ouse | UNNAMED TRIB OF LITTLE BECK | Not Applicable | Not Applicable | Not Applicable | 748:00 | 56 | 53.6 | 2020 | 100 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00350
YWS00351 | Yorkshire Water | Live | SKIPTON ON SWALE STW | SKIPTON ON SWALE/STW | 27/23/0216 | 27/23/0216 | 2 | Inlet SO at WwTW | SE3640079770 | 436400 | 479770 | GB104027069591 | Swale from Wiske to River Ure | River | 3283 | Lower Swale | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER SWALE | Not Applicable | Not Applicable | Not Applicable | 16:15 | 9 | 52.6 | 2020 | 92.72 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00351
YWS00352 | Yorkshire Water | Live | RIVERSIDE ROAD NO.2 CSO | RIVERSIDE ROAD/NO 2 CSO | 27/23/0219 | 27/23/0219 | A1 | SO on sewer network | NZ1697200612 | 416972 | 500612 | GB104027069122 | Swale from Clapgate Beck to Bedale Beck | River | 3317 | Middle Swale | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER SWALE | Not Applicable | Not Applicable | Not Applicable | 186:44 | 62 | 54.6 | 2020 | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement ongoing | SOAF investigation ongoing | YWS00352
YWS00353 | Yorkshire Water | Live | OTTERINGTON SEWAGE PUMPING STATION | OTTERINGTON CHURCH/CSO | 27/23/0220 | 27/23/0220 | A2 | Storm discharge at pumping station | SE3725087640 | 437250 | 487640 | GB104027069530 | Wiske from Trenholme Stell to River Swale | River | 3541 | Wiske | 3088 | Swale, Ure, Nidd and Upper Ouse | HOWE BECK | Not Applicable | Not Applicable | Not Applicable | 69:45 | 7 | 3.8 | 2020 | 99.98 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00353
YWS00355 | Yorkshire Water | Live | MOWBRAY ROAD SEWAGE PUMPING STATION | MOWBRAY ROAD/CSO | 27/23/0222 | 27/23/0222 | 1 | Storm discharge at pumping station | SE2389698457 | 423890 | 498450 | GB104027069122 | Swale from Clapgate Beck to Bedale Beck | River | 3317 | Middle Swale | 3088 | Swale, Ure, Nidd and Upper Ouse | CULVERTED TRIB OF RIVER SWALE | Not Applicable | Not Applicable | Not Applicable | 0:15 | 1 | 0.2 | 2020 | 91.86 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00355
YWS00356 | Yorkshire Water | Live | RICHMOND BRIDGE NO2 CSO | RICHMOND BRIDGE/NO 2 CSO | 27/23/0226 | 27/23/0226 | A1 | SO on sewer network | NZ1700000560 | 417000 | 500560 | GB104027069122 | Swale from Clapgate Beck to Bedale Beck | River | 3317 | Middle Swale | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER SWALE | Not Applicable | Not Applicable | Not Applicable | 0:16 | 5 | 3.2 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00356
YWS00357 | Yorkshire Water | Live | REETH ROAD NO 2 CSO | REETH ROAD/NO 2 CSO | 27/23/0227 | 27/23/0227 | A1 | SO on sewer network | NZ1623700985 | 416237 | 500985 | GB104027069122 | Swale from Clapgate Beck to Bedale Beck | River | 3317 | Middle Swale | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER SWALE | Not Applicable | Not Applicable | Not Applicable | 151:16 | 58 | 66.2 | 2020 | 99.99 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS00357
YWS00358 | Yorkshire Water | Live | BLAKEY LANE NO 2 CSO | BLAKEY LANE/NO 2 CSO | 27/23/0245 | 27/23/0245 | A1 | SO on sewer network | SE4350681143 | 443506 | 481143 | GB104027068820 | Cod Beck from Spital Beck to River Swale | River | 3283 | Lower Swale | 3088 | Swale, Ure, Nidd and Upper Ouse | COD BECK | Not Applicable | Not Applicable | Not Applicable | 23:30 | 20 | 22.6 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00358
YWS00359 | Yorkshire Water | Live | THIRSK FINKLE STREET NO. 2 CSO | THIRSK FINKLE ST/NO 2 CSO | 27/23/0246 | 27/23/0246 | A1 | SO on sewer network | SE4315682119 | 443156 | 482119 | GB104027068820 | Cod Beck from Spital Beck to River Swale | River | 3283 | Lower Swale | 3088 | Swale, Ure, Nidd and Upper Ouse | COD BECK | Not Applicable | Not Applicable | Not Applicable | 60:15 | 20 | 18.8 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00359
YWS00360 | Yorkshire Water | Live | CHURCH BANK CSO | CHURCH BANK/NO 2 CSO | 27/23/0248 | 27/23/0248 | 1 | SO on sewer network | SE1906092620 | 419060 | 492622 | GB104027068960 | Brompton Bk from Source to Newton Bk | River | 3317 | Middle Swale | 3088 | Swale, Ure, Nidd and Upper Ouse | UNNAMED TRIB OF HUNTON BECK | Not Applicable | Not Applicable | Not Applicable | 0:30 | 2 | 3 | 2020 | 98.4 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00360
YWS00361 | Yorkshire Water | Live | OLDSTEAD SEWAGE TREATMENT WORKS | OLDSTEAD/STW | 27/23/0249 | 27/23/0249 | 2 | Inlet SO at WwTW | SE5288179640 | 452880 | 479640 | GB104027068790 | Birdforth/Green's Bks Catch (trib of Swale) | River | 3283 | Lower Swale | 3088 | Swale, Ure, Nidd and Upper Ouse | UNNAMED TRIB OF WAKENDALE BECK | Not Applicable | Not Applicable | Not Applicable | 122:30 | 21 | 7.2 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00361
YWS00362 | Yorkshire Water | Live | BURRILL SEWAGE TREATMENT WORKS | BURRILL/NO 2 STW | 27/23/0254 | 27/23/0254 | 2 | Inlet SO at WwTW | SE2425087000 | 424250 | 487000 | GB104027068841 | Old Stell Catchment (trib of Bedale Beck) | River | 3317 | Middle Swale | 3088 | Swale, Ure, Nidd and Upper Ouse | BURRILL BECK | Not Applicable | Not Applicable | Not Applicable | 39:30 | 23 | 33.4 | 2020 | 99.8 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00362
YWS00363 | Yorkshire Water | Live | MYTON ON SWALE SEWAGE WORKS | MYTON ON SWALE/NO 2 STW | 27/23/0256 | 27/23/0256 | 2 | Inlet SO at WwTW | SE4361066730 | 443610 | 466730 | GB104027069591 | Swale from Wiske to River Ure | River | 3283 | Lower Swale | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER SWALE | Not Applicable | Not Applicable | Not Applicable | 2042:45 | 124 | 89.2 | 2020 | 100 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00363
YWS00364 | Yorkshire Water | Live | KIRKLINGTON WASTEWATER T-MENT WORKS | KIRKLINGTON/STW/PRELIMINARY TREATMENT-STW/3XDWF OVERFLOW | 27/23/0263 | 27/23/0263 | A2 | Inlet SO at WwTW | SE3177181611 | 431771 | 481611 | GB104027068800 | Ings Goit from Source to Burneston Beck | River | 3317 | Middle Swale | 3088 | Swale, Ure, Nidd and Upper Ouse | HEALAM BECK | Not Applicable | Not Applicable | Not Applicable | 64:00 | 20 | 13.2 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00364
YWS00365 | Yorkshire Water | Live | HELPERBY SEWAGE TREATMENT WORKS | HELPERBY/STW | 27/23/0264 | 27/23/0264 | A2 | Storm tank at WwTW | SE4391069890 | 443910 | 469890 | GB104027069591 | Swale from Wiske to River Ure | River | 3283 | Lower Swale | 3088 | Swale, Ure, Nidd and Upper Ouse | CULVERTED TRIB OF SWALE | Not Applicable | Not Applicable | Not Applicable | 158:30 | 11 | 16.8 | 2020 | 99.91 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00365
YWS00366 | Yorkshire Water | Live | BELLERBY SEWAGE TREATMENT WORKS | BELLERBY/STW | 27/23/0265 | 27/23/0265 | A2 | Inlet SO at WwTW | SE1205092780 | 412050 | 492780 | GB104027068940 | Bedale/Newton/Burton Bk from Source to Brompton Bk | River | 3317 | Middle Swale | 3088 | Swale, Ure, Nidd and Upper Ouse | BELLERBY BECK | Not Applicable | Not Applicable | Not Applicable | 38:45 | 13 | 62.8 | 2020 | 99.97 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00366
YWS00367 | Yorkshire Water | Live | NORTON LE CLAY SEWAGE WORKS | NORTON LE CLAY/STW | 27/23/0272 | 27/23/0272 | 2 | Inlet SO at WwTW | SE4006071170 | 440060 | 471170 | GB104027068780 | Cundall Beck/Soppa Gutter Catch (trib of Swale) | River | 3283 | Lower Swale | 3088 | Swale, Ure, Nidd and Upper Ouse | UNNAMED TRIB OF MAIN GOIT | Not Applicable | Not Applicable | Not Applicable | 1429:15 | 110 | 90.2 | 2020 | 98.88 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS00367
YWS00368 | Yorkshire Water | Live | HACKFORTH NO. 2 STW | HACKFORTH/NO 2 STW | 27/23/0273 | 27/23/0273 | A2 | Inlet SO at WwTW | SE2453093230 | 424530 | 493230 | GB104027068970 | Scurf Beck from Source to Bedale Beck | River | 3317 | Middle Swale | 3088 | Swale, Ure, Nidd and Upper Ouse | BOWBRIDGE BECK | Not Applicable | Not Applicable | Not Applicable | 246:00 | 50 | 10 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00368
YWS00369 | Yorkshire Water | Live | NORTON LE CLAY SEWAGEPUMPINGSTATION | NORTON LE CLAY/SPS | 27/23/0274 | 27/23/0274 | 1 | Storm discharge at pumping station | SE4031071320 | 440310 | 471320 | GB104027068780 | Cundall Beck/Soppa Gutter Catch (trib of Swale) | River | 3283 | Lower Swale | 3088 | Swale, Ure, Nidd and Upper Ouse | UNNAMED TRIB OF MAIN GOIT | Not Applicable | Not Applicable | Not Applicable | 1:00 | 2 | 10.8 | 2020 | 99.96 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00369
YWS00370 | Yorkshire Water | Live | HUNTON STW FINAL EFFLUENT | HUNTON/STW | 27/23/0275 | 27/23/0275 | 2 | Inlet SO at WwTW | SE1947092120 | 419470 | 492120 | GB104027068960 | Brompton Bk from Source to Newton Bk | River | 3317 | Middle Swale | 3088 | Swale, Ure, Nidd and Upper Ouse | HUNTON BECK | Not Applicable | Not Applicable | Not Applicable | 691:45 | 73 | 61.6 | 2020 | 99.95 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00370
YWS00371 | Yorkshire Water | Live | SCRUTON WPC WORKS | SCRUTON/STW | 27/23/0276 | 27/23/0276 | 2 | Inlet SO at WwTW | SE3070092700 | 430710 | 482710 | GB104027068800 | Ings Goit from Source to Burneston Beck | River | 3317 | Middle Swale | 3088 | Swale, Ure, Nidd and Upper Ouse | COMMON STELL | Not Applicable | Not Applicable | Not Applicable | 90:00 | 14 | 9.2 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00371
YWS00372 | Yorkshire Water | Live | ARC FACTORY NO 2 CSO | ARC FACTORY/NO 2 CSO | 27/23/0277 | 27/23/0277 | A1 | SO on sewer network | SE2036097820 | 420362 | 497825 | GB104027068990 | Brough Bk/Scotton Bk from Source to River Swale | River | 3317 | Middle Swale | 3088 | Swale, Ure, Nidd and Upper Ouse | SOUR BECK | Not Applicable | Not Applicable | Not Applicable | 460:45 | 49 | 41.8 | 2020 | 99.92 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00372
YWS00373 | Yorkshire Water | Live | RICHMOND SEWAGE TREATMENT WORKS | RICHMOND/STW | 27/23/0279 | 27/23/0279 | A2 | Storm tank at WwTW | SE1835099890 | 418358 | 499880 | GB104027069122 | Swale from Clapgate Beck to Bedale Beck | River | 3317 | Middle Swale | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER SWALE | Not Applicable | Not Applicable | Not Applicable | 600:00 | 82 | 93.8 | 2020 | 99.94 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00373
YWS00374 | Yorkshire Water | Live | HUSTHWAITE STW | HUSTHWAITE/STW | 27/23/0280 | 27/23/0280 | 2 | Inlet SO at WwTW | SE5150075310 | 451500 | 475310 | GB104027068790 | Birdforth/Green's Bks Catch (trib of Swale) | River | 3283 | Lower Swale | 3088 | Swale, Ure, Nidd and Upper Ouse | ELPHIN BECK | Not Applicable | Not Applicable | Not Applicable | 319:30 | 90 | 62.6 | 2020 | 99.97 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS00374
YWS00375 | Yorkshire Water | Live | NEWTON LE WILLOWS STW | NEWTON LE WILLOWS/STW | 27/23/0281 | 27/23/0281 | A2 | Storm tank at WwTW | SE2189090080 | 421890 | 490080 | GB104027068940 | Bedale/Newton/Burton Bk from Source to Brompton Bk | River | 3317 | Middle Swale | 3088 | Swale, Ure, Nidd and Upper Ouse | NEWTON BECK | Not Applicable | Not Applicable | Not Applicable | 179:15 | 19 | 16 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00375
YWS00376 | Yorkshire Water | Live | NEWTON LE WILLOWS STW | NEWTON LE WILLOWS/STW | 27/23/0281 | 27/23/0281 | A3 | Inlet SO at WwTW | SE2189090080 | 421890 | 490080 | GB104027068940 | Bedale/Newton/Burton Bk from Source to Brompton Bk | River | 3317 | Middle Swale | 3088 | Swale, Ure, Nidd and Upper Ouse | NEWTON BECK | Not Applicable | Not Applicable | Not Applicable | 15:00 | 4 | 7.8 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00376
YWS00377 | Yorkshire Water | Live | JAMESVILLE WAY CSO | JAMESVILLE WAY/CSO | 27/23/0286 | 27/23/0286 | 1 | SO on sewer network | SE4020075500 | 440200 | 475500 | GB104027069591 | Swale from Wiske to River Ure | River | 3283 | Lower Swale | 3088 | Swale, Ure, Nidd and Upper Ouse | TRIB OF RIVER SWALE | Not Applicable | Not Applicable | Not Applicable | 46:30 | 20 | 20 | 2020 | 70.29 | Comms failure / issue | Resolved - Apr | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00377
YWS00378 | Yorkshire Water | Live | CHAPEL STREET CSO | THIRSK CHAPEL STREET/CSO | 27/23/0287 | 27/23/0287 | 1 | SO on sewer network | SE4315082000 | 443150 | 482000 | GB104027068820 | Cod Beck from Spital Beck to River Swale | River | 3283 | Lower Swale | 3088 | Swale, Ure, Nidd and Upper Ouse | COD BECK | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0.6 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00378
YWS00379 | Yorkshire Water | Live | APPLETON WISKE STW | APPLETON WISKE/STW/6XDWF OVERFLOW | 27/23/0302 | 27/23/0302 | A2 | Inlet SO at WwTW | NZ3866004540 | 438660 | 504540 | GB104027069550 | Wiske from Source to Trenholme Stell | River | 3541 | Wiske | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER WISKE | Not Applicable | Not Applicable | Not Applicable | 145:30 | 20 | 24.8 | 2020 | 91.38 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00379
YWS00380 | Yorkshire Water | Live | LOW LANE SEWAGE PUMPING STATION | LOW LN HUTTON SESSAY/CSO | 27/23/0303 | 27/23/0303 | 1 | Storm discharge at pumping station | SE4737075980 | 447370 | 475980 | GB104027068790 | Birdforth/Green's Bks Catch (trib of Swale) | River | 3283 | Lower Swale | 3088 | Swale, Ure, Nidd and Upper Ouse | CULVERTED TRIB BIRDFORTH BECK | Not Applicable | Not Applicable | Not Applicable | 431:00 | 61 | 36.8 | 2020 | 99.25 |  |  | Performance - Infiltration | High spill threshold not met | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS00380
YWS00381 | Yorkshire Water | Live | LANGTHORNE STW | LANGTHORNE/NO 2 STW | 27/23/0305 | 27/23/0305 | 2 | Inlet SO at WwTW | SE2602091730 | 426020 | 491730 | GB104027068970 | Scurf Beck from Source to Bedale Beck | River | 3317 | Middle Swale | 3088 | Swale, Ure, Nidd and Upper Ouse | COBSHAW DYKE | Not Applicable | Not Applicable | Not Applicable | 5128:00 | 282 | 190.2 | 2020 | 99.99 |  |  | Performance - Infiltration | Performance - Infiltration | UWWTR investigation ongoing, Operational investigation completed | Operational improvement ongoing | SOAF investigation ongoing | YWS00381
YWS00382 | Yorkshire Water | Live | ST JAMES GREEN SPS | ST JAMES GREEN/CSO | 27/23/0353 | 27/23/0353 | A2 | Storm discharge at pumping station | SE4314282156 | 443142 | 482156 | GB104027068820 | Cod Beck from Spital Beck to River Swale | River | 3283 | Lower Swale | 3088 | Swale, Ure, Nidd and Upper Ouse | COD BECK | Not Applicable | Not Applicable | Not Applicable | 289:00 | 59 | 56 | 2020 | 100 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00382
YWS00383 | Yorkshire Water | Live | RAWCLIFFE (YORK) STW | RAWCLIFFE YORK/STW | 27/24/0129 | 27/24/0129 | 3 | Storm tank at WwTW | SE5876052900 | 458700 | 452900 | GB104027069593 | Ouse from River Nidd to Stillingfleet Beck | River | 3499 | Upper Ouse Yorkshire | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER OUSE/RAWCLIFFE INGS DR | Not Applicable | Not Applicable | Not Applicable | 437:15 | 44 | 30.6 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00383
YWS00384 | Yorkshire Water | Live | FULFORD SEWAGE PUMPING STATION | FULFORD/NO 2 SPS | 27/24/0146 | 27/24/0146 | 1 | Storm discharge at pumping station | SE6028049680 | 460280 | 449680 | GB104027069593 | Ouse from River Nidd to Stillingfleet Beck | River | 3499 | Upper Ouse Yorkshire | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER OUSE | Not Applicable | Not Applicable | Not Applicable | 2321:40 | 143 | 114.6 | 2020 | 99.94 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS00384
YWS00385 | Yorkshire Water | Live | SUTTON-ON-THE-FOREST STW | SUTTON ON THE FOREST/STW | 27/24/0148 | 27/24/0148 | A2 | Storm tank at WwTW | SE5885962209 | 458850 | 462210 | GB104027063830 | New Parks Beck from Source to Huby Burn | River | 3499 | Upper Ouse Yorkshire | 3088 | Swale, Ure, Nidd and Upper Ouse | TRIB OF NEW PARKS BECK | Not Applicable | Not Applicable | Not Applicable | 230:15 | 26 | 17.2 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00385
YWS00386 | Yorkshire Water | Live | CHESHIRE HOMES | ALNE CHESHIRE HOME/CSO | 27/24/0154 | 27/24/0154 | 2 | Storm discharge at pumping station | SE4955065160 | 449550 | 465160 | GB104027063860 | Kyle from Derrings Beck to New Parks Beck | River | 3499 | Upper Ouse Yorkshire | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER KYLE | Not Applicable | Not Applicable | Not Applicable | 236:15 | 56 | 46.2 | 2020 | 99.99 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00386
YWS00387 | Yorkshire Water | Live | SHIPYARD ROAD | SHIPYARD ROAD/CSO | 27/24/0156 | 27/24/0156 | 2 | SO on sewer network | SE6207032140 | 462070 | 432140 | GB104027064270 | Ouse from R Wharfe to Upper Humber | River | 3280 | Lower Ouse Yorkshire | 3115 | Wharfe and Lower Ouse | CULVERTED BRAYTON JUNCTION | Not Applicable | Not Applicable | Not Applicable | 188:00 | 35 | 96.8 | 2020 | 97.52 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement ongoing | SOAF investigation ongoing | YWS00387
YWS00388 | Yorkshire Water | Live | SHERBURN IN ELMET STW | SHERBURN IN ELMET/STW | 27/24/0162 | 27/24/0162 | A2 | Storm tank at WwTW | SE5292033420 | 452920 | 433420 | GB104027063610 | Upper Fox Drain Catchment ds of Sherburn STW | River | 3280 | Lower Ouse Yorkshire | 3115 | Wharfe and Lower Ouse | UPPER FOX DRAIN | Not Applicable | Not Applicable | Not Applicable | 163:15 | 33 | 23.8 | 2020 | 95.96 |  |  | High spill threshold not met | High spill threshold not met | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00388
YWS00389 | Yorkshire Water | Live | EASINGWOLD SEWAGE TREATMENT WORKS | EASINGWOLD/STW | 27/24/0166 | 27/24/0166 | A2 | Storm tank at WwTW | SE5201367511 | 452013 | 467511 | GB104027063910 | Alne Beck from Source to River Kyle | River | 3499 | Upper Ouse Yorkshire | 3088 | Swale, Ure, Nidd and Upper Ouse | SHIRES BECK | Not Applicable | Not Applicable | Not Applicable | 276:00 | 32 | 42.8 | 2020 | 99.98 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00389
YWS00390 | Yorkshire Water | Live | HEMINGBROUGH WPC WORKS | HEMINGBROUGH/NO 2 STW | 27/24/0168 | 27/24/0168 | A2 | Storm tank at WwTW | SE6689030040 | 466890 | 430040 | GB104027064270 | Ouse from R Wharfe to Upper Humber | River | 3280 | Lower Ouse Yorkshire | 3115 | Wharfe and Lower Ouse | RIVER OUSE (TIDAL) | Not Applicable | Not Applicable | Not Applicable | 121:00 | 26 | 22.8 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00390
YWS00391 | Yorkshire Water | Live | SHIPTON STW | SHIPTON/NO 2 STW | 27/24/0171 | 27/24/0171 | 2 | Storm tank at WwTW | SE5580058300 | 456040 | 458210 | GB104027063780 | Hurns Gutterfrom Source to River Ouse | River | 3499 | Upper Ouse Yorkshire | 3088 | Swale, Ure, Nidd and Upper Ouse | HURNS GUTTER | Not Applicable | Not Applicable | Not Applicable | 281:45 | 65 | 35.4 | 2020 | 100 |  |  | Not asset maintenance - Hydraulic capacity | High spill threshold not met | UWWTR investigation ongoing, Operational investigation ongoing | Operational improvement ongoing | SOAF investigation ongoing | YWS00391
YWS00392 | Yorkshire Water | Live | SHIPTON STW | SHIPTON/NO 2 STW | 27/24/0171 | 27/24/0171 | 3 | Inlet SO at WwTW | SE5580058300 | 456040 | 458210 | GB104027063780 | Hurns Gutterfrom Source to River Ouse | River | 3499 | Upper Ouse Yorkshire | 3088 | Swale, Ure, Nidd and Upper Ouse | HURNS GUTTER | Not Applicable | Not Applicable | Not Applicable | 17:45 | 12 | 42.4 | 2020 | 100 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation ongoing | Operational improvement ongoing | SOAF investigation ongoing | YWS00392
YWS00393 | Yorkshire Water | Live | MICKLEFIELD STW | MICKLEFIELD/NO 2 STW | 27/24/0179 | 27/24/0179 | A2 | Storm tank at WwTW | SE4487033240 | 444870 | 433240 | GB104027063640 | Mill Dike from Source to Bishop Dike | River | 3280 | Lower Ouse Yorkshire | 3115 | Wharfe and Lower Ouse | SHEEP DIKE | Not Applicable | Not Applicable | Not Applicable | 134:30 | 19 | 10.6 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00393
YWS00394 | Yorkshire Water | Live | PROVIDENCE NOOK YORK ROAD | EASINGWOLD YORK RD/2 CSO | 27/24/0181 | 27/24/0181 | A1 | SO on sewer network | SE5333169118 | 453331 | 469118 | GB104027063910 | Alne Beck from Source to River Kyle | River | 3499 | Upper Ouse Yorkshire | 3088 | Swale, Ure, Nidd and Upper Ouse | LEASMIRES DRAIN | Not Applicable | Not Applicable | Not Applicable | 125:30 | 34 | 30.8 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00394
YWS00395 | Yorkshire Water | Live | HOLME LANE SPS | HOLME LANE/CSO | 27/24/0188 | 27/24/0188 | 2 | Storm discharge at pumping station | SE6156032670 | 461560 | 432640 | GB104027063620 | Selby Dam from Conf. Fox Dike and Carr Dike to Ouse | River | 3280 | Lower Ouse Yorkshire | 3115 | Wharfe and Lower Ouse | OUSE | Not Applicable | Not Applicable | Not Applicable | 822:00 | 70 | 53.6 | 2020 | 100 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS00395
YWS00396 | Yorkshire Water | Live | HESLINGTON MAIN STREET SPS | HESLINGTON MAIN ST/CSO | 27/24/0203 | 27/24/0203 | A2 | Storm discharge at pumping station | SE6309249951 | 463092 | 449951 | GB104027069593 | Ouse from River Nidd to Stillingfleet Beck | River | 3499 | Upper Ouse Yorkshire | 3088 | Swale, Ure, Nidd and Upper Ouse | TRIB OF GERMANY BECK | Not Applicable | Not Applicable | Not Applicable | 80:30 | 48 | 17.2 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS00396
YWS00397 | Yorkshire Water | Live | FRYSTON COMMON LANE SPS | FRYSTON COMMON LANE/2 CSO | 27/24/0204 | 27/24/0204 | 2 | SO on sewer network | SE5084029760 | 450840 | 429760 | GB104027063620 | Selby Dam from Conf. Fox Dike and Carr Dike to Ouse | River | 3280 | Lower Ouse Yorkshire | 3115 | Wharfe and Lower Ouse | CEMETARY DRAIN | Not Applicable | Not Applicable | Not Applicable | 3:30 | 3 | 2.6 | 2020 | 99.94 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00397
YWS00398 | Yorkshire Water | Live | THE ESPLANADE YORK CSO | THE ESPLANADE YORK/CSO | 27/24/0205 | 27/24/0205 | A1 | SO on sewer network | SE5919652407 | 459196 | 452407 | GB104027069593 | Ouse from River Nidd to Stillingfleet Beck | River | 3499 | Upper Ouse Yorkshire | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER OUSE | Not Applicable | Not Applicable | Not Applicable | 1500:02 | 123 | 108.6 | 2020 | 100 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS00398
YWS00399 | Yorkshire Water | Live | KELFIELD STW | KELFIELD/STW | 27/24/0211 | 27/24/0211 | 2 | Storm tank at WwTW | SE5872038270 | 458720 | 438270 | GB104027064280 | Ouse Still/fleet bk - Kelfield and Wharfe d/s Ryther | River | 3280 | Lower Ouse Yorkshire | 3115 | Wharfe and Lower Ouse | TIDAL OUSE | Not Applicable | Not Applicable | Not Applicable | 1972:15 | 173 | 96.2 | 2020 | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement completed | SOAF investigation ongoing | YWS00399
YWS00400 | Yorkshire Water | Live | ANSON GROVE SEWAGE PUMPING STATION | ANSON GROVE/CSO | 27/24/0212 | 27/24/0212 | 2 | Storm discharge at pumping station | SE5725038190 | 457250 | 438190 | GB104027064280 | Ouse Still/fleet bk - Kelfield and Wharfe d/s Ryther | River | 3280 | Lower Ouse Yorkshire | 3115 | Wharfe and Lower Ouse | UNNAMED TRIB OF TIDAL OUSE | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0.8 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00400
YWS00401 | Yorkshire Water | Live | BISHOP DIKE SEWAGE PUMPING STATION | BISHOPDYKE/CSO | 27/24/0213 | 27/24/0213 | 2 | Storm discharge at pumping station | SE5745037800 | 457450 | 437800 | GB104027064280 | Ouse Still/fleet bk - Kelfield and Wharfe d/s Ryther | River | 3280 | Lower Ouse Yorkshire | 3115 | Wharfe and Lower Ouse | BISHOP DIKE | Not Applicable | Not Applicable | Not Applicable | 59:30 | 16 | 13.2 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00401
YWS00402 | Yorkshire Water | Live | CHURCH END SEWAGE PUMPING STATION | CHURCH END/CSO | 27/24/0214 | 27/24/0214 | A2 | Storm discharge at pumping station | SE5767437748 | 457674 | 437748 | GB104027064280 | Ouse Still/fleet bk - Kelfield and Wharfe d/s Ryther | River | 3280 | Lower Ouse Yorkshire | 3115 | Wharfe and Lower Ouse | RIVER OUSE (TIDAL) | Not Applicable | Not Applicable | Not Applicable | 728:00 | 73 | 30.4 | 2020 | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | High spill threshold not met | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00402
YWS00403 | Yorkshire Water | Live | CLOUGH DIKE SEWAGE PUMPING STATION | CLOUGH DYKE/CSO | 27/24/0215 | 27/24/0215 | 2 | SO on sewer network | SE5814037980 | 458140 | 437980 | GB104027064280 | Ouse Still/fleet bk - Kelfield and Wharfe d/s Ryther | River | 3280 | Lower Ouse Yorkshire | 3115 | Wharfe and Lower Ouse | CLOUGH DIKE | Not Applicable | Not Applicable | Not Applicable | 1:00 | 1 | 1.4 | 2020 | 99.86 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00403
YWS00404 | Yorkshire Water | Live | KELFIELD SEWAGE PUMPING STATION | KELFIELD MAIN ST/CSO | 27/24/0216 | 27/24/0216 | 2 | SO on sewer network | SE5931038250 | 459310 | 438250 | GB104027064280 | Ouse Still/fleet bk - Kelfield and Wharfe d/s Ryther | River | 3280 | Lower Ouse Yorkshire | 3115 | Wharfe and Lower Ouse | TIDAL OUSE | Not Applicable | Not Applicable | Not Applicable | 1421:30 | 110 | 84.6 | 2020 | 99.97 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement ongoing | SOAF investigation ongoing | YWS00404
YWS00405 | Yorkshire Water | Live | WISTOW SEWAGE TREATMENT WORKS | WISTOW/STW | 27/24/0228 | 27/24/0228 | A2 | Storm tank at WwTW | SE6055136380 | 460550 | 436380 | GB104027064270 | Ouse from R Wharfe to Upper Humber | River | 3280 | Lower Ouse Yorkshire | 3115 | Wharfe and Lower Ouse | RIVER OUSE (TIDAL) | Not Applicable | Not Applicable | Not Applicable | 3158:15 | 179 | 106.4 | 2020 | 99.98 |  |  | Performance - GW inundation | Performance - GW inundation | UWWTR investigation ongoing, Operational investigation completed | Operational improvement completed | SOAF investigation ongoing | YWS00405
YWS00406 | Yorkshire Water | Live | WISTOW SEWAGE TREATMENT WORKS | WISTOW/STW | 27/24/0228 | 27/24/0228 | A3 | Inlet SO at WwTW | SE5970034860 | 459700 | 434860 | GB104027063650 | Holmes Dike catchment (trib of Ouse) | River | 3280 | Lower Ouse Yorkshire | 3115 | Wharfe and Lower Ouse | RIVER OUSE (TIDAL) | Not Applicable | Not Applicable | Not Applicable | 2001:30 | 133 | 109.8 | 2020 | 99.98 |  |  | Performance - GW inundation | Performance - GW inundation | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00406
YWS00407 | Yorkshire Water | Live | NORTH LANE SPS | NORTH LANE/SPS | 27/24/0230 | 27/24/0230 | A2 | Storm discharge at pumping station | SE5827050200 | 458270 | 450200 | GB104027064001 | Holgate Beck to Ouse | River | 3499 | Upper Ouse Yorkshire | 3088 | Swale, Ure, Nidd and Upper Ouse | TRIB OF HOLGATE BECK | Not Applicable | Not Applicable | Not Applicable | 1:00 | 2 | 0.5 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00407
YWS00408 | Yorkshire Water | Live | GREAT NORTH ROAD NO2 CSO | GREAT NORTH ROAD/NO 2 CSO | 27/24/0239 | 27/24/0239 | A1 | SO on sewer network | SE4436833657 | 444368 | 433657 | GB104027063640 | Mill Dike from Source to Bishop Dike | River | 3280 | Lower Ouse Yorkshire | 3115 | Wharfe and Lower Ouse | SHEEP DIKE | Not Applicable | Not Applicable | Not Applicable | 20:00 | 17 | 14.2 | 2020 | 91.06 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00408
YWS00409 | Yorkshire Water | Live | PIT LANE COMBINED SEWER OVERFLOW | PIT LANE/NO 2 CSO | 27/24/0240 | 27/24/0240 | 1 | SO on sewer network | SE4423033060 | 444238 | 433063 | GB104027063640 | Mill Dike from Source to Bishop Dike | River | 3280 | Lower Ouse Yorkshire | 3115 | Wharfe and Lower Ouse | TRIB OF SHEEP DIKE | Not Applicable | Not Applicable | Not Applicable | 2:00 | 2 | 1.2 | 2020 | 99.88 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00409
YWS00410 | Yorkshire Water | Live | SCHOOL CLOSE SEWAGE PUMPING STATION | SCHOOL CLOSE/CSO | 27/24/0241 | 27/24/0241 | A2 | Storm discharge at pumping station | SE5638765169 | 456387 | 465169 | GB104027063900 | Huby Burn from Source to New Parks Beck | River | 3499 | Upper Ouse Yorkshire | 3088 | Swale, Ure, Nidd and Upper Ouse | TRIBUTARY OF RIVER KYLE | Not Applicable | Not Applicable | Not Applicable | 184:45 | 37 | 21.67 | 2020 | 89.01 | Comms failure / issue | Resolved - Oct | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00410
YWS00411 | Yorkshire Water | Live | SOUTH MILFORD SPS | SOUTH MILFORD/CSO | 27/24/0242 | 27/24/0242 | A2 | Storm discharge at pumping station | SE5026831465 | 450268 | 431465 | GB104027063610 | Upper Fox Drain Catchment ds of Sherburn STW | River | 3280 | Lower Ouse Yorkshire | 3115 | Wharfe and Lower Ouse | CAWDEL HEAD DRAIN (CULVERTED) | Not Applicable | Not Applicable | Not Applicable | 5:00 | 9 | 23.2 | 2020 | 91.35 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00411
YWS00412 | Yorkshire Water | Live | TADCASTER ROAD CSO & BISHOPTHORPE | TADCASTER ROAD/CSO | 27/24/0245 | 27/24/0245 | 1 | Storm discharge at pumping station | SE5913048610 | 449130 | 448610 | GB104027063980 | The Foss Catchment (trib of Wharfe) | River | 3287 | Lower Wharfe | 3115 | Wharfe and Lower Ouse | UNNAMED TRIB OF RIVER OUSE | Not Applicable | Not Applicable | Not Applicable | 161:24 | 20 | 11.4 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00412
YWS00413 | Yorkshire Water | Live | DANESFORT AVENUE CSO | DANESFORT AVENUE/CSO | 27/24/0246 | 27/24/0246 | A1 | SO on sewer network | SE5781250716 | 457812 | 450716 | GB104027064001 | Holgate Beck to Ouse | River | 3499 | Upper Ouse Yorkshire | 3088 | Swale, Ure, Nidd and Upper Ouse | TRIB OF HOLGATE BECK | Not Applicable | Not Applicable | Not Applicable | 3:45 | 2 | 1.8 | 2020 | 98.86 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00413
YWS00414 | Yorkshire Water | Live | POPPLETON ROAD NORTH CSO | POPPLETON ROAD NORTH/CSO | 27/24/0248 | 27/24/0248 | A1 | SO on sewer network | SE5871251555 | 458712 | 451555 | GB104027064001 | Holgate Beck to Ouse | River | 3499 | Upper Ouse Yorkshire | 3088 | Swale, Ure, Nidd and Upper Ouse | CULVERTED HOLGATE BECK | Not Applicable | Not Applicable | Not Applicable | 57:20 | 46 | 51.2 | 2020 | 100 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS00414
YWS00415 | Yorkshire Water | Live | LITTLE OUSEBURN SPS | LITTLE OUSEBURN/NO 2 CSO | 27/24/0249 | 27/24/0249 | A1 | SO on sewer network | SE4499560930 | 444995 | 460930 | GB104027063800 | Ouse from Source to River Ure | River | 3309 | Middle and Lower Ure | 3088 | Swale, Ure, Nidd and Upper Ouse | TRIB OF OUSE GILL BECK | Not Applicable | Not Applicable | Not Applicable | 34:00 | 16 | 8.4 | 2020 | 99.8 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00415
YWS00416 | Yorkshire Water | Live | BROADLANDS FARM NO 2 CSO | BROADLANDS FARM/NO 2 CSO | 27/24/0250 | 27/24/0250 | A1 | SO on sewer network | SE4458760954 | 444587 | 460954 | GB104027063800 | Ouse from Source to River Ure | River | 3309 | Middle and Lower Ure | 3088 | Swale, Ure, Nidd and Upper Ouse | TRIB OF OUSE GILL BECK | Not Applicable | Not Applicable | Not Applicable | 8:30 | 13 | 3.4 | 2020 | 98.98 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00416
YWS00417 | Yorkshire Water | Live | NABURN YORK ROAD SPS | NABURN YORK ROAD/CSO | 27/24/0261 | 27/24/0261 | A2 | Storm discharge at pumping station | SE5978045588 | 459780 | 445588 | GB104027069593 | Ouse from River Nidd to Stillingfleet Beck | River | 3499 | Upper Ouse Yorkshire | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER OUSE | Not Applicable | Not Applicable | Not Applicable | 474:10 | 38 | 33 | 2020 | 99.12 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00417
YWS00418 | Yorkshire Water | Live | POPPLETON ROAD SOUTH 2 CSO | POPPLETON RD SOUTH/2 CSO | 27/24/0264 | 27/24/0264 | A1 | SO on sewer network | SE5871251555 | 458712 | 451554 | GB104027064001 | Holgate Beck to Ouse | River | 3499 | Upper Ouse Yorkshire | 3088 | Swale, Ure, Nidd and Upper Ouse | HOLGATE BECK | Not Applicable | Not Applicable | Not Applicable | 516:20 | 65 | 60.2 | 2020 | 99.98 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS00418
YWS00419 | Yorkshire Water | Live | HAMILTON DRIVE YORK CSO | HAMILTON DRIVE YORK/CSO | 27/24/0285 | 27/24/0285 | A1 | SO on sewer network | SE5873950979 | 458739 | 450979 | GB104027064001 | Holgate Beck to Ouse | River | 3499 | Upper Ouse Yorkshire | 3088 | Swale, Ure, Nidd and Upper Ouse | HOLGATE BECK | Not Applicable | Not Applicable | Not Applicable | 6:15 | 4 | 3.8 | 2020 | 99.81 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00419
YWS00420 | Yorkshire Water | Live | HEWORTH GREEN NO 2 CSO | HEWORTH GREEN/NO 2 CSO | 27/24/0287 | 27/24/0287 | A1 | SO on sewer network | SE6089852505 | 460898 | 452505 | GB104027063520 | Foss from the Syke to the River Ouse | River | 3190 | Foss | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER FOSS | Not Applicable | Not Applicable | Not Applicable | 133:30 | 30 | 22.2 | 2020 | 99.98 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00420
YWS00421 | Yorkshire Water | Live | HOLGATE ROAD NO.2 CSO | HOLGATE ROAD/NO 2 CSO | 27/24/0288 | 27/24/0288 | A1 | SO on sewer network | SE5880051312 | 458800 | 451312 | GB104027064001 | Holgate Beck to Ouse | River | 3499 | Upper Ouse Yorkshire | 3088 | Swale, Ure, Nidd and Upper Ouse | HOLGATE BECK | Not Applicable | Not Applicable | Not Applicable | 522:08 | 64 | 43.2 | 2020 | 100 |  |  | N/A - Ongoing investigation | N/A - Ongoing investigation | UWWTR investigation ongoing, Operational investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00421
YWS00422 | Yorkshire Water | Live | BEECH AVENUE CSO | BEECH AVENUE/CSO | 27/24/0293 | 27/24/0293 | 1 | SO on sewer network | SE5878051100 | 458780 | 451100 | GB104027064001 | Holgate Beck to Ouse | River | 3499 | Upper Ouse Yorkshire | 3088 | Swale, Ure, Nidd and Upper Ouse | HOLGATE BECK VIA PUBLIC SEWER | Not Applicable | Not Applicable | Not Applicable | 20:30 | 10 | 5.6 | 2020 | 96.04 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00422
YWS00423 | Yorkshire Water | Live | SHERBURN OLD WORKS CSO | SHERBURN OLD WORKS/CSO | 27/24/0295 | 27/24/0295 | A1 | SO on sewer network | SE4983733468 | 449837 | 433468 | GB104027063640 | Mill Dike from Source to Bishop Dike | River | 3280 | Lower Ouse Yorkshire | 3115 | Wharfe and Lower Ouse | CULVERTED GREEN DIKE | Not Applicable | Not Applicable | Not Applicable | 5:45 | 8 | 7.4 | 2020 | 99.9 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00423
YWS00424 | Yorkshire Water | Live | YORK ROAD BARBLY NO2 CSO | YORK ROAD BARLBY/NO 2 CSO | 27/24/0296 | 27/24/0296 | A1 | SO on sewer network | SE6308033510 | 463045 | 433629 | GB104027064270 | Ouse from R Wharfe to Upper Humber | River | 3280 | Lower Ouse Yorkshire | 3115 | Wharfe and Lower Ouse | UNNAMED TRIB OF CHERRY ORCHARD | Not Applicable | Not Applicable | Not Applicable | 104:45 | 24 | 22.2 | 2020 | 99.68 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00424
YWS00425 | Yorkshire Water | Live | BRECKSFIELD NO 2 CSO | BRECKSFIELD/NO 2 CSO | 27/24/0303 | 27/24/0303 | A1 | SO on sewer network | SE5738556364 | 457385 | 456364 | GB104027069593 | Ouse from River Nidd to Stillingfleet Beck | River | 3499 | Upper Ouse Yorkshire | 3088 | Swale, Ure, Nidd and Upper Ouse | BURTREE DAM | Not Applicable | Not Applicable | Not Applicable | 22:00 | 5 | 8.4 | 2020 | 13 | Sensor failure / issue | Scheduled | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00425
YWS00426 | Yorkshire Water | Live | OULSTON SEWAGE TREATMENT WORKS | OULSTON/STW | 27/24/0311 | 27/24/0311 | A2 | Inlet SO at WwTW | SE5478074020 | 454780 | 474020 | GB104027068270 | Kyle from Source to Alne Beck | River | 3499 | Upper Ouse Yorkshire | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER KYLE | Not Applicable | Not Applicable | Not Applicable | 166:15 | 76 | 59.6 | 2020 | 100 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00426
YWS00427 | Yorkshire Water | Live | TOLLERTON SEWAGE TREATMENT WORKS | TOLLERTON/STW | 27/24/0321 | 27/24/0321 | A2 | Storm tank at WwTW | SE5110064983 | 451110 | 464983 | GB104027063860 | Kyle from Derrings Beck to New Parks Beck | River | 3499 | Upper Ouse Yorkshire | 3088 | Swale, Ure, Nidd and Upper Ouse | SIDINGS DRAIN | Not Applicable | Not Applicable | Not Applicable | 220:00 | 56 | 65.6 | 2020 | 99.97 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation ongoing | Operational improvement ongoing | SOAF investigation ongoing | YWS00427
YWS00428 | Yorkshire Water | Live | ASKHAM BRYAN STW | ASKHAM BRYAN/STW | 27/24/0322 | 27/24/0322 | 2 | Storm tank at WwTW | SE5586047850 | 455820 | 447900 | GB104027064001 | Holgate Beck to Ouse | River | 3499 | Upper Ouse Yorkshire | 3088 | Swale, Ure, Nidd and Upper Ouse | FOSS DIKE | Not Applicable | Not Applicable | Not Applicable | 877:30 | 77 | 74.2 | 2020 | 100 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00428
YWS00429 | Yorkshire Water | Live | FLAWITH SEWAGE TREATMENT WORKS | FLAWITH/STW | 27/24/0330 | 27/24/0330 | 2 | Inlet SO at WwTW | SE4847065420 | 448470 | 465420 | GB104027063860 | Kyle from Derrings Beck to New Parks Beck | River | 3499 | Upper Ouse Yorkshire | 3088 | Swale, Ure, Nidd and Upper Ouse | UNNAMED TRIB OF RIVER KYLE | Not Applicable | Not Applicable | Not Applicable | 363:00 | 101 | 94.6 | 2020 | 99.98 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation ongoing | Operational improvement ongoing | SOAF investigation ongoing | YWS00429
YWS00430 | Yorkshire Water | Live | RUFFORTH STW | RUFFORTH/STW | 27/24/0337 | 27/24/0337 | A2 | Inlet SO at WwTW | SE5368352263 | 453683 | 452263 | GB104027063720 | Foss Dike | River | 3499 | Upper Ouse Yorkshire | 3088 | Swale, Ure, Nidd and Upper Ouse | SMAWITH DIKE | Not Applicable | Not Applicable | Not Applicable | 267:45 | 26 | 19.2 | 2020 | 99.98 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00430
YWS00431 | Yorkshire Water | Live | BARLBY SEWAGE TREATMENT WORKS | BARLBY/STW | 27/24/0338 | 27/24/0338 | A2 | Storm tank at WwTW | SE6263335418 | 462633 | 435418 | GB104027064270 | Ouse from R Wharfe to Upper Humber | River | 3280 | Lower Ouse Yorkshire | 3115 | Wharfe and Lower Ouse | RIVER OUSE (TIDAL) | Not Applicable | Not Applicable | Not Applicable | 353:00 | 63 | 52.8 | 2020 | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement completed | SOAF investigation ongoing | YWS00431
YWS00432 | Yorkshire Water | Live | MAYFIELD GROVE CSO | MAYFIELD GROVE/CSO | 27/24/0344 | 27/24/0344 | A1 | SO on sewer network | SE5853549875 | 458535 | 449875 | GB104027064001 | Holgate Beck to Ouse | River | 3499 | Upper Ouse Yorkshire | 3088 | Swale, Ure, Nidd and Upper Ouse | TRIB OF HOLGATE BECK | Not Applicable | Not Applicable | Not Applicable | 39:30 | 18 | 15.2 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00432
YWS00433 | Yorkshire Water | Live | WEST LILLING SPS | WEST LILLING/CSO | 27/24/0357 | 27/24/0357 | 1 | Storm discharge at pumping station | SE6496064850 | 464960 | 464850 | GB104027063540 | Foss from Farlington Beck to the Syke | River | 3190 | Foss | 3088 | Swale, Ure, Nidd and Upper Ouse | TRIB OF BLACK DIKE | Not Applicable | Not Applicable | Not Applicable | 3260:30 | 174 | 124.4 | 2020 | 100 |  |  | Performance - Infiltration | Performance - Infiltration | UWWTR investigation ongoing, Operational investigation completed | Operational improvement ongoing | SOAF investigation ongoing | YWS00433
YWS00434 | Yorkshire Water | Live | RASKELF STW | RASKELF/STW | 27/24/0362 | 27/24/0362 | A2 | Inlet SO at WwTW | SE4963070584 | 449630 | 470584 | GB104027068270 | Kyle from Source to Alne Beck | River | 3499 | Upper Ouse Yorkshire | 3088 | Swale, Ure, Nidd and Upper Ouse | THE KYLE | Not Applicable | Not Applicable | Not Applicable | 97:15 | 18 | 12.6 | 2020 | 99.7 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00434
YWS00435 | Yorkshire Water | Live | SHERIFF HUTTON STW | SHERIFF HUTTON/STW | 27/24/0363 | 27/24/0363 | A2 | Storm tank at WwTW | SE6439065580 | 464393 | 465598 | GB104027063540 | Foss from Farlington Beck to the Syke | River | 3190 | Foss | 3088 | Swale, Ure, Nidd and Upper Ouse | HOWL BECK | Not Applicable | Not Applicable | Not Applicable | 438:30 | 55 | 73.2 | 2020 | 99.61 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00435
YWS00436 | Yorkshire Water | Live | SHERIFF HUTTON STW | SHERIFF HUTTON/STW | 27/24/0363 | 27/24/0363 | A3 | Inlet SO at WwTW | SE6439065580 | 464393 | 465598 | GB104027063540 | Foss from Farlington Beck to the Syke | River | 3190 | Foss | 3088 | Swale, Ure, Nidd and Upper Ouse | HOWL BECK | Not Applicable | Not Applicable | Not Applicable | 29:15 | 12 | 15.4 | 2020 | 99.62 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00436
YWS00437 | Yorkshire Water | Live | BARLOW SEWAGE TREATMENT WORKS | SELBY BARLOW/NO 2 STW | 27/24/0368 | 27/24/0368 | A2 | Inlet SO at WwTW | SE6480028270 | 464800 | 428270 | GB104027064270 | Ouse from R Wharfe to Upper Humber | River | 3280 | Lower Ouse Yorkshire | 3115 | Wharfe and Lower Ouse | LENDALL CARR DYKE | Not Applicable | Not Applicable | Not Applicable | 158:45 | 17 | 26.4 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00437
YWS00438 | Yorkshire Water | Live | FLAXTON SEWAGE TREATMENT WORKS | FLAXTON/STW | 27/24/0369 | 27/24/0369 | A2 | Inlet SO at WwTW | SE6806061480 | 468060 | 461480 | GB104027063530 | The Syke from Source to River Foss | River | 3190 | Foss | 3088 | Swale, Ure, Nidd and Upper Ouse | UNNAMED TRIB OF THE SIKE | Not Applicable | Not Applicable | Not Applicable | 281:45 | 69 | 104.2 | 2020 | 99.68 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00438
YWS00439 | Yorkshire Water | Live | ASSELBY COMBINED SEWER OVERFLOW | ASSELBY/STW/6XDWF OVERFLOW | 27/24/0403 | 27/24/0403 | A1 | Inlet SO at WwTW | SE7194028230 | 471943 | 428234 | Not part of a WFD catchment | Not part of a WFD catchment | River | N/A | N/A | N/A | N/A | UNNAMED TRIB OF RIVER OUSE | Not Applicable | Not Applicable | Not Applicable | 111:45 | 38 | 37 | 2020 | 99.74 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00439
YWS00440 | Yorkshire Water | Live | HAXBY STORM TANKS STW | HAXBY STORM TANKS/STW | 27/24/0404 | 27/24/0404 | A1 | Storm tank at WwTW | SE6163057610 | 461630 | 457610 | GB104027063520 | Foss from the Syke to the River Ouse | River | 3190 | Foss | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER FOSS | Not Applicable | Not Applicable | Not Applicable | 933:45 | 65 | 41.2 | 2020 | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00440
YWS00441 | Yorkshire Water | Live | COPMANTHORPE SEWAGE PUMPING STATION | COPMANTHORPE/CSO | 27/24/0407 | 27/24/0407 | 1 | Storm discharge at pumping station | SE5701046900 | 457010 | 446900 | GB104027064002 | The Fleet/The Foss from Source to R Wharfe | River | 3287 | Lower Wharfe | 3115 | Wharfe and Lower Ouse | TOWN INGS DRAIN | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00441
YWS00442 | Yorkshire Water | Live | LENDAL HILL COMBINED SEWER OVERFLOW | LENDAL HILL/CSO | 27/24/0417 | 27/24/0417 | A1 | SO on sewer network | SE5999451950 | 459994 | 451950 | GB104027069593 | Ouse from River Nidd to Stillingfleet Beck | River | 3499 | Upper Ouse Yorkshire | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER OUSE | Not Applicable | Not Applicable | Not Applicable | 1296:04 | 108 | 100 | 2020 | 100 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS00442
YWS00443 | Yorkshire Water | Live | COMMON HALL LANE CSO | COMMON HALL LANE/CSO | 27/24/0418 | 27/24/0418 | A1 | SO on sewer network | SE6008051888 | 460080 | 451888 | GB104027069593 | Ouse from River Nidd to Stillingfleet Beck | River | 3499 | Upper Ouse Yorkshire | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER OUSE | Not Applicable | Not Applicable | Not Applicable | 55:10 | 7 | 9.4 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00443
YWS00444 | Yorkshire Water | Live | WOOLWORTHS CSO | WOOLWORTHS/CSO | 27/24/0419 | 27/24/0419 | A1 | SO on sewer network | SE6022051700 | 460220 | 451704 | GB104027069593 | Ouse from River Nidd to Stillingfleet Beck | River | 3499 | Upper Ouse Yorkshire | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER OUSE | Not Applicable | Not Applicable | Not Applicable | 3602:15 | 194 | 153.6 | 2020 | 99.78 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement completed | SOAF investigation ongoing | YWS00444
YWS00445 | Yorkshire Water | Live | SKELDERGATE BRIDGE CSO | SKELDERGATE BRIDGE/CSO | 27/24/0420 | 27/24/0420 | A1 | SO on sewer network | SE6040051315 | 460400 | 451315 | GB104027069593 | Ouse from River Nidd to Stillingfleet Beck | River | 3499 | Upper Ouse Yorkshire | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER OUSE | Not Applicable | Not Applicable | Not Applicable | 12:46 | 48 | 28 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | SOAF investigation completed - No work required | YWS00445
YWS00446 | Yorkshire Water | Live | FISHERGATE CSO | FISHERGATE/CSO | 27/24/0421 | 27/24/0421 | A1 | SO on sewer network | SE6074051004 | 460740 | 451004 | GB104027063520 | Foss from the Syke to the River Ouse | River | 3190 | Foss | 3088 | Swale, Ure, Nidd and Upper Ouse | TANG HALL BECK | Not Applicable | Not Applicable | Not Applicable | 190:12 | 9 | 93.4 | 2020 | 5.58 | Sensor failure / issue | Scheduled | High spill threshold not met | Not asset maintenance - Hydraulic capacity | Operational investigation completed | Operational improvement completed | SOAF investigation completed - No work required | YWS00446
YWS00447 | Yorkshire Water | Live | HARTOFT STREET CSO | HARTOFT STREET/CSO | 27/24/0422 | 27/24/0422 | A1 | SO on sewer network | SE6057550671 | 460577 | 450668 | GB104027069593 | Ouse from River Nidd to Stillingfleet Beck | River | 3499 | Upper Ouse Yorkshire | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER OUSE | Not Applicable | Not Applicable | Not Applicable | 7:24 | 35 | 23.2 | 2020 | 65.1 | Sensor failure / issue | Resolved - Sep | High spill threshold not met | High spill threshold not met | Operational investigation completed | Operational improvement completed | No SOAF investigation required | YWS00447
YWS00448 | Yorkshire Water | Live | FARNDALE STREET CSO | FARNDALE STREET/CSO | 27/24/0423 | 27/24/0423 | A1 | SO on sewer network | SE6055850628 | 460558 | 450628 | GB104027069593 | Ouse from River Nidd to Stillingfleet Beck | River | 3499 | Upper Ouse Yorkshire | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER OUSE | Not Applicable | Not Applicable | Not Applicable | 19:08 | 13 | 13.2 | 2020 | 99.57 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00448
YWS00449 | Yorkshire Water | Live | NEW WALK CSO | NEW WALK/CSO | 27/24/0424 | 27/24/0424 | A1 | SO on sewer network | SE6043350373 | 460433 | 450373 | GB104027069593 | Ouse from River Nidd to Stillingfleet Beck | River | 3499 | Upper Ouse Yorkshire | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER OUSE | Not Applicable | Not Applicable | Not Applicable | 238:22 | 22 | 12.33 | 2020 | 33.61 | Sensor failure / issue | Resolved - Aug | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00449
YWS00450 | Yorkshire Water | Live | SKELDERGATE BRIDGE CSO | SKELDERGATE/CSO | 27/24/0426 | 27/24/0426 | A1 | SO on sewer network | SE6034851297 | 460348 | 451297 | GB104027069593 | Ouse from River Nidd to Stillingfleet Beck | River | 3499 | Upper Ouse Yorkshire | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER OUSE | Not Applicable | Not Applicable | Not Applicable | 598:52 | 46 | 63.6 | 2020 | 48.96 | Sensor failure / issue | Resolved - Jul | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00450
YWS00451 | Yorkshire Water | Live | TERRY AVENUE CSO | TERRY AVENUE/CSO | 27/24/0427 | 27/24/0427 | A1 | SO on sewer network | SE6049251039 | 460504 | 451024 | GB104027069593 | Ouse from River Nidd to Stillingfleet Beck | River | 3499 | Upper Ouse Yorkshire | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER OUSE | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0 | 2020 | 67.12 | Sensor failure / issue | Resolved - Apr | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | SOAF investigation completed - No work required | YWS00451
YWS00452 | Yorkshire Water | Live | BUTCHER TERRACE CSO | BUTCHER TERRACE/CSO | 27/24/0428 | 27/24/0428 | A1 | SO on sewer network | SE6033350288 | 460333 | 450288 | GB104027069593 | Ouse from River Nidd to Stillingfleet Beck | River | 3499 | Upper Ouse Yorkshire | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER OUSE | Not Applicable | Not Applicable | Not Applicable | 1435:00 | 102 | 83 | 2020 | 99.98 |  |  | Performance - Infiltration | Performance - Infiltration | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS00452
YWS00454 | Yorkshire Water | Live | HUNTINGTON ROAD CSO | HUNTINGTON ROAD/CSO | 27/24/0430 | 27/24/0430 | A1 | SO on sewer network | SE6088152570 | 460881 | 452570 | GB104027063520 | Foss from the Syke to the River Ouse | River | 3190 | Foss | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER FOSS | Not Applicable | Not Applicable | Not Applicable | 30:45 | 16 | 13.6 | 2020 | 99.97 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00454
YWS00455 | Yorkshire Water | Live | LAYERTHORPE BRIDGE CSO | LAYERTHORPE BRIDGE/CSO | 27/24/0431 | 27/24/0431 | A1 | SO on sewer network | SE6086252080 | 460862 | 452080 | GB104027063520 | Foss from the Syke to the River Ouse | River | 3190 | Foss | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER FOSS | Not Applicable | Not Applicable | Not Applicable | 54:52 | 34 | 70.4 | 2020 | 82.62 | Sensor failure / issue | Resolved - Dec | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement ongoing | SOAF investigation ongoing | YWS00455
YWS00456 | Yorkshire Water | Live | PICCADILLY CSO | PICCADILLY/CSO | 27/24/0432 | 27/24/0432 | A1 | SO on sewer network | SE6055451637 | 460554 | 451637 | GB104027063520 | Foss from the Syke to the River Ouse | River | 3190 | Foss | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER FOSS | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 13 | 2020 | 86.06 | Sensor failure / issue | Resolved - Dec | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00456
YWS00457 | Yorkshire Water | Live | FOSS ISLANDS ROAD CSO | FOSS ISLANDS ROAD/CSO | 27/24/0433 | 27/24/0433 | A1 | SO on sewer network | SE6090051771 | 460900 | 451771 | GB104027063520 | Foss from the Syke to the River Ouse | River | 3190 | Foss | 3088 | Swale, Ure, Nidd and Upper Ouse | TANG HALL BECK | Not Applicable | Not Applicable | Not Applicable | 238:26 | 47 | 46.6 | 2020 | 99.99 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00457
YWS00458 | Yorkshire Water | Live | NAVIGATION ROAD CSO | NAVIGATION ROAD/CSO | 27/24/0434 | 27/24/0434 | A1 | SO on sewer network | SE6092651736 | 460926 | 451736 | GB104027063500 | Tang Hall Bk/Old Foss Bk catch, trib of River Foss | River | 3190 | Foss | 3088 | Swale, Ure, Nidd and Upper Ouse | TANG HALL BECK | Not Applicable | Not Applicable | Not Applicable | 2038:24 | 186 | 70.8 | 2020 | 99.14 |  |  | Data collection - Tidal / river inundation | Data collection - Tidal / river inundation | UWWTR investigation ongoing, Operational investigation ongoing | Operational improvement ongoing | SOAF investigation ongoing | YWS00458
YWS00459 | Yorkshire Water | Live | HULL ROAD YORK CSO | HULL ROAD YORK/CSO | 27/24/0435 | 27/24/0435 | A1 | SO on sewer network | SE6205651426 | 462056 | 451426 | GB104027063500 | Tang Hall Bk/Old Foss Bk catch, trib of River Foss | River | 3190 | Foss | 3088 | Swale, Ure, Nidd and Upper Ouse | OSBALDWICK BECK | Not Applicable | Not Applicable | Not Applicable | 0:54 | 5 | 8.6 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00459
YWS00460 | Yorkshire Water | Live | WALMGATE CSO | WALMGATE/CSO | 27/24/0436 | 27/24/0436 | A1 | SO on sewer network | SE6088551519 | 460885 | 451519 | GB104027063500 | Tang Hall Bk/Old Foss Bk catch, trib of River Foss | River | 3190 | Foss | 3088 | Swale, Ure, Nidd and Upper Ouse | TANG HALL BECK | Not Applicable | Not Applicable | Not Applicable | 25:36 | 18 | 16.4 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00460
YWS00461 | Yorkshire Water | Live | KNAVESMIRE ROAD CSO | KNAVESMIRE ROAD/CSO | 27/24/0437 | 27/24/0437 | A1 | SO on sewer network | SE5926050438 | 459260 | 450438 | GB104027064001 | Holgate Beck to Ouse | River | 3499 | Upper Ouse Yorkshire | 3088 | Swale, Ure, Nidd and Upper Ouse | TRIBUTARY OF RIVER OUSE | Not Applicable | Not Applicable | Not Applicable | 327:10 | 45 | 66.25 | 2020 | 99.95 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement completed | SOAF investigation ongoing | YWS00461
YWS00462 | Yorkshire Water | Live | HAMILTON DRIVE WEST CSO | HAMILTON DRIVE WEST/CSO | 27/24/0438 | 27/24/0438 | A1 | SO on sewer network | SE5786050740 | 457868 | 450740 | GB104027064001 | Holgate Beck to Ouse | River | 3499 | Upper Ouse Yorkshire | 3088 | Swale, Ure, Nidd and Upper Ouse | HOLGATE BECK | Not Applicable | Not Applicable | Not Applicable | 11:45 | 16 | 9.25 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00462
YWS00463 | Yorkshire Water | Live | MARYGATE LANE CSO | MARYGATE LANE/CSO | 27/24/0449 | 27/24/0449 | A1 | SO on sewer network | SE5960052080 | 459600 | 452080 | GB104027069593 | Ouse from River Nidd to Stillingfleet Beck | River | 3499 | Upper Ouse Yorkshire | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER OUSE | Not Applicable | Not Applicable | Not Applicable | 657:52 | 71 | 39.4 | 2020 | 98.49 |  |  | Performance - Infiltration | High spill threshold not met | UWWTR investigation ongoing, Operational investigation ongoing | Operational improvement ongoing | SOAF investigation ongoing | YWS00463
YWS00464 | Yorkshire Water | Live | PORTLAND STREET CSO | PORTLAND STREET/CSO | 27/24/0450 | 27/24/0450 | A1 | SO on sewer network | SE5960652083 | 459606 | 452083 | GB104027069593 | Ouse from River Nidd to Stillingfleet Beck | River | 3499 | Upper Ouse Yorkshire | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER OUSE | Not Applicable | Not Applicable | Not Applicable | 320:56 | 74 | 15 | 2020 | 94.91 |  |  | N/A - Ongoing investigation | High spill threshold not met | UWWTR investigation ongoing, Operational investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00464
YWS00465 | Yorkshire Water | Live | BOOTHAM HOSPITAL CSO | BOOTHAM HOSPITAL/CSO | 27/24/0451 | 27/24/0451 | A1 | SO on sewer network | SE5960520830 | 459606 | 452083 | GB104027069593 | Ouse from River Nidd to Stillingfleet Beck | River | 3499 | Upper Ouse Yorkshire | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER OUSE | Not Applicable | Not Applicable | Not Applicable | 20:08 | 13 | 9.2 | 2020 | 99.97 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00465
YWS00466 | Yorkshire Water | Live | GROSVENOR TERRACE CSO | GROSVENOR TERRACE/CSO | 27/24/0452 | 27/24/0452 | A1 | SO on sewer network | SE5960520830 | 459606 | 452083 | GB104027069593 | Ouse from River Nidd to Stillingfleet Beck | River | 3499 | Upper Ouse Yorkshire | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER OUSE | Not Applicable | Not Applicable | Not Applicable | 5:18 | 10 | 50.25 | 2020 | 100 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | No investigation activity in reporting period | No improvement action in reporting period | SOAF investigation completed - No work required | YWS00466
YWS00467 | Yorkshire Water | Live | QUEEN STREET BRIDGE CSO | QUEEN STREET BRIDGE/CSO | 27/24/0453 | 27/24/0453 | A1 | SO on sewer network | SE5995051914 | 459950 | 451914 | GB104027069593 | Ouse from River Nidd to Stillingfleet Beck | River | 3499 | Upper Ouse Yorkshire | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER OUSE | Not Applicable | Not Applicable | Not Applicable | 19:16 | 4 | 21.4 | 2020 | 30.17 | Capital / maintenance works affect EDM operation | Scheduled | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00467
YWS00468 | Yorkshire Water | Live | STATION ROAD CSO | YORK STATION ROAD/CSO | 27/24/0454 | 27/24/0454 | A1 | SO on sewer network | SE5995051914 | 459950 | 451914 | GB104027069593 | Ouse from River Nidd to Stillingfleet Beck | River | 3499 | Upper Ouse Yorkshire | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER OUSE | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0 | 2020 | 99.12 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00468
YWS00469 | Yorkshire Water | Live | ROYAL YORK HOTEL NO.2 CSO | ROYAL YORK HOTEL/NO 2 CSO | 27/24/0455 | 27/24/0455 | A1 | SO on sewer network | SE5995051914 | 459950 | 451914 | GB104027069593 | Ouse from River Nidd to Stillingfleet Beck | River | 3499 | Upper Ouse Yorkshire | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER OUSE | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0.67 | 2020 | 99.12 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00469
YWS00470 | Yorkshire Water | Live | ROYAL YORK HOTEL NO.1 CSO | ROYAL YORK HOTEL/NO 1 CSO | 27/24/0457 | 27/24/0457 | A1 | SO on sewer network | SE5995051914 | 459950 | 451914 | GB104027069593 | Ouse from River Nidd to Stillingfleet Beck | River | 3499 | Upper Ouse Yorkshire | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER OUSE | Not Applicable | Not Applicable | Not Applicable | 0:18 | 1 | 0.2 | 2020 | 99.12 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00470
YWS00471 | Yorkshire Water | Live | LANDING LANE CSO | YORK LANDING LANE/CSO | 27/24/0458 | 27/24/0458 | A1 | SO on sewer network | SE5834752566 | 458347 | 452566 | GB104027069593 | Ouse from River Nidd to Stillingfleet Beck | River | 3499 | Upper Ouse Yorkshire | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER OUSE | Not Applicable | Not Applicable | Not Applicable | 106:00 | 33 | 20.2 | 2020 | 99.52 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00471
YWS00472 | Yorkshire Water | Live | QUEENS STAITH CSO | QUEENS STAITH/CSO | 27/24/0459 | 27/24/0459 | A1 | SO on sewer network | SE6020451590 | 460204 | 451590 | GB104027069593 | Ouse from River Nidd to Stillingfleet Beck | River | 3499 | Upper Ouse Yorkshire | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER OUSE | Not Applicable | Not Applicable | Not Applicable |  |  | 60.25 | 2020 | 0 | Sensor failure / issue | Scheduled | High spill threshold not met | Performance - Infiltration | UWWTR investigation ongoing, Operational investigation ongoing | Operational improvement ongoing | SOAF investigation ongoing | YWS00472
YWS00473 | Yorkshire Water | Live | KITCHENER STREET CSO | KITCHENER STREET/CSO | 27/24/0460 | 27/24/0460 | A1 | SO on sewer network | SE6088653229 | 460886 | 453229 | GB104027063520 | Foss from the Syke to the River Ouse | River | 3190 | Foss | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER FOSS | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0.25 | 2020 | 92.88 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00473
YWS00474 | Yorkshire Water | Live | ASHVILLE STREET CSO | ASHVILLE STREET/CSO | 27/24/0461 | 27/24/0461 | 1 | SO on sewer network | SE6088053221 | 460912 | 453309 | GB104027063520 | Foss from the Syke to the River Ouse | River | 3190 | Foss | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER FOSS | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0 | 2020 | 82.88 | Sensor failure / issue | Scheduled | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00474
YWS00475 | Yorkshire Water | Live | OAKVILLE STREET CSO | OAKVILLE STREET/CSO | 27/24/0462 | 27/24/0462 | A1 | SO on sewer network | SE6091353309 | 460913 | 453309 | GB104027063520 | Foss from the Syke to the River Ouse | River | 3190 | Foss | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER FOSS | Not Applicable | Not Applicable | Not Applicable |  |  | 0 | 2020 | 0 | Power failure / issue | Scheduled | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00475
YWS00476 | Yorkshire Water | Live | MILNER STREET CSO | MILNER STREET/CSO | 27/24/0463 | 27/24/0463 | A1 | SO on sewer network | SE5778851290 | 457788 | 451290 | GB104027064001 | Holgate Beck to Ouse | River | 3499 | Upper Ouse Yorkshire | 3088 | Swale, Ure, Nidd and Upper Ouse | CULVERTED TRIB HOLGATE BECK | Not Applicable | Not Applicable | Not Applicable | 7:00 | 14 | 3.6 | 2020 | 99.63 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00476
YWS00477 | Yorkshire Water | Live | MILL HILL SEWAGE PUMPING STATION | MILL HILL/CSO | 27/24/0464 | 27/24/0464 | A2 | Storm discharge at pumping station | SE6167055790 | 461670 | 455790 | GB104027063520 | Foss from the Syke to the River Ouse | River | 3190 | Foss | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER FOSS | Not Applicable | Not Applicable | Not Applicable | 121:30 | 25 | 19.8 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00477
YWS00478 | Yorkshire Water | Live | RIVERSIDE GARDENS SPS | RIVERSIDE GARDENS/CSO | 27/24/0465 | 27/24/0465 | A2 | Storm discharge at pumping station | SE5569654982 | 455696 | 454982 | GB104027069593 | Ouse from River Nidd to Stillingfleet Beck | River | 3499 | Upper Ouse Yorkshire | 3088 | Swale, Ure, Nidd and Upper Ouse | A TRIBUTARY OF THE RIVER OUSE | Not Applicable | Not Applicable | Not Applicable | 1054:38 | 110 | 71.2 | 2020 | 100 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation completed, Operational investigation completed | Operational improvement ongoing | SOAF investigation completed - No work required | YWS00478
YWS00479 | Yorkshire Water | Live | MILLFIELD LANE CSO | MILLFIELD LANE YORK/CSO | 27/24/0466 | 27/24/0466 | A1 | SO on sewer network | SE5661053910 | 456619 | 453913 | GB104027069593 | Ouse from River Nidd to Stillingfleet Beck | River | 3499 | Upper Ouse Yorkshire | 3088 | Swale, Ure, Nidd and Upper Ouse | TRIB RIVER OUSE | Not Applicable | Not Applicable | Not Applicable | 87:42 | 33 | 36.8 | 2020 | 99.68 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00479
YWS00480 | Yorkshire Water | Live | OUTGANG ROAD SPS | OUTGANG ROAD/CSO | 27/25/0074 | 27/25/0074 | 2 | SO on sewer network | SE8056083360 | 480670 | 482770 | GB104027068460 | The Syme form Source to Thornton | River | 3489 | Upper Derwent Yorkshire | 3027 | Derwent Humber | OUTGANG DRAIN | Not Applicable | Not Applicable | Not Applicable | 41:15 | 26 | 36.2 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00480
YWS00481 | Yorkshire Water | Live | PICKERING SEWAGE TREATMENT WORKS | PICKERING/STW/3XDWF OVERFLOW | 27/25/0075 | 27/25/0075 | 2 | Storm tank at WwTW | SE7746083680 | 477460 | 483680 | GB104027068480 | Costa Beck from Source to Pickering Beck | River | 3387 | Rye | 3027 | Derwent Humber | COSTA BECK | Not Applicable | Not Applicable | Not Applicable | 256:15 | 47 | 71 | 2020 | 99.97 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00481
YWS00482 | Yorkshire Water | Live | PICKERING SEWAGE TREATMENT WORKS | PICKERING/STW/6XDWF OVERFLOW | 27/25/0075 | 27/25/0075 | 3 | Inlet SO at WwTW | SE7746083680 | 477460 | 483680 | GB104027068480 | Costa Beck from Source to Pickering Beck | River | 3387 | Rye | 3027 | Derwent Humber | COSTA BECK | Not Applicable | Not Applicable | Not Applicable | 55:45 | 35 | 44.6 | 2020 | 99.88 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00482
YWS00483 | Yorkshire Water | Live | KIRKBYMOORSIDE STW | KIRKBYMOORSIDE/STW | 27/25/0078 | 27/25/0078 | 2 | Storm tank at WwTW | SE7045085680 | 470440 | 485680 | GB104027068260 | Dove from Source to Hodge Beck | River | 3387 | Rye | 3027 | Derwent Humber | RIVER DOVE | Not Applicable | Not Applicable | Not Applicable | 391:30 | 48 | 76.75 | 2020 | 95.1 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00483
YWS00484 | Yorkshire Water | Live | HAROME SEWAGE TREATMENT WORKS | HAROME/STW | 27/25/0079 | 27/25/0079 | A2 | Storm tank at WwTW | SE6598082150 | 465930 | 482160 | GB104027068210 | Walmouth Beck from Source to River Riccal | River | 3387 | Rye | 3027 | Derwent Humber | HAROME MOOR DRAIN | Not Applicable | Not Applicable | Not Applicable | 2190:15 | 142 | 116.2 | 2020 | 99.97 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS00484
YWS00485 | Yorkshire Water | Live | HELMSLEY SEWAGE TREATMENT WORKS | HELMSLEY/STW | 27/25/0082 | 27/25/0082 | A2 | Storm tank at WwTW | SE6235082880 | 462352 | 482883 | GB104027068200 | Rye from River Seph to Holbeck | River | 3387 | Rye | 3027 | Derwent Humber | RIVER RYE | Not Applicable | Not Applicable | Not Applicable | 298:15 | 59 | 58.6 | 2020 | 99.97 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation ongoing | Operational improvement ongoing | SOAF investigation ongoing | YWS00485
YWS00486 | Yorkshire Water | Live | KIRBY MISPERTON STW | KIRBY MISPERTON/STW | 27/25/0083 | 27/25/0083 | 2 | Inlet SO at WwTW | SE7871079420 | 478710 | 479420 | GB104027068401 | Costa Beck from Pickering Beck to R Rye/Ackland Beck | River | 3387 | Rye | 3027 | Derwent Humber | COSTA BECK | Not Applicable | Not Applicable | Not Applicable | 1920:00 | 135 | 128.6 | 2020 | 100 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation ongoing | Operational improvement ongoing | SOAF investigation ongoing | YWS00486
YWS00487 | Yorkshire Water | Live | MARTON BRIDGE SEWAGE PUMPING STATIO | MARTON BRIDGE/CSO | 27/25/0085 | 27/25/0085 | 1 | Storm discharge at pumping station | SE7329083180 | 473290 | 483180 | GB104027068440 | Seven from Catter Beck to River Rye | River | 3387 | Rye | 3027 | Derwent Humber | RIVER SEVEN | Not Applicable | Not Applicable | Not Applicable | 50:00 | 7 | 40.5 | 2020 | 95.24 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement ongoing | SOAF investigation ongoing | YWS00487
YWS00488 | Yorkshire Water | Live | MALTON HAROME SPS | MALTON HAROME/CSO | 27/25/0092 | 27/25/0092 | A2 | Storm discharge at pumping station | SE6479681523 | 464796 | 481523 | GB104027068220 | Riccal from Bogmire Gill to R Rye | River | 3387 | Rye | 3027 | Derwent Humber | RIVER RICCALL | Not Applicable | Not Applicable | Not Applicable | 8:15 | 5 | 4.8 | 2020 | 99.97 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00488
YWS00489 | Yorkshire Water | Live | KIRKBY MILLS SEWAGE PUMPING STATION | KIRKBY MILLS/CSO | 27/25/0094 | 27/25/0094 | 1 | Storm discharge at pumping station | SE7045185680 | 470450 | 485690 | GB104027068260 | Dove from Source to Hodge Beck | River | 3387 | Rye | 3027 | Derwent Humber | RIVER DOVE | Not Applicable | Not Applicable | Not Applicable | 8:45 | 3 | 0.6 | 2020 | 99.14 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00489
YWS00490 | Yorkshire Water | Live | RAILWAY STREET SPS | RAILWAY ST SLINGSBY/CSO | 27/25/0096 | 27/25/0096 | 1 | Storm discharge at pumping station | SE6980075350 | 469800 | 475350 | GB104027068330 | Wath Beck from Souce to Holbeck | River | 3387 | Rye | 3027 | Derwent Humber | WATH BECK | Not Applicable | Not Applicable | Not Applicable | 12:30 | 5 | 5.6 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00490
YWS00491 | Yorkshire Water | Live | GREAT BARUGH SEWAGE TREATMENT WORKS | GREAT BARUGH/STW | 27/25/0097 | 27/25/0097 | A2 | Inlet SO at WwTW | SE7456078940 | 474560 | 478940 | GB104027068440 | Seven from Catter Beck to River Rye | River | 3387 | Rye | 3027 | Derwent Humber | UNNAMED TRIB OF THE SEVEN | Not Applicable | Not Applicable | Not Applicable | 358:15 | 35 | 28 | 2020 | 99.53 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00491
YWS00492 | Yorkshire Water | Live | LITTLE BARUGH SEWAGE TREATMENT WORK | LITTLE BARUGH/STW | 27/25/0111 | 27/25/0111 | 2 | Inlet SO at WwTW | SE7600079380 | 476000 | 479380 | GB104027068440 | Seven from Catter Beck to River Rye | River | 3387 | Rye | 3027 | Derwent Humber | UNNAMED TRIB OF COSTA BECK | Not Applicable | Not Applicable | Not Applicable | 126:15 | 26 | 38.4 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00492
YWS00493 | Yorkshire Water | Live | HOVINGHAM SEWAGE TREATMENT WORKS | HOVINGHAM/STW | 27/25/0119 | 27/25/0119 | A2 | Storm tank at WwTW | SE6698076010 | 466985 | 476014 | GB104027068340 | Marrs Beck from Source to Holbeck | River | 3387 | Rye | 3027 | Derwent Humber | UNNAMED TRIB OF MARRS BECK | Not Applicable | Not Applicable | Not Applicable | 276:45 | 35 | 15.6 | 2020 | 99.98 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00493
YWS00494 | Yorkshire Water | Live | GALE LANE CSO | GALE LANE/NO X CSO | 27/25/0121 | 27/25/0121 | 2 | SO on sewer network | SE6570084010 | 465700 | 484010 | GB104027068210 | Walmouth Beck from Source to River Riccal | River | 3387 | Rye | 3027 | Derwent Humber | SYKE CUT VIA A PUBLIC SEWER | Not Applicable | Not Applicable | Not Applicable | 79:45 | 18 | 9.5 | 2023 | 52.57 | Sensor failure / issue | Resolved - Aug | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00494
YWS00495 | Yorkshire Water | Live | GALE LANE CSO | GALE LANE/NO 2 CSO | 27/25/0121 | 27/25/0121 | 3 | SO on sewer network | SE6570084010 | 465700 | 484010 | GB104027068210 | Walmouth Beck from Source to River Riccal | River | 3387 | Rye | 3027 | Derwent Humber | SYKE CUT VIA A PUBLIC SEWER | Not Applicable | Not Applicable | Not Applicable | 0:15 | 1 | 15.4 | 2020 | 94.36 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00495
YWS00496 | Yorkshire Water | Live | SPORTSFIELD NO2 CSO | SPORTSFIELD/NO 2 CSO | 27/25/0123 | 27/25/0123 | A1 | SO on sewer network | SE7049886057 | 470498 | 486057 | GB104027068260 | Dove from Source to Hodge Beck | River | 3387 | Rye | 3027 | Derwent Humber | RIVER DOVE | Not Applicable | Not Applicable | Not Applicable | 106:15 | 44 | 47.6 | 2020 | 100 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation completed | No improvement action in reporting period | SOAF investigation completed - No work required | YWS00496
YWS00497 | Yorkshire Water | Live | LOCKTON SEWAGE TREATMENT WORKS | LOCKTON/STW | 27/25/0125 | 27/25/0125 | 2 | Inlet SO at WwTW | SE8416090020 | 484160 | 490020 | GB104027068520 | Levisham Beck from Source to Pickering Beck | River | 3387 | Rye | 3027 | Derwent Humber | TRIB OF LEVISHAM BECK | Not Applicable | Not Applicable | Not Applicable | 221:30 | 85 | 83.4 | 2020 | 99.54 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00497
YWS00498 | Yorkshire Water | Live | WASS SEWAGE TREATMENT WORKS | WASS/NO 2 STW | 27/25/0126 | 27/25/0126 | 2 | Inlet SO at WwTW | SE5597078690 | 455970 | 478690 | GB104027068420 | Holbeck from Source to Wath Beck | River | 3387 | Rye | 3027 | Derwent Humber | TRIB OF HOLBECK | Not Applicable | Not Applicable | Not Applicable | 284:45 | 50 | 57 | 2020 | 99.99 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS00498
YWS00499 | Yorkshire Water | Live | KIRKBY MOORSIDE NO.2 CSO | KIRKBY MOORSIDE/NO 2 CSO | 27/25/0130 | 27/25/0130 | A1 | SO on sewer network | SE7051385943 | 470513 | 485943 | GB104027068260 | Dove from Source to Hodge Beck | River | 3387 | Rye | 3027 | Derwent Humber | RIVER DOVE | Not Applicable | Not Applicable | Not Applicable | 364:15 | 92 | 100 | 2020 | 99.95 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation completed, Operational investigation completed | Operational improvement ongoing | SOAF investigation completed - No work required | YWS00499
YWS00500 | Yorkshire Water | Live | NORMANBY SEWAGE PUMPING STATION | NORMANBY/CSO | 27/25/0131 | 27/25/0131 | 1 | Storm discharge at pumping station | SE7354081500 | 473540 | 481500 | GB104027068440 | Seven from Catter Beck to River Rye | River | 3387 | Rye | 3027 | Derwent Humber | UNNAMED TRIB OF RIVER SEVEN | Not Applicable | Not Applicable | Not Applicable | 169:45 | 18 | 4 | 2020 | 98.64 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00500
YWS00501 | Yorkshire Water | Live | MARTON SEWAGE TREATMENT WORKS | MARTON/STW | 27/25/0132 | 27/25/0132 | 2 | Inlet SO at WwTW | SE7348082630 | 473480 | 482630 | GB104027068440 | Seven from Catter Beck to River Rye | River | 3387 | Rye | 3027 | Derwent Humber | RIVER SEVEN | Not Applicable | Not Applicable | Not Applicable | 64:15 | 11 | 18 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00501
YWS00502 | Yorkshire Water | Live | SAWMILL LANE CSO | SAWMILL LANE/CSO | 27/25/0147 | 27/25/0147 | A1 | SO on sewer network | SE6161983501 | 461619 | 483501 | GB104027068200 | Rye from River Seph to Holbeck | River | 3387 | Rye | 3027 | Derwent Humber | RIVER RYE | Not Applicable | Not Applicable | Not Applicable | 53:30 | 24 | 54.2 | 2020 | 99.95 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00502
YWS00503 | Yorkshire Water | Live | NEWBY BRIDGE STORM DETENTION TANK | NEWBY BRIDGE TANK/CSO | 27/26/0014 | 27/26/0014 | 1 | SO on sewer network | TA0141090360 | 501414 | 490367 | GB104027067980 | Burniston Beck/Sea Cut/Scalby Beck Catch to N Sea | River | 3489 | Upper Derwent Yorkshire | 3027 | Derwent Humber | SCALBY BECK - NORTH SEA | Not Applicable | Scarborough North Bay | Not Applicable | 231:50 | 23 | 26.2 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00503
YWS00504 | Yorkshire Water | Live | COW WATH BECK CSO | COW WATH BECK/CSO | 27/26/0015 | 27/26/0015 | 1 | SO on sewer network | TA0187090480 | 501842 | 490484 | GB104027067980 | Burniston Beck/Sea Cut/Scalby Beck Catch to N Sea | River | 3489 | Upper Derwent Yorkshire | 3027 | Derwent Humber | THE NORTH SEA | Not Applicable | Scarborough North Bay | Not Applicable | 389:28 | 36 | 31.2 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | Operational investigation completed | No improvement action in reporting period | No SOAF investigation required | YWS00504
YWS00505 | Yorkshire Water | Live | HILLCREST AVENUE | HILLCREST AV TANK/CSO | 27/26/0016 | 27/26/0016 | 1 | SO on sewer network | TA0225090550 | 502256 | 490535 | GB104027067980 | Burniston Beck/Sea Cut/Scalby Beck Catch to N Sea | River | 3489 | Upper Derwent Yorkshire | 3027 | Derwent Humber | SCALBY BECK - NORTH SEA | Not Applicable | Scarborough North Bay | Not Applicable | 639:40 | 73 | 34.6 | 2020 | 99.98 |  |  | Performance - Pump failure / issue | High spill threshold not met | UWWTR investigation ongoing, Operational investigation completed | Operational improvement completed | SOAF investigation ongoing | YWS00505
YWS00506 | Yorkshire Water | Live | Buurnt Howe Sewage Pumping Station* | BURNT HOWE RAVENSCAR/CSO | 27/26/0035 | 27/26/0035 | A1 | Storm discharge at pumping station | NZ9881601317 | 498737 | 501312 | GB40402G702300 | Esk & Yorkshire Coast Ravenscar | Groundwater Body | 1082 | Esk and Yorkshire Coast Ravenscar | 1006 | Humber GW | GROUNDWATER | Not Applicable | Not Applicable | Not Applicable | 52:45 | 25 | 22.6 | 2020 | 94.79 |  |  | High spill threshold not met | High spill threshold not met | UWWTR investigation ongoing, Operational investigation completed | Operational improvement ongoing | SOAF investigation ongoing | YWS00506
YWS00507 | Yorkshire Water | Live | RAVENSCAR SEWAGE TREATMENT WORKS | RAVENSCAR/STW | 27/26/0036 | 27/26/0036 | A2 | Inlet SO at WwTW | NZ9843101770 | 498430 | 501770 | GB40402G702300 | Esk & Yorkshire Coast Ravenscar | Groundwater Body | 1082 | Esk and Yorkshire Coast Ravenscar | 1006 | Humber GW | LAND | Not Applicable | Not Applicable | Not Applicable | 268:45 | 41 | 38.2 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00507
YWS00508 | Yorkshire Water | Live | PLAXTONS FACTORY NO 2 CSO | PLAXTONS FACTORY/NO 2 CSO | 27/26/0038 | 27/26/0038 | A1 | SO on sewer network | TA0429583445 | 504295 | 483445 | GB104027073281 | Eastfield Drain Lower to River Hertford | River | 3489 | Upper Derwent Yorkshire | 3027 | Derwent Humber | CULVERTED TRIB RIVER HERTFORD | Not Applicable | Not Applicable | Not Applicable | 144:00 | 28 | 28 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00508
YWS00509 | Yorkshire Water | Live | MALTON SEWAGE TREATMENT WORKS | MALTON/STW/3XDWF OVERFLOW | QR.27/27/0040 | 27/27/0040 | 2 | Storm tank at WwTW | SE7757070410 | 477550 | 470410 | GB104027068313 | Derwent from River Rye to Kirkham | River | 3311 | Middle Derwent Yorkshire | 3027 | Derwent Humber | THE RIVER DERWENT | Not Applicable | Not Applicable | Not Applicable | 220:45 | 25 | 32.4 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00509
YWS00510 | Yorkshire Water | Live | FILEY WASTE WATER TREATMENT WORKS | FILEY TRANSFER/CSO | 27/27/0051 | 27/27/0051 | 2 | Storm discharge at pumping station | TA1377081370 | 513770 | 481370 | GB650401500004 | Yorkshire North | Coastal Water | 3179 | Esk TraC | 3040 | Humber TraC | NORTH SEA | Not Applicable | Filey | Not Applicable | 158:46 | 61 | 54.4 | 2020 | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00510
YWS00511 | Yorkshire Water | Live | FILEY WASTE WATER TREATMENT WORKS | FILEY TRANSFER/CSO | 27/27/0051 | 27/27/0051 | 3 | SO on sewer network | TA1205080810 | 512249 | 480770 | GB650401500004 | Yorkshire North | Coastal Water | 3179 | Esk TraC | 3040 | Humber TraC | NORTH SEA | Not Applicable | Filey | Not Applicable | 60:54 | 16 | 8.5 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00511
YWS00512 | Yorkshire Water | Live | FILEY WASTE WATER TREATMENT WORKS | FILEY TRANSFER/CSO | 27/27/0051 | 27/27/0051 | 4 | SO on sewer network | TA1205080820 | 512050 | 480810 | GB650401500004 | Yorkshire North | Coastal Water | 3179 | Esk TraC | 3040 | Humber TraC | NORTH SEA | Not Applicable | Filey | Not Applicable | 52:32 | 12 | 8.4 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00512
YWS00513 | Yorkshire Water | Live | SCALBY NESS OUTFALL | SCALBY MILLS/CSO | 27/27/0055 | 27/27/0055 | 1 | SO on sewer network | TA0470091640 | 503670 | 491270 | GB650401500004 | Yorkshire North | Coastal Water | 3179 | Esk TraC | 3040 | Humber TraC | NORTH SEA | Not Applicable | Scarborough North Bay | Not Applicable | 94:45 | 54 | 53.33 | 2020 | 99.94 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00513
YWS00514 | Yorkshire Water | Live | EBBERSTON SPS | MALTON EBBERSTON/CSO | 27/27/0056 | 27/27/0056 | 2 | Storm discharge at pumping station | SE8967081860 | 489670 | 481860 | GB104027067890 | Ebberston Beck catchment (trib of Derwent) | River | 3489 | Upper Derwent Yorkshire | 3027 | Derwent Humber | EBBERSTON BECK | Not Applicable | Not Applicable | Not Applicable | 173:30 | 73 | 40.4 | 2020 | 100 |  |  | Performance - Infiltration | Performance - Infiltration | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS00514
YWS00515 | Yorkshire Water | Live | SNAINTON NO.2 FOULBRIDGE LANE SPS | FOULBRIDGE LANE/CSO | 27/27/0058 | 27/27/0058 | 2 | Storm discharge at pumping station | SE9183081870 | 491830 | 481870 | GB104027067930 | Derwent from Black Beck to River Rye | River | 3489 | Upper Derwent Yorkshire | 3027 | Derwent Humber | WELLDALE BECK | Not Applicable | Not Applicable | Not Applicable | 100:00 | 15 | 14.4 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00515
YWS00516 | Yorkshire Water | Live | THORNTON LE DALE STW | THORNTON LE DALE/STW | 27/27/0063 | 27/27/0063 | A2 | Storm tank at WwTW | SE8331681851 | 483316 | 481851 | GB104027067950 | Thornton/Dalby/Staindale from Source to the Syme | River | 3489 | Upper Derwent Yorkshire | 3027 | Derwent Humber | THORNTON BECK | Not Applicable | Not Applicable | Not Applicable | 3419:00 | 159 | 80.2 | 2020 | 99.89 |  |  | Performance - GW inundation | Performance - GW inundation | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS00516
YWS00517 | Yorkshire Water | Live | RILLINGTON STW | RILLINGTON/STW | 27/27/0065 | 27/27/0065 | A2 | Storm tank at WwTW | SE8480074700 | 484720 | 474730 | GB104027068313 | Derwent from River Rye to Kirkham | River | 3311 | Middle Derwent Yorkshire | 3027 | Derwent Humber | RILLINGTON BECK | Not Applicable | Not Applicable | Not Applicable | 91:30 | 17 | 8.6 | 2020 | 99.98 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00517
YWS00518 | Yorkshire Water | Live | RILLINGTON STW | RILLINGTON/STW | 27/27/0065 | 27/27/0065 | A3 | Inlet SO at WwTW | SE8480074700 | 484720 | 474730 | GB104027068313 | Derwent from River Rye to Kirkham | River | 3311 | Middle Derwent Yorkshire | 3027 | Derwent Humber | RILLINGTON BECK | Not Applicable | Not Applicable | Not Applicable | 19:30 | 23 | 17 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00518
YWS00519 | Yorkshire Water | Live | STONEGATE CSO | HUNMANBY STONEGATE/CSO | 27/27/0067 | 27/27/0067 | A1 | SO on sewer network | TA1046977811 | 510469 | 477811 | GB104027067811 | Hertford from Source to River Derwent | River | 3489 | Upper Derwent Yorkshire | 3027 | Derwent Humber | TRIB MAIN DRAIN RIVER HERTFORD | Not Applicable | Not Applicable | Not Applicable | 234:15 | 68 | 62.2 | 2020 | 100 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00519
YWS00520 | Yorkshire Water | Live | MALTON NORTON SPS | WELHAM ROAD NORTH/HLR | 27/27/0076 | 27/27/0076 | A2 | Storm discharge at pumping station | SE7907771303 | 479077 | 471303 | GB104027068313 | Derwent from River Rye to Kirkham | River | 3311 | Middle Derwent Yorkshire | 3027 | Derwent Humber | CULVERTED MILL BECK | Not Applicable | Not Applicable | Not Applicable | 406:30 | 56 | 97 | 2020 | 80.02 | Installation set-up/design issue | Resolved - May | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement ongoing | SOAF investigation ongoing | YWS00520
YWS00521 | Yorkshire Water | Live | CHANDLERS WHARF SPS | CHANDLERS WHARF/CSO | 27/27/0078 | 27/27/0078 | A2 | SO on sewer network | SE7902071460 | 479020 | 471460 | GB104027068313 | Derwent from River Rye to Kirkham | River | 3311 | Middle Derwent Yorkshire | 3027 | Derwent Humber | RIVER DERWENT | Not Applicable | Not Applicable | Not Applicable | 555:18 | 46 | 30 | 2020 | 99.98 |  |  | High spill threshold not met | High spill threshold not met | Operational investigation completed | No improvement action in reporting period | No SOAF investigation required | YWS00521
YWS00522 | Yorkshire Water | Live | LASCELLES LANE SPS | LASCELLES LANE/CSO | 27/27/0091 | 27/27/0091 | A2 | Storm discharge at pumping station | SE7992272748 | 479922 | 472748 | GB104027068313 | Derwent from River Rye to Kirkham | River | 3311 | Middle Derwent Yorkshire | 3027 | Derwent Humber | RIVER DERWENT | Not Applicable | Not Applicable | Not Applicable | 54:45 | 29 | 26.8 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00522
YWS00523 | Yorkshire Water | Live | FIRBY SEWAGE TREATMENT WORKS | FIRBY/STW | 27/27/0092 | 27/27/0092 | A2 | Inlet SO at WwTW | SE7512066490 | 475120 | 466490 | GB104027068313 | Derwent from River Rye to Kirkham | River | 3311 | Middle Derwent Yorkshire | 3027 | Derwent Humber | UNNAMED TRIB OF DERWENT | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 1.4 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00523
YWS00524 | Yorkshire Water | Live | ALLERSTON SEWAGE PUMPING STATION | ALLERSTON/CSO | 27/27/0093 | 27/27/0093 | A2 | Storm discharge at pumping station | SE8790181980 | 487901 | 481980 | GB104027067930 | Derwent from Black Beck to River Rye | River | 3489 | Upper Derwent Yorkshire | 3027 | Derwent Humber | ALLERSTON BECK | Not Applicable | Not Applicable | Not Applicable | 66:45 | 15 | 4.2 | 2020 | 99.35 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00524
YWS00525 | Yorkshire Water | Live | LEBBERSTON SEWAGE PUMPING STATION | LEBBERSTON/CSO | 27/27/0095 | 27/27/0095 | A1 | Storm discharge at pumping station | TA0762082340 | 507630 | 482346 | GB104027067811 | Hertford from Source to River Derwent | River | 3489 | Upper Derwent Yorkshire | 3027 | Derwent Humber | UNNAMED TRIB OF HERTFORD | Not Applicable | Not Applicable | Not Applicable | 1531:00 | 106 | 95.4 | 2020 | 99.93 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00525
YWS00526 | Yorkshire Water | Live | FLAT CLIFFS SEWAGE PUMPING STATION | FLATCLIFFS/CSO | 27/27/0097 | 27/27/0097 | 1 | Storm discharge at pumping station | TA1245078210 | 512450 | 478210 | GB650401500004 | Yorkshire North | Coastal Water | 3179 | Esk TraC | 3040 | Humber TraC | THE NORTH SEA | Not Applicable | Reighton | Not Applicable | 109:02 | 18 | 13.8 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00526
YWS00528 | Yorkshire Water | Live | CASTLEGATE SEWAGE PUMPING STATION | CASTLEGATE/CSO | 27/27/0101 | 27/27/0101 | A2 | Storm discharge at pumping station | SE7923071470 | 479230 | 471470 | GB104027068313 | Derwent from River Rye to Kirkham | River | 3311 | Middle Derwent Yorkshire | 3027 | Derwent Humber | RIVER DERWENT | Not Applicable | Not Applicable | Not Applicable | 1873:24 | 92 | 35.5 | 2020 | 99.78 |  |  | Performance - Infiltration | High spill threshold not met | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS00528
YWS00529 | Yorkshire Water | Live | MUSTON SPS | MUSTON/CSO | 27/27/0102 | 27/27/0102 | A1 | Storm discharge at pumping station | TA0956079840 | 509560 | 479840 | GB104027067811 | Hertford from Source to River Derwent | River | 3489 | Upper Derwent Yorkshire | 3027 | Derwent Humber | UNNAMED TRIB OF HERTFORD | Not Applicable | Not Applicable | Not Applicable | 190:45 | 27 | 25 | 2020 | 96.7 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00529
YWS00530 | Yorkshire Water | Live | SHERBURN WPC WORKS | SHERBURN/STW | 27/27/0105 | 27/27/0105 | A2 | Storm tank at WwTW | SE9550077600 | 495600 | 477690 | GB104027067800 | Sherburn Beck catchment (trib of Derwent) | River | 3489 | Upper Derwent Yorkshire | 3027 | Derwent Humber | SHERBURN BECK | Not Applicable | Not Applicable | Not Applicable | 16:30 | 6 | 11.8 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00530
YWS00531 | Yorkshire Water | Live | BALACLAVA NO. 2 SPS | BALACLAVA/NO 2 CSO | 27/27/0107 | 27/27/0107 | 1 | Storm discharge at pumping station | SE7987371844 | 479860 | 471870 | GB104027068313 | Derwent from River Rye to Kirkham | River | 3311 | Middle Derwent Yorkshire | 3027 | Derwent Humber | PRIORPOT BECK | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00531
YWS00532 | Yorkshire Water | Live | MALTON HOLMESFIELD SPS | MALTON HOLMESFLD/CSO | 27/27/0109 | 27/27/0109 | A2 | Storm discharge at pumping station | SE7935071574 | 479350 | 471574 | GB104027068313 | Derwent from River Rye to Kirkham | River | 3311 | Middle Derwent Yorkshire | 3027 | Derwent Humber | RIVER DERWENT | Not Applicable | Not Applicable | Not Applicable | 16:28 | 88 | 77.2 | 2020 | 100 |  |  | Performance - Infiltration | Performance - Infiltration | UWWTR investigation ongoing, Operational investigation completed | Operational improvement completed | SOAF investigation ongoing | YWS00532
YWS00533 | Yorkshire Water | Live | PRIORPOT BRIDGE CSO | PRIORPOT BRIDGE/CSO | 27/27/0130 | 27/27/0130 | A1 | SO on sewer network | SE8001271844 | 480012 | 471844 | GB104027068313 | Derwent from River Rye to Kirkham | River | 3311 | Middle Derwent Yorkshire | 3027 | Derwent Humber | PRIORPOT BECK | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0.4 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00533
YWS00534 | Yorkshire Water | Live | THE BROWS CSO | THE BROWS/CSO | 27/27/0131 | 27/27/0131 | A1 | SO on sewer network | SE7808071151 | 478080 | 471151 | GB104027068313 | Derwent from River Rye to Kirkham | River | 3311 | Middle Derwent Yorkshire | 3027 | Derwent Humber | RIVER DERWENT | Not Applicable | Not Applicable | Not Applicable | 0:30 | 1 | 1.2 | 2020 | 99.91 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00534
YWS00535 | Yorkshire Water | Live | WELHAM ROAD SOUTH CSO | WELHAM ROAD SOUTH/CSO | 27/27/0132 | 27/27/0132 | A1 | SO on sewer network | SE7905771103 | 479057 | 471103 | GB104027068313 | Derwent from River Rye to Kirkham | River | 3311 | Middle Derwent Yorkshire | 3027 | Derwent Humber | MILL BECK | Not Applicable | Not Applicable | Not Applicable | 4:00 | 8 | 4.2 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00535
YWS00536 | Yorkshire Water | Live | WHEELGATE CSO | WHEELGATE/CSO | 27/27/0133 | 27/27/0133 | A1 | SO on sewer network | SE7873471477 | 478734 | 471477 | GB104027068313 | Derwent from River Rye to Kirkham | River | 3311 | Middle Derwent Yorkshire | 3027 | Derwent Humber | RIVER DERWENT | Not Applicable | Not Applicable | Not Applicable | 53:56 | 48 | 64 | 2020 | 100 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | No investigation activity in reporting period | No improvement action in reporting period | SOAF investigation completed - No work required | YWS00536
YWS00537 | Yorkshire Water | Live | CURLEW DRIVE CSO | CURLEW DRIVE/CSO | 27/27/0134 | 27/27/0134 | A1 | SO on sewer network | TA0300583590 | 503005 | 483590 | GB104027073281 | Eastfield Drain Lower to River Hertford | River | 3489 | Upper Derwent Yorkshire | 3027 | Derwent Humber | TRIBUTARY OF BLACK DIKE | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0 | 2020 | 70.1 | Comms failure / issue | Scheduled | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00537
YWS00538 | Yorkshire Water | Live | CARRHOUSE LANE CAYTON NO 2 CSO | CARRHOUSE LN CAYTON/2 CSO | 27/27/0137 | 27/27/0137 | A1 | SO on sewer network | TA0470583184 | 504705 | 483184 | GB104027073281 | Eastfield Drain Lower to River Hertford | River | 3489 | Upper Derwent Yorkshire | 3027 | Derwent Humber | RIVER HERTFORD | Not Applicable | Not Applicable | Not Applicable | 205:00 | 32 | 27.2 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | SOAF investigation completed - Work required | YWS00538
YWS00539 | Yorkshire Water | Live | ACKLAM SEWAGE TREATMENT WORKS | ACKLAM/STW | 27/27/0140 | 27/27/0140 | 2 | Inlet SO at WwTW | SE7803061390 | 478030 | 461390 | GB104027068312 | Derwent from Kirkham to Elvington Beck | River | 3311 | Middle Derwent Yorkshire | 3027 | Derwent Humber | ACKLAM BECK | Not Applicable | Not Applicable | Not Applicable | 268:45 | 35 | 25.6 | 2020 | 99.98 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00539
YWS00540 | Yorkshire Water | Live | ACKLAM SPS | ACKLAM/CSO | 27/27/0141 | 27/27/0141 | A1 | Storm discharge at pumping station | SE7854061580 | 478540 | 461580 | GB104027068312 | Derwent from Kirkham to Elvington Beck | River | 3311 | Middle Derwent Yorkshire | 3027 | Derwent Humber | ACKLAM BECK | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00540
YWS00541 | Yorkshire Water | Live | STONE BRIDGE NO 2 CSO | STONE BRIDGE/NO 2 CSO | 27/27/0143 | 27/27/0143 | A1 | SO on sewer network | SE8362083082 | 483620 | 483082 | GB104027067950 | Thornton/Dalby/Staindale from Source to the Syme | River | 3489 | Upper Derwent Yorkshire | 3027 | Derwent Humber | THORNTON BECK | Not Applicable | Not Applicable | Not Applicable | 97:30 | 27 | 11 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | Operational investigation completed | Operational improvement completed | No SOAF investigation required | YWS00541
YWS00542 | Yorkshire Water | Live | SHEEPFOOT HILL CSO | SHEEPFOOT HILL/CSO | 27/27/0156 | 27/27/0156 | A1 | SO on sewer network | SE7902571459 | 479025 | 471459 | GB104027068313 | Derwent from River Rye to Kirkham | River | 3311 | Middle Derwent Yorkshire | 3027 | Derwent Humber | RIVER DERWENT | Not Applicable | Not Applicable | Not Applicable | 389:08 | 28 | 19 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00542
YWS00543 | Yorkshire Water | Live | YORKERSGATE COMBINED SEWER OVERFLOW | YORKERSGATE/CSO | 27/27/0164 | 27/27/0164 | A1 | SO on sewer network | SE7855571504 | 478555 | 471504 | GB104027068313 | Derwent from River Rye to Kirkham | River | 3311 | Middle Derwent Yorkshire | 3027 | Derwent Humber | RIVER DERWENT | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 33.6 | 2020 | 99.95 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | SOAF investigation completed - No work required | YWS00543
YWS00544 | Yorkshire Water | Live | OUTGAITS LANE CSO | OUTGAITS LANE/CSO | 27/27/0165 | 27/27/0165 | 1 | SO on sewer network | TA0981078040 | 509821 | 478048 | GB104027067811 | Hertford from Source to River Derwent | River | 3489 | Upper Derwent Yorkshire | 3027 | Derwent Humber | UNNAMED TRIB OF RIVER HERTFORD | Not Applicable | Not Applicable | Not Applicable | 1:00 | 2 | 2.8 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00544
YWS00545 | Yorkshire Water | Live | NORTON CHURCH STREET CSO | NORTON CHURCH ST/2 CSO | 27/27/0166 | 27/27/0166 | A1 | SO on sewer network | SE7919671444 | 479196 | 471444 | GB104027068313 | Derwent from River Rye to Kirkham | River | 3311 | Middle Derwent Yorkshire | 3027 | Derwent Humber | RIVER DERWENT | Not Applicable | Not Applicable | Not Applicable | 218:26 | 50 | 58 | 2020 | 100 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00545
YWS00546 | Yorkshire Water | Live | NEWTON ON DERWENT SPS | NEWTON DERWENT/SPS | 27/28/0076 | 27/28/0076 | 2 | Storm discharge at pumping station | SE7184049760 | 471840 | 449760 | GB104027068312 | Derwent from Kirkham to Elvington Beck | River | 3311 | Middle Derwent Yorkshire | 3027 | Derwent Humber | BIRKER GOIT (UN-NAMED TRIB) | Not Applicable | Not Applicable | Not Applicable | 148:30 | 22 | 19.4 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00546
YWS00547 | Yorkshire Water | Live | SPITTAL SEWAGE PUMPING STATION | SPITTAL BRIDGE/CSO | 27/28/0095 | 27/28/0095 | A2 | SO on sewer network | SE7679052520 | 476795 | 452521 | GB104027063460 | Blackfoss Bk lower Catch (trib of Pocklington Bk) | River | 3271 | Lower Derwent Yorkshire | 3027 | Derwent Humber | SPITTAL BECK | Not Applicable | Not Applicable | Not Applicable | 327:30 | 35 | 32 | 2020 | 99.96 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00547
YWS00548 | Yorkshire Water | Live | STAMFORD BRIDGE NORTH SPS | STAMFORD BRIDGE NTH/SPS | 27/28/0096 | 27/28/0096 | A2 | Storm discharge at pumping station | SE7109055550 | 476795 | 452521 | GB104027063460 | Blackfoss Bk lower Catch (trib of Pocklington Bk) | River | 3271 | Lower Derwent Yorkshire | 3027 | Derwent Humber | RIVER DERWENT | Not Applicable | Not Applicable | Not Applicable | 2188:45 | 118 | 88.2 | 2020 | 99.98 |  |  | Data collection - Tidal / river inundation | Data collection - Tidal / river inundation | UWWTR investigation ongoing, Operational investigation ongoing | Operational improvement ongoing | SOAF investigation ongoing | YWS00548
YWS00549 | Yorkshire Water | Live | STAMFORD BRIDGE SPS | STAMFORD BRIDGE STH/SPS | 27/28/0097 | 27/28/0097 | A2 | Storm discharge at pumping station | SE7109055530 | 471090 | 455530 | GB104027068312 | Derwent from Kirkham to Elvington Beck | River | 3311 | Middle Derwent Yorkshire | 3027 | Derwent Humber | RIVER DERWENT | Not Applicable | Not Applicable | Not Applicable | 72:45 | 21 | 14 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00549
YWS00550 | Yorkshire Water | Live | WHENBY SEWAGE TREATMENT WORKS | WHENBY/NO 2 STW | 27/28/0100 | 27/28/0100 | 2 | Inlet SO at WwTW | SE6319069540 | 463190 | 469540 | GB104027063580 | Spittle/Bulmer/Ings Becks catch (trib of Derwent) | River | 3311 | Middle Derwent Yorkshire | 3027 | Derwent Humber | TRIB OF INGS BECK | Not Applicable | Not Applicable | Not Applicable | 0:30 | 2 | 2.8 | 2020 | 99.09 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00550
YWS00551 | Yorkshire Water | Live | BISHOP WILTON STW | BISHOP WILTON/STW | 27/28/0104 | 27/28/0104 | A2 | Storm tank at WwTW | SE7920054300 | 479310 | 454400 | GB104027063470 | Bishop Wilton Beck Catch (trib of Blackfoss Beck) | River | 3271 | Lower Derwent Yorkshire | 3027 | Derwent Humber | BISHOP WILTON BECK | Not Applicable | Not Applicable | Not Applicable | 623:45 | 83 | 87.8 | 2020 | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation ongoing | Operational improvement ongoing | SOAF investigation ongoing | YWS00551
YWS00552 | Yorkshire Water | Live | CHURCH END SPS | SHERIFF HUTTON/CSO | 27/28/0112 | 27/28/0112 | A1 | Storm discharge at pumping station | SE6589066410 | 465890 | 466410 | GB104027063580 | Spittle/Bulmer/Ings Becks catch (trib of Derwent) | River | 3311 | Middle Derwent Yorkshire | 3027 | Derwent Humber | TRIB OF BULMER BECK | Not Applicable | Not Applicable | Not Applicable | 3:30 | 6 | 6.8 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00552
YWS00554 | Yorkshire Water | Live | POCKLINGTON AIRFIELD SPS | POCKLINGTON AIRFIELD/CSO | 27/28/0114 | 27/28/0114 | 1 | Storm discharge at pumping station | SE7855048170 | 478550 | 448170 | GB104027063480 | Pocklington Beck from Source to Bielby beck | River | 3271 | Lower Derwent Yorkshire | 3027 | Derwent Humber | TRIB OF STONE BECK | Not Applicable | Not Applicable | Not Applicable | 0:45 | 1 | 7 | 2020 | 78.8 | Comms failure / issue | Resolved - Mar | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00554
YWS00555 | Yorkshire Water | Live | THE WERES SEWAGE PUMPING STATION | THE WERES/NO 2 CSO | 27/28/0118 | 27/28/0118 | 1 | Storm discharge at pumping station | SE7085039900 | 470850 | 439900 | GB104027068311 | Derwent from Elvington Beck to River Ouse | River | 3271 | Lower Derwent Yorkshire | 3027 | Derwent Humber | THE WERES POND | Not Applicable | Not Applicable | Not Applicable | 328:45 | 60 | 30 | 2020 | 98.64 |  |  | High spill threshold not met | High spill threshold not met | Operational investigation completed | No improvement action in reporting period | No SOAF investigation required | YWS00555
YWS00556 | Yorkshire Water | Live | ELVINGTON BECK SPS | ELVINGTON BECK/CSO | 27/28/0121 | 27/28/0121 | A2 | Storm discharge at pumping station | SE7022647438 | 470226 | 447438 | GB104027068312 | Derwent from Kirkham to Elvington Beck | River | 3311 | Middle Derwent Yorkshire | 3027 | Derwent Humber | ELVINGTON BECK | Not Applicable | Not Applicable | Not Applicable | 1283:00 | 97 | 91.4 | 2020 | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement ongoing | SOAF investigation ongoing | YWS00556
YWS00557 | Yorkshire Water | Live | BUGTHORPE SEWAGE TREATMENT WORKS | BUGTHORPE/STW | 27/28/0123 | 27/28/0123 | 2 | Inlet SO at WwTW | SE7679057810 | 476790 | 457810 | GB104027063510 | Barlam/Skirpen Beck catch (trib of Derwent) | River | 3311 | Middle Derwent Yorkshire | 3027 | Derwent Humber | BUGTHORPE BECK | Not Applicable | Not Applicable | Not Applicable | 423:00 | 41 | 36.2 | 2020 | 99.97 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00557
YWS00558 | Yorkshire Water | Live | BECK ROW SEWAGE PUMPING STATION | BUGTHORPE BECK ROW/CSO | 27/28/0124 | 27/28/0124 | 1 | Storm discharge at pumping station | SE7721058210 | 477210 | 458210 | GB104027063510 | Barlam/Skirpen Beck catch (trib of Derwent) | River | 3311 | Middle Derwent Yorkshire | 3027 | Derwent Humber | BUGTHORPE BECK | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 1.8 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00558
YWS00559 | Yorkshire Water | Live | BARF LANE SEWAGE PUMPING STATION | BUGTHORPE BARF LANE/CSO | 27/28/0125 | 27/28/0125 | 1 | Storm discharge at pumping station | SE7746057570 | 477460 | 457570 | GB104027063510 | Barlam/Skirpen Beck catch (trib of Derwent) | River | 3311 | Middle Derwent Yorkshire | 3027 | Derwent Humber | TRIB OF KELDSIKE BECK | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 6.2 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00559
YWS00560 | Yorkshire Water | Live | BARMBY MOOR SPS CSO | BARMBY MOOR/CSO | 27/28/0127 | 27/28/0127 | 1 | SO on sewer network | SE7733048900 | 477339 | 448900 | GB104027063440 | Pocklington Beck from Bielby Bk to River Derwent | River | 3271 | Derwent Lower Yorkshire | 3027 | Derwent Humber | UNNAMED TRIB OF BLACK DIKE | Not Applicable | Not Applicable | Not Applicable | 1212:30 | 112 | 42.8 | 2020 | 99.82 |  |  | Performance - Infiltration | Performance - Infiltration | UWWTR investigation ongoing, Operational investigation completed | Operational improvement completed | SOAF investigation ongoing | YWS00560
YWS00561 | Yorkshire Water | Live | SUTTON ON DERWENT SPS | DERWENT/CSO | 27/28/0131 | 27/28/0131 | 1 | Storm discharge at pumping station | SE7070046890 | 470700 | 446890 | GB104027068311 | Derwent from Elvington Beck to River Ouse | River | 3271 | Lower Derwent Yorkshire | 3027 | Derwent Humber | UNNAMED TRIB OF DERWENT | Not Applicable | Not Applicable | Not Applicable | 31:00 | 4 | 6.8 | 2020 | 99.93 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00561
YWS00562 | Yorkshire Water | Live | RECTORY FARM SEWAGE PUMPING STATION | SCRAYINGHAM RECTRY FM/CSO | 27/28/0144 | 27/28/0144 | 1 | Storm discharge at pumping station | SE7311160330 | 473110 | 460330 | GB104027068312 | Derwent from Kirkham to Elvington Beck | River | 3311 | Middle Derwent Yorkshire | 3027 | Derwent Humber | UNNAMED TRIB OF DERWENT | Not Applicable | Not Applicable | Not Applicable | 7:15 | 1 | 3.75 | 2020 | 7.98 | Comms failure / issue | Resolved - February after reporting year | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00562
YWS00563 | Yorkshire Water | Live | SOUTH FARM SEWAGE PUMPING STATION | SCRAYINGHAM SOUTH FM/CSO | 27/28/0145 | 27/28/0145 | 1 | Storm discharge at pumping station | SE7297159850 | 472970 | 459850 | GB104027068312 | Derwent from Kirkham to Elvington Beck | River | 3311 | Middle Derwent Yorkshire | 3027 | Derwent Humber | THE GOIT VIA A CULVERTEDSYSTEM | Not Applicable | Not Applicable | Not Applicable | 370:15 | 56 | 57 | 2020 | 54.65 | Sensor failure / issue | Resolved - Aug | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement ongoing | SOAF investigation ongoing | YWS00563
YWS00564 | Yorkshire Water | Live | ST PETERS CLOSE CSO | ST PETERS SQUARE/NO 2 CSO | 27/28/0149 | 27/28/0149 | 1 | SO on sewer network | SE8033049020 | 480336 | 449027 | GB104027063480 | Pocklington Beck from Source to Bielby beck | River | 3271 | Lower Derwent Yorkshire | 3027 | Derwent Humber | POCKLINGTON BECK | Not Applicable | Not Applicable | Not Applicable | 13:00 | 14 | 17.8 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00564
YWS00565 | Yorkshire Water | Live | GEORGE STREET POCKLINGTON CSO | GEORGE ST POCKLINGTON/CSO | 27/28/0150 | 27/28/0150 | A1 | SO on sewer network | SE8017048967 | 480170 | 448967 | GB104027063480 | Pocklington Beck from Source to Bielby beck | River | 3271 | Lower Derwent Yorkshire | 3027 | Derwent Humber | POCKLINGTON BECK | Not Applicable | Not Applicable | Not Applicable | 6:15 | 9 | 16 | 2020 | 99.34 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00565
YWS00566 | Yorkshire Water | Live | NUNBURNHOLME STW | NUNBURNHOLME/NO 3 STW | 27/28/0165 | 27/28/0165 | 2 | Inlet SO at WwTW | SE8493047840 | 484930 | 447840 | GB104027063450 | Bielby Beck from Source to Pocklington Beck | River | 3271 | Lower Derwent Yorkshire | 3027 | Derwent Humber | NUNBURNHOLME BECK | Not Applicable | Not Applicable | Not Applicable | 523:30 | 39 | 25.4 | 2020 | 99.97 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00566
YWS00567 | Yorkshire Water | Live | CRAMBE STW | CRAMBE/STW | 27/28/0171 | 27/28/0171 | A2 | Inlet SO at WwTW | SE7353064750 | 473530 | 464750 | GB104027068312 | Derwent from Kirkham to Elvington Beck | River | 3311 | Middle Derwent Yorkshire | 3027 | Derwent Humber | UNNAMED TRIB OF RIVER DERWENT | Not Applicable | Not Applicable | Not Applicable | 102:45 | 17 | 14.6 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00567
YWS00568 | Yorkshire Water | Live | HOWSHAM SEWAGE TREATMENT WORKS | HOWSHAM/STW | 27/28/0172 | 27/28/0172 | A2 | Inlet SO at WwTW | SE7356063000 | 473560 | 463000 | GB104027068312 | Derwent from Kirkham to Elvington Beck | River | 3311 | Middle Derwent Yorkshire | 3027 | Derwent Humber | UNNAMED TRIB OF RIVER DERWENT | Not Applicable | Not Applicable | Not Applicable | 136:15 | 25 | 13.4 | 2020 | 99.71 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00568
YWS00569 | Yorkshire Water | Live | KEXBY SEWAGE TREATMENT WORKS | KEXBY/STW | 27/28/0180 | 27/28/0180 | 2 | Inlet SO at WwTW | SE7029050820 | 470290 | 450820 | GB104027068312 | Derwent from Kirkham to Elvington Beck | River | 3311 | Middle Derwent Yorkshire | 3027 | Derwent Humber | UNNAMED TRIB OF RIVER DERWENT | Not Applicable | Not Applicable | Not Applicable | 2048:30 | 131 | 97 | 2020 | 99.86 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement ongoing | SOAF investigation ongoing | YWS00569
YWS00570 | Yorkshire Water | Live | HAYTON SEWAGE TREATMENT WORKS | HAYTON/STW | 27/28/0183 | 27/28/0183 | A2 | Inlet SO at WwTW | SE8179045670 | 481790 | 445670 | GB104027063450 | Bielby Beck from Source to Pocklington Beck | River | 3271 | Lower Derwent Yorkshire | 3027 | Derwent Humber | HAYTON BECK | Not Applicable | Not Applicable | Not Applicable | 439:00 | 34 | 32.6 | 2020 | 99.95 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00570
YWS00571 | Yorkshire Water | Live | FOSTON STW | FOSTON/STW | 27/28/0194 | 27/28/0194 | A2 | Inlet SO at WwTW | SE7058065330 | 470560 | 465300 | GB104027063580 | Spittle/Bulmer/Ings Becks catch (trib of Derwent) | River | 3311 | Middle Derwent Yorkshire | 3027 | Derwent Humber | SPITAL BECK | Not Applicable | Not Applicable | Not Applicable | 45:30 | 12 | 32.6 | 2020 | 99.96 |  |  | High spill threshold not met | High spill threshold not met | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00571
YWS00572 | Yorkshire Water | Live | POCKLINGTON SEWAGE TREATMENT WORKS | POCKLINGTON/STW | 27/28/0195 | 27/28/0195 | 2 | Storm tank at WwTW | SE8004047310 | 480040 | 447310 | GB104027063480 | Pocklington Beck from Source to Bielby beck | River | 3271 | Lower Derwent Yorkshire | 3027 | Derwent Humber | POCKLINGTON BECK | Not Applicable | Not Applicable | Not Applicable | 900:00 | 77 | 41 | 2020 | 99.67 |  |  | Performance - Infiltration | Performance - Infiltration | UWWTR investigation ongoing, Operational investigation completed | Operational improvement completed | SOAF investigation ongoing | YWS00572
YWS00573 | Yorkshire Water | Live | HAWKSWELL LANE CSO | HAWKSWELL LANE/CSO | 27/28/0198 | 27/28/0198 | A1 | SO on sewer network | SE7890271477 | 478902 | 471477 | GB104027068313 | Derwent from River Rye to Kirkham | River | 3311 | Middle Derwent Yorkshire | 3027 | Derwent Humber | RIVER DERWENT | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0.2 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00573
YWS00574 | Yorkshire Water | Live | SPRING LANE SPS | SPRING LANE/CSO | 27/28/0206 | 27/28/0206 | 1 | Storm discharge at pumping station | SE8313051590 | 483130 | 451590 | GB104027063480 | Pocklington Beck from Source to Bielby beck | River | 3271 | Lower Derwent Yorkshire | 3027 | Derwent Humber | TRIB OF MILLINGTON BECK | Not Applicable | Not Applicable | Not Applicable | 2:00 | 4 | 4.6 | 2020 | 99.94 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00574
YWS00575 | Yorkshire Water | Live | TOWN STREET MALTON CSO | TOWN STREET MALTON/CSO | 27/28/0207 | 27/28/0207 | A1 | SO on sewer network | SE7994772614 | 479947 | 472614 | GB104027068313 | Derwent from River Rye to Kirkham | River | 3311 | Middle Derwent Yorkshire | 3027 | Derwent Humber | RIVER DERWENT | Not Applicable | Not Applicable | Not Applicable | 3:45 | 5 | 5 | 2020 | 88.69 | Sensor failure / issue | Resolved - Mar | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00575
YWS00576 | Yorkshire Water | Live | ENDEAVOUR WHARF PUMPING STATION | ENDEAVOUR WHARF/CSO | 27/29/0040 | 27/29/0040 | 1 | Storm discharge at pumping station | NZ9053011620 | 490530 | 511620 | GB650401500004 | Yorkshire North | Coastal Water | 3179 | Esk TraC | 3040 | Humber TraC | THE NORTH SEA AND RIVER ESK | Not Applicable | Whitby | Not Applicable | 225:30 | 58 | 31.2 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS00576
YWS00577 | Yorkshire Water | Live | ENDEAVOUR WHARF PUMPING STATION | ENDEAVOUR WHARF/CSO | 27/29/0040 | 27/29/0040 | 2 | Storm discharge at pumping station | NZ8993010930 | 489930 | 510930 | GB510402703400 | ESK (E) | Transitional Water | 3179 | Esk TraC | 3040 | Humber TraC | THE NORTH SEA AND RIVER ESK | Not Applicable | Not Applicable | Not Applicable | 141:00 | 40 | 32.6 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | Operational investigation completed | No improvement action in reporting period | No SOAF investigation required | YWS00577
YWS00578 | Yorkshire Water | Live | PIER ROAD CSO | WHITBY PIER ROAD/CSO | 27/29/0041 | 27/29/0041 | 1 | Storm discharge at pumping station | NZ8984011200 | 489840 | 511200 | GB510402703400 | ESK (E) | Transitional Water | 3179 | Esk TraC | 3040 | Humber TraC | RIVER ESK (TIDAL) | Not Applicable | Whitby | Not Applicable | 4:30 | 5 | 3.2 | 2020 | 99.83 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00578
YWS00579 | Yorkshire Water | Live | LYTHE BANK SPS | LYTHE BANK/CSO | 27/29/0042 | 27/29/0042 | 1 | Storm discharge at pumping station | NZ8608013130 | 486080 | 513130 | GB650401500004 | Yorkshire North | Coastal Water | 3179 | Esk TraC | 3040 | Humber TraC | NORTH SEA | Not Applicable | Sandsend | Not Applicable | 522:42 | 47 | 15.6 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00579
YWS00580 | Yorkshire Water | Live | NORTH TERRACE CSO | NORTH TERRACE/CSO | 27/29/0043 | 27/29/0043 | 1 | SO on sewer network | NZ8934011530 | 489349 | 511523 | GB650401500004 | Yorkshire North | Coastal Water | 3179 | Esk TraC | 3040 | Humber TraC | THE NORTH SEA | Not Applicable | Whitby | Not Applicable | 0:00 | 0 | 0.2 | 2020 | 42.31 | Sensor failure / issue | Resolved - Sep | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00580
YWS00581 | Yorkshire Water | Live | WHITBY ROAD BRIDGE CSO | WHITBY ROAD BDG/CSO | 27/29/0044 | 27/29/0044 | 1 | Storm discharge at pumping station | TA0346091320 | 503460 | 491320 | GB650401500004 | Yorkshire North | Coastal Water | 3179 | Esk TraC | 3040 | Humber TraC | THE NORTH SEA | Not Applicable | Scarborough North Bay | Not Applicable | 303:26 | 54 | 56.4 | 2020 | 99.98 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement ongoing | SOAF investigation ongoing | YWS00581
YWS00582 | Yorkshire Water | Live | ROBIN HOODS BAY SEA OUTFALL | ROBIN HOODS BAY LWR/CSO | 27/29/0045 | 27/29/0045 | 1 | Storm discharge at pumping station | NZ9557005290 | 495570 | 505290 | GB650401500004 | Yorkshire North | Coastal Water | 3179 | Esk TraC | 3040 | Humber TraC | NORTH SEA | Not Applicable | Robin Hoods Bay | Not Applicable | 203:56 | 31 | 19.6 | 2020 | 99.98 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00582
YWS00583 | Yorkshire Water | Live | STAITHES HARBOUR PUMPING STATION | STAITHES/CSO | 27/29/0050 | 27/29/0050 | 1 | Storm discharge at pumping station | NZ7828018940 | 478300 | 519250 | GB650401500004 | Yorkshire North | Coastal Water | 3179 | Esk TraC | 3040 | Humber TraC | STAITHES HARBOUR - NORTH SEA | Not Applicable | Not Applicable | Not Applicable | 1696:45 | 102 | 48.4 | 2020 | 100 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS00583
YWS00584 | Yorkshire Water | Live | RUNSWICK BAY SPS | RUNSWICK BAY LOWER/CSO | 27/29/0051 | 27/29/0051 | 1 | Storm discharge at pumping station | NZ8135016550 | 481350 | 516550 | GB650401500004 | Yorkshire North | Coastal Water | 3179 | Esk TraC | 3040 | Humber TraC | NORTH SEA | Not Applicable | Runswick Bay | Not Applicable | 462:48 | 32 | 14.6 | 2020 | 99.97 |  |  | High spill threshold not met | High spill threshold not met | Operational investigation completed | No improvement action in reporting period | No SOAF investigation required | YWS00584
YWS00585 | Yorkshire Water | Live | NEW ROAD BRIDGE CSO | NEW ROAD BRIDGE/CSO | 27/29/0052 | 27/29/0052 | A1 | SO on sewer network | NZ9522005000 | 495224 | 504998 | Not part of a WFD catchment | Not part of a WFD catchment | River | N/A | N/A | N/A | N/A | NORTH SEA | Not Applicable | Robin Hoods Bay | Not Applicable | 5:06 | 7 | 5.6 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00585
YWS00586 | Yorkshire Water | Live | STAINSACRE INDUSTRIAL ESTATE | FAIRFIELD WAY/CSO | 27/29/0056 | 27/29/0056 | 2 | Storm discharge at pumping station | NZ9092009510 | 490920 | 509510 | Not part of a WFD catchment | Not part of a WFD catchment | River | N/A | N/A | N/A | N/A | SPITAL BECK | Not Applicable | Not Applicable | Not Applicable | 26:00 | 20 | 15.8 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00586
YWS00587 | Yorkshire Water | Live | UPGANG LANE SPS | UPGANG LANE/NO 2 CSO | 27/29/0057 | 27/29/0057 | 2 | Storm discharge at pumping station | NZ8815011900 | 488150 | 511910 | Not part of a WFD catchment | Not part of a WFD catchment | River | N/A | N/A | N/A | N/A | UPGANG BECK | Not Applicable | Whitby | Not Applicable | 18:42 | 9 | 4.6 | 2020 | 99.67 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00587
YWS00588 | Yorkshire Water | Live | HAWSKER SEWAGE PUMPING STATION | HAWSKER/NO 2 CSO | 27/29/0058 | 27/29/0058 | A1 | SO on sewer network | NZ9211007450 | 492110 | 507450 | GB104027068140 | Rigg Mill Bk/Long Mill Bk catch (trib of Esk) | River | 3177 | Esk | 3037 | Esk and Coast | STAINSACRE BECK | Not Applicable | Not Applicable | Not Applicable | 358:00 | 71 | 55.2 | 2020 | 100 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement ongoing | SOAF investigation ongoing | YWS00588
YWS00589 | Yorkshire Water | Live | GOATHLAND GREENWAY SPS | GOATHLAND GRNWAY/CSO | 27/29/0059 | 27/29/0059 | A2 | Storm discharge at pumping station | NZ8364601426 | 483646 | 501426 | GB104027068030 | Murk Esk from Wheeldale Gill to Eller Beck | River | 3177 | Esk | 3037 | Esk and Coast | ELLER BECK | Not Applicable | Not Applicable | Not Applicable | 225:15 | 28 | 25.8 | 2020 | 99.97 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00589
YWS00590 | Yorkshire Water | Live | LEALHOLM SEWAGE PUMPING STATION | LEALHOLM SCHOOL/CSO | 27/29/0061 | 27/29/0061 | 2 | Storm discharge at pumping station | NZ7625007640 | 476250 | 507640 | GB104027068150 | Esk from Sleddale Beck to Ruswarp | River | 3177 | Esk | 3037 | Esk and Coast | RIVER ESK | Not Applicable | Not Applicable | Not Applicable | 147:15 | 17 | 17.6 | 2020 | 88.97 | Sensor failure / issue | Resolved - Jun | High spill threshold not met | High spill threshold not met | Operational investigation completed | No improvement action in reporting period | No SOAF investigation required | YWS00590
YWS00591 | Yorkshire Water | Live | CASTLETON SEWAGE PUMPING STATION | CASTLETON/SPS | 27/29/0062 | 27/29/0062 | A2 | Storm discharge at pumping station | NZ6912008033 | 469120 | 508033 | GB104027068110 | Danby Beck catchement (trib of Esk) | River | 3177 | Esk | 3037 | Esk and Coast | DANBY BECK | Not Applicable | Not Applicable | Not Applicable | 206:45 | 49 | 57 | 2020 | 89.99 | Sensor failure / issue | Resolved - Oct | High spill threshold not met | Performance - Pump failure / issue | UWWTR investigation ongoing, Operational investigation completed | Operational improvement completed | SOAF investigation ongoing | YWS00591
YWS00592 | Yorkshire Water | Live | GOATHLAND STW FINAL EFFLUENT | GOATHLAND/NO 3 STW | 27/29/0065 | 27/29/0065 | A2 | Inlet SO at WwTW | NZ8284001700 | 482840 | 501700 | GB104027068050 | Eller beck from Source to Murk Esk | River | 3177 | Esk | 3037 | Esk and Coast | UNNAMED TRIB OF MURK ESK | Not Applicable | Not Applicable | Not Applicable | 724:15 | 99 | 97 | 2020 | 99.94 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation ongoing | Operational improvement ongoing | SOAF investigation ongoing | YWS00592
YWS00593 | Yorkshire Water | Live | RUSWARP SEWAGE PUMPING STATION | RUSWARP/CSO | 27/29/0071 | 27/29/0071 | A1 | Storm discharge at pumping station | NZ8901009060 | 489010 | 509060 | GB104027068150 | Esk from Sleddale Beck to Ruswarp | River | 3177 | Esk | 3037 | Esk and Coast | RIVER ESK | Not Applicable | Not Applicable | Not Applicable | 587:45 | 101 | 103.6 | 2020 | 96.78 |  |  | Data collection - Tidal / river inundation | Data collection - Tidal / river inundation | UWWTR investigation ongoing, Operational investigation completed | Operational improvement completed | SOAF investigation ongoing | YWS00593
YWS00594 | Yorkshire Water | Live | MAYFIELD ROAD CSO | MAYFIELD ROAD/NO 2 CSO | 27/29/0073 | 27/29/0073 | 1 | SO on sewer network | NZ8899010470 | 488997 | 510470 | Not part of a WFD catchment | Not part of a WFD catchment | River | N/A | N/A | N/A | N/A | BAGDALE BECK | Not Applicable | Not Applicable | Not Applicable | 3:15 | 4 | 2.2 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00594
YWS00595 | Yorkshire Water | Live | EAST CRESCENT CSO | EAST CRESCENT/CSO | 27/29/0074 | 27/29/0074 | A1 | SO on sewer network | NZ8986011368 | 489860 | 511368 | GB510402703400 | ESK (E) | Transitional Water | 3179 | Esk TraC | 3040 | Humber TraC | RIVER ESK TIDAL | Not Applicable | Whitby | Not Applicable | 0:00 | 0 | 0 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00595
YWS00596 | Yorkshire Water | Live | BOULBY BANK CSO | BOULBY BANK/CSO | 27/29/0075 | 27/29/0075 | A1 | SO on sewer network | NZ9012410808 | 490124 | 510808 | GB510402703400 | ESK (E) | Transitional Water | 3179 | Esk TraC | 3040 | Humber TraC | RIVER ESK TIDAL | Not Applicable | Not Applicable | Not Applicable | 0:15 | 1 | 0.4 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00596
YWS00597 | Yorkshire Water | Live | CRESCENT TERRACE CSO | CRESCENT TERRACE/CSO | 27/29/0076 | 27/29/0076 | A1 | SO on sewer network | NZ8986011380 | 489860 | 511368 | GB510402703400 | ESK (E) | Transitional Water | 3179 | Esk TraC | 3040 | Humber TraC | RIVER ESK (TIDAL) | Not Applicable | Whitby | Not Applicable | 1:00 | 2 | 4 | 2020 | 99.97 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00597
YWS00598 | Yorkshire Water | Live | THE ORCHARD NO 2 CSO | THE ORCHARDS/NO 2 CSO | 27/29/0077 | 27/29/0077 | A1 | SO on sewer network | NZ8287701589 | 482877 | 501589 | GB104027068030 | Murk Esk from Wheeldale Gill to Eller Beck | River | 3177 | Esk | 3037 | Esk and Coast | TRIB OF WEST BECK / MURK ESK | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00598
YWS00599 | Yorkshire Water | Live | PORRET LANE COMBINED SEWER OVERFLOW | PORRET LANE/NO 2 CSO | 27/29/0078 | 27/29/0078 | 1 | SO on sewer network | NZ7893016920 | 478932 | 516920 | GB104027068750 | Newton Beck from Source to Staithes Beck | River | 3390 | Sandsend and Staithes | 3037 | Esk and Coast | TRIB OF DALES BECK | Not Applicable | Not Applicable | Not Applicable | 119:00 | 33 | 31.4 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00599
YWS00600 | Yorkshire Water | Live | WESLEY SQUARE STAITHES SPS | WESLEY SQR STAITHES/CSO | 27/29/0079 | 27/29/0079 | A2 | Storm discharge at pumping station | NZ7811918852 | 478119 | 518852 | GB104027068770 | Staithes Beck from Source to Newton Beck | River | 3390 | Sandsend and Staithes | 3037 | Esk and Coast | STAITHES BECK | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0 | 2020 | 97.8 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00600
YWS00601 | Yorkshire Water | Live | STAINSACRE SEWAGE PUMPING STATION | STAINSACRE/CSO | 27/29/0086 | 27/29/0086 | A1 | Storm discharge at pumping station | NZ9100008310 | 491000 | 508310 | GB104027068140 | Rigg Mill Bk/Long Mill Bk catch (trib of Esk) | River | 3177 | Esk | 3037 | Esk and Coast | INTAKE BECK | Not Applicable | Not Applicable | Not Applicable | 6:30 | 7 | 4.8 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00601
YWS00602 | Yorkshire Water | Live | WHITBY GOLF COURSE CSO | WHITBY GOLF COURSE/CSO | 27/29/0087 | 27/29/0087 | 1 | SO on sewer network | NZ8829011350 | 488290 | 511350 | Not part of a WFD catchment | Not part of a WFD catchment | River | N/A | N/A | N/A | N/A | TRIB OF UPGANG BECK | Not Applicable | Whitby | Not Applicable | 46:02 | 23 | 15.6 | 2020 | 99.98 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00602
YWS00603 | Yorkshire Water | Live | ESPLANADE WHITBY CSO | ESPLANADE WHITBY/CSO | 27/29/0088 | 27/29/0088 | A1 | SO on sewer network | NZ8986111380 | 489860 | 511368 | GB510402703400 | ESK (E) | Transitional Water | 3179 | Esk TraC | 3040 | Humber TraC | RIVER ESK | Not Applicable | Whitby | Not Applicable | 30:00 | 19 | 54.4 | 2020 | 79.27 | Sensor failure / issue | Resolved - Mar | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement completed | SOAF investigation ongoing | YWS00603
YWS00604 | Yorkshire Water | Live | LOWDALE LANE NO 2 CSO | LOWDALE LANE/NO 2 CSO | 27/29/0089 | 27/29/0089 | A1 | SO on sewer network | NZ8695507900 | 486955 | 507900 | GB104027068100 | Little Beck/May Beck catchment (trib of Esk) | River | 3177 | Esk | 3037 | Esk and Coast | IBURNDALE BECK | Not Applicable | Not Applicable | Not Applicable | 107:45 | 29 | 19 | 2020 | 99.86 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00604
YWS00605 | Yorkshire Water | Live | RUNSWICK BECK CSO | RUNSWICK BECK/CSO | 27/29/0090 | 27/29/0090 | 1 | Storm discharge at pumping station | NZ8074016120 | 480740 | 516120 | Not part of a WFD catchment | Not part of a WFD catchment | River | N/A | N/A | N/A | N/A | CULVERTED RUNWICK BECK | Not Applicable | Runswick Bay | Not Applicable | 713:42 | 62 | 54.4 | 2020 | 98.82 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | No investigation activity in reporting period | No improvement action in reporting period | SOAF investigation completed - Work required | YWS00605
YWS00607 | Yorkshire Water | Live | GLAISDALE STW | GLAISDALE/STW | 27/29/0105 | 27/29/0105 | 2 | Inlet SO at WwTW | NZ7800005520 | 477960 | 505520 | GB104027068150 | Esk from Sleddale Beck to Ruswarp | River | 3177 | Esk | 3037 | Esk and Coast | RIVER ESK | Not Applicable | Not Applicable | Not Applicable | 445:00 | 88 | 63.6 | 2020 | 99.97 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS00607
YWS00608 | Yorkshire Water | Live | GROSMONT STW | GROSMONT/STW | 27/29/0106 | 27/29/0106 | A2 | Storm tank at WwTW | NZ8262005500 | 482626 | 505507 | GB104027068150 | Esk from Sleddale Beck to Ruswarp | River | 3177 | Esk | 3037 | Esk and Coast | RIVER ESK | Not Applicable | Not Applicable | Not Applicable | 197:15 | 23 | 23.2 | 2020 | 99.58 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00608
YWS00609 | Yorkshire Water | Live | GROSMONT STW | GROSMONT/STW | 27/29/0106 | 27/29/0106 | A3 | Inlet SO at WwTW | NZ8262005500 | 482626 | 505507 | GB104027068150 | Esk from Sleddale Beck to Ruswarp | River | 3177 | Esk | 3037 | Esk and Coast | RIVER ESK | Not Applicable | Not Applicable | Not Applicable | 47:30 | 14 | 21.8 | 2020 | 99.58 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00609
YWS00610 | Yorkshire Water | Live | DANBY SEWAGE TREATMENT WORKS | DANBY/STW | 27/29/0108 | 27/29/0108 | A2 | Inlet SO at WwTW | NZ7093008320 | 470922 | 508301 | GB104027068150 | Esk from Sleddale Beck to Ruswarp | River | 3177 | Esk | 3037 | Esk and Coast | RIVER ESK | Not Applicable | Not Applicable | Not Applicable | 169:30 | 43 | 105.4 | 2020 | 99.96 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00610
YWS00611 | Yorkshire Water | Live | LEALHOLM SEWAGE TREATMENT WORKS | LEALHOLM/STW | 27/29/0109 | 27/29/0109 | A2 | Inlet SO at WwTW | NZ7654007530 | 476540 | 507530 | GB104027068150 | Esk from Sleddale Beck to Ruswarp | River | 3177 | Esk | 3037 | Esk and Coast | RIVER ESK | Not Applicable | Not Applicable | Not Applicable | 73:15 | 34 | 29.8 | 2020 | 99.46 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00611
YWS00612 | Yorkshire Water | Live | EGTON BRIDGE SEWAGE TREATMENT WORKS | EGTON BRIDGE/STW | 27/29/0110 | 27/29/0110 | A2 | Inlet SO at WwTW | NZ8093004930 | 480860 | 505060 | GB104027068150 | Esk from Sleddale Beck to Ruswarp | River | 3177 | Esk | 3037 | Esk and Coast | RIVER ESK | Not Applicable | Not Applicable | Not Applicable | 197:15 | 42 | 44.8 | 2020 | 100 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00612
YWS00613 | Yorkshire Water | Live | LOWER UNDERHILL CSO | LOWER UNDER HILL/CSO | 27/29/0118 | 27/29/0118 | 1 | SO on sewer network | NZ7782005450 | 477853 | 505475 | GB104027068150 | Esk from Sleddale Beck to Ruswarp | River | 3177 | Esk | 3037 | Esk and Coast | UNNAMED TRIB OF RIVER ESK | Not Applicable | Not Applicable | Not Applicable | 57:15 | 12 | 20.2 | 2020 | 91.79 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00613
YWS00614 | Yorkshire Water | Live | IVY HOUSE CSO | IVY HOUSE/CSO | 27/29/0119 | 27/29/0119 | A1 | SO on sewer network | NZ8614208727 | 486142 | 508727 | GB104027068150 | Esk from Sleddale Beck to Ruswarp | River | 3177 | Esk | 3037 | Esk and Coast | TRIB OF RIVER ESK | Not Applicable | Not Applicable | Not Applicable | 4:30 | 8 | 7.5 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00614
YWS00615 | Yorkshire Water | Live | BIRCH AVENUE CSO | BIRCH AVENUE/CSO | 27/29/0121 | 27/29/0121 | 1 | SO on sewer network | NZ8707007600 | 487070 | 507607 | GB104027068100 | Little Beck/May Beck catchment (trib of Esk) | River | 3177 | Esk | 3037 | Esk and Coast | IBURNDALE BECK | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 1.4 | 2020 | 70.64 | Comms failure / issue | Resolved - Jun | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00615
YWS00617 | Yorkshire Water | Live | BRIDGE INN CSO | BRIDGE INN/CSO | 27/29/0125 | 27/29/0125 | A1 | SO on sewer network | NZ8898809113 | 488988 | 509113 | GB104027068150 | Esk from Sleddale Beck to Ruswarp | River | 3177 | Esk | 3037 | Esk and Coast | RIVER ESK (TIDAL) | Not Applicable | Not Applicable | Not Applicable | 188:45 | 41 | 42 | 2020 | 97.43 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement ongoing | SOAF investigation ongoing | YWS00617
YWS00618 | Yorkshire Water | Live | WATTON WWTW | WATTON/STW | 2704 | 2704 | A2 | Storm tank at WwTW | TA0146049830 | 501466 | 449829 | GB104026066980 | Middleton on the Wolds and Watton Beck | River | 3274 | Lower Hull | 3039 | Hull and East Riding | WATTON BECK | Not Applicable | Not Applicable | Not Applicable | 250:15 | 36 | 58.6 | 2020 | 99.96 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00618
YWS00619 | Yorkshire Water | Live | NELSON STREET CSO | NELSON STREET/CSO | 2714 | 2714 | A1 | SO on sewer network | SE1642732569 | 416427 | 432569 | GB104027062862 | Bradford Beck (Clayton Bk to R Aire) | River | 3307 | Middle Aire | 3001 | Aire and Calder | BOWLING BECK | Not Applicable | Not Applicable | Not Applicable | 1:00 | 3 | 5 | 2020 | 11.94 | Comms failure / issue | Scheduled | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00619
YWS00620 | Yorkshire Water | Live | VALLEY CRESCENT CSO | VALLEY CRESCENT/CSO | 2721 | 2721 | A1 | SO on sewer network | SK3899170440 | 438991 | 370440 | GB104027057640 | Spital/Calow/Muster Brook | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | SPITAL BROOK CULVERTED | Not Applicable | Not Applicable | Not Applicable | 9:00 | 14 | 28.4 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00620
YWS00621 | Yorkshire Water | Live | BRANDY MILL 34 CSO | BRANDY MILL 34/CSO | 2739 | 2739 | A1 | SO on sewer network | SE0609740305 | 406097 | 440305 | GB104027062891 | Worth from Bridgehouse Beck to R Aire | River | 3307 | Middle Aire | 3001 | Aire and Calder | RIVER WORTH | Not Applicable | Not Applicable | Not Applicable | 40:45 | 20 | 26.2 | 2020 | 99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00621
YWS00622 | Yorkshire Water | Live | BECK BOTTOM CSO | BECK BOTTOM/CSO | 2754 | 2754 | A1 | SO on sewer network | SE1947536872 | 419475 | 436872 | GB104027063032 | Aire from Gill Beck (Baildon) to River Calder | River | 3265 | Lower Aire | 3001 | Aire and Calder | CARR BECK | Not Applicable | Not Applicable | Not Applicable | 60:30 | 38 | 33.6 | 2020 | 79.47 | Comms failure / issue | Resolved - Feb | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00622
YWS00623 | Yorkshire Water | Live | GREEN LANE JUNCTION NO 2 CSO | GREEN LANE JUNCTION/2 CSO | 2756 | 2756 | A1 | SO on sewer network | SE1481038038 | 414810 | 438038 | GB104027063034 | Aire (R Worth to Gill Beck) | River | 3307 | Middle Aire | 3001 | Aire and Calder | RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0.6 | 2020 | 99.8 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00623
YWS00624 | Yorkshire Water | Live | LISTING MILL FARM CSO | LISTING MILL FARM/CSO | 2767 | 2767 | 1 | SO on sewer network | SE2071024850 | 420716 | 424859 | GB104027062710 | Spen Beck from Source to River Calder | River | 3268 | Lower Calder | 3001 | Aire and Calder | TRIBUTARY OF THE RIVER SPEN | Not Applicable | Not Applicable | Not Applicable | 78:30 | 38 | 41 | 2020 | 100 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00624
YWS00625 | Yorkshire Water | Live | PADDOCK FOOT CSO | PADDOCK FOOT/CSO | 2773 | 2773 | A1 | SO on sewer network | SE1336516131 | 413365 | 416131 | GB104027063330 | Colne from Wessenden Brook to R Holme | River | 3097 | Colne and Holme | 3001 | Aire and Calder | CULVERTED TRIB OF RIVER COLNE | Not Applicable | Not Applicable | Not Applicable | 97:15 | 57 | 60.6 | 2020 | 100 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | No investigation activity in reporting period | No improvement action in reporting period | SOAF investigation completed - No work required | YWS00625
YWS00626 | Yorkshire Water | Live | LOWFIELDS ROAD CSO | LOWFIELDS ROAD/CSO | 2774 | 2774 | A1 | SO on sewer network | SE2826331603 | 428263 | 431603 | GB104027062830 | Low/Wortley/Pudsey Bks | River | 3265 | Lower Aire | 3001 | Aire and Calder | WORTLEY BECK CULVERTED | Not Applicable | Not Applicable | Not Applicable | 40:30 | 32 | 35.4 | 2020 | 98.15 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00626
YWS00627 | Yorkshire Water | Live | BRINSWORTH STREET SPS | BRINSWORTH STREET/CSO | 2775 | 2775 | A1 | SO on sewer network | SK4230692630 | 442306 | 392630 | GB104027057452 | Don from River Rother to River Dearne | River | 3312 | Middle Don | 3029 | Don and Rother | HOLMES TAIL GOIT | Not Applicable | Not Applicable | Not Applicable | 110:30 | 19 | 15.6 | 2020 | 99.25 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00627
YWS00628 | Yorkshire Water | Live | WOOLLEY STW | WOOLLEY VILLAGE/STW/3XDWF OVERFLOW | 2776 | 2776 | 3 | Storm tank at WwTW | SE3270013700 | 432700 | 413700 | GB104027062530 | Owler Beck from Source to River Calder | River | 3268 | Lower Calder | 3001 | Aire and Calder | TOTTY BECK | Not Applicable | Not Applicable | Not Applicable | 871:45 | 88 | 107 | 2020 | 99.94 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS00628
YWS00629 | Yorkshire Water | Live | WOOLLEY STW | WOOLLEY VILLAGE/STW/6XDWF OVERFLOW | 2776 | 2776 | 4 | Inlet SO at WwTW | SE3270013700 | 432700 | 413700 | GB104027062530 | Owler Beck from Source to River Calder | River | 3268 | Lower Calder | 3001 | Aire and Calder | TOTTY BECK | Not Applicable | Not Applicable | Not Applicable | 1:30 | 5 | 7.2 | 2020 | 99.97 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00629
YWS00630 | Yorkshire Water | Live | BUCK MILL LANE CSO | BUCK MILL LANE/CSO | 2788 | 2788 | A1 | SO on sewer network | SE1689338881 | 416893 | 438881 | GB104027063032 | Aire from Gill Beck (Baildon) to River Calder | River | 3265 | Lower Aire | 3001 | Aire and Calder | BRACKENDALE BECK | Not Applicable | Not Applicable | Not Applicable | 152:45 | 58 | 55.2 | 2020 | 95.88 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation completed | No improvement action in reporting period | SOAF investigation completed - No work required | YWS00630
YWS00631 | Yorkshire Water | Live | RETFORD ROAD CSO | RETFORD RD REC GND/1 CSO | 2805 | 2805 | 1 | SO on sewer network | SK4317085820 | 443170 | 385825 | GB104027057772 | Rother, Doe Lea to Don | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | RIVER ROTHER | Not Applicable | Not Applicable | Not Applicable | 252:00 | 24 | 64.25 | 2020 | 100 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS00631
YWS00632 | Yorkshire Water | Live | SANDALL WWTW | SANDALL/STW | 2829(T) | 2829(T) | A2 | Storm tank at WwTW | SE5981006170 | 459810 | 406170 | GB104028064330 | Hatfield Waste Drain Catchment (trib of Torne/Three Rivers) | River | 3234 | Isle of Axholme | 3041 | Idle and Torne | R. DON & R. DON (OLD COURSE) | Not Applicable | Not Applicable | Not Applicable | 158:45 | 11 | 20 | 2021 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00632
YWS00633 | Yorkshire Water | Live | ABERFORD ROAD CSO | ABERFORD ROAD/CSO | 2830 | 2830 | 1 | SO on sewer network | SE3480023700 | 434744 | 423606 | GB104027062632 | Calder from River Chald to River Aire | River | 3268 | Lower Calder | 3001 | Aire and Calder | RIVER CALDER | Not Applicable | Not Applicable | Not Applicable | 61:15 | 40 | 40.8 | 2020 | 100 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00633
YWS00634 | Yorkshire Water | Live | BRADLEY OLD WORKS CSO | BRADLEY OLD WKS/CSO | 2836 | 2836 | A1 | SO on sewer network | SD9969947967 | 399699 | 447967 | GB104027063033 | Aire (Eshton Beck to R Worth) | River | 3484 | Upper Aire | 3001 | Aire and Calder | LAITHEHOUSE BECK | Not Applicable | Not Applicable | Not Applicable | 20:45 | 15 | 15.4 | 2020 | 92.47 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00634
YWS00635 | Yorkshire Water | Live | CARLETON WEST STREET SPS | CARLETON WEST ST/CSO | 2837 | 2837 | A2 | Storm discharge at pumping station | SD9703950322 | 397039 | 450322 | GB104027063033 | Aire (Eshton Beck to R Worth) | River | 3484 | Upper Aire | 3001 | Aire and Calder | CARLETON BECK | Not Applicable | Not Applicable | Not Applicable | 206:15 | 74 | 67.6 | 2020 | 99.77 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00635
YWS00636 | Yorkshire Water | Live | SKIPTON SEWAGE TREATMENT WORKS | SKIPTON/STW/3XDWF OVERFLOW | 2838 | 2838 | A2 | Storm tank at WwTW | SD9859049710 | 398590 | 449710 | GB104027063033 | Aire (Eshton Beck to R Worth) | River | 3484 | Upper Aire | 3001 | Aire and Calder | RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 891:50 | 86 | 75.2 | 2020 | 99.97 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00636
YWS00637 | Yorkshire Water | Live | SKIPTON SEWAGE TREATMENT WORKS | SKIPTON/STW/6XDWF OVERFLOW | 2838 | 2838 | A3 | Inlet SO at WwTW | SD9859049710 | 398590 | 449710 | GB104027063033 | Aire (Eshton Beck to R Worth) | River | 3484 | Upper Aire | 3001 | Aire and Calder | RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 525:30 | 115 | 96.8 | 2020 | 99.9 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS00637
YWS00638 | Yorkshire Water | Live | BATLEY GRANGE ROAD CSO | BATLEY GRANGE ROAD/CSO | 2844 | 2844 | A1 | SO on sewer network | SE2500923615 | 425009 | 423615 | GB104027062670 | Batley Beck from Source to River Calder | River | 3268 | Lower Calder | 3001 | Aire and Calder | GREENHILL DIKE CULVERTED | Not Applicable | Not Applicable | Not Applicable | 0:15 | 1 | 0.4 | 2020 | 99.81 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00638
YWS00639 | Yorkshire Water | Live | LEYBURN WPC WORKS | LEYBURN/STW | 2846 | 2846 | 2 | Storm tank at WwTW | SE1221088940 | 412210 | 488940 | GB104027069464 | Ure from Mill Beck to Thornton Steward Beck | River | 3505 | Upper Ure | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER URE | Not Applicable | Not Applicable | Not Applicable | 3169:15 | 212 | 167.6 | 2020 | 99.81 |  |  | Performance - GW inundation | Performance - GW inundation | UWWTR investigation ongoing, Operational investigation completed | Operational improvement ongoing | SOAF investigation ongoing | YWS00639
YWS00640 | Yorkshire Water | Live | LEYBURN WPC WORKS | LEYBURN/STW | 2846 | 2846 | 4 | Inlet SO at WwTW | SE1213089250 | 412130 | 489250 | GB104027069464 | Ure from Mill Beck to Thornton Steward Beck | River | 3505 | Upper Ure | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER URE | Not Applicable | Not Applicable | Not Applicable | 103:15 | 14 | 22.2 | 2020 | 99.81 |  |  | High spill threshold not met | High spill threshold not met | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00640
YWS00641 | Yorkshire Water | Live | BAGLEY LANE 39 CSO | BAGLEY LANE 39/CSO | 2847 | 2847 | A1 | SO on sewer network | SE2226535662 | 422265 | 435662 | GB104027063032 | Aire from Gill Beck (Baildon) to River Calder | River | 3265 | Lower Aire | 3001 | Aire and Calder | BAGLEY BECK CULVERTED | Not Applicable | Not Applicable | Not Applicable | 17:45 | 14 | 3.8 | 2020 | 99.96 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00641
YWS00642 | Yorkshire Water | Live | CARVER CLOUGH NO 2 CSO | CARVER CLOUGH/NO 2 CSO | 2853 | 2853 | A1 | SO on sewer network | SE0345518360 | 403445 | 418360 | GB104027062520 | Booth Dean Clough from Source to River Ryburn | River | 3310 | Middle Calder | 3001 | Aire and Calder | CARVER CLOUGH | Not Applicable | Not Applicable | Not Applicable | 12:15 | 6 | 2 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00642
YWS00643 | Yorkshire Water | Live | GARGRAVE SEWAGE TREATMENT WORKS | GARGRAVE/STW | 2855 | 2855 | A2 | Inlet SO at WwTW | SD9461853570 | 394570 | 453670 | GB104027063033 | Aire (Eshton Beck to R Worth) | River | 3484 | Upper Aire | 3001 | Aire and Calder | RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 178:45 | 64 | 69.6 | 2020 | 100 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement ongoing | SOAF investigation ongoing | YWS00643
YWS00644 | Yorkshire Water | Live | ALL SAINTS CHURCH CSO | ALL SAINTS CHURCH/CSO | 2889 | 2889 | A1 | SO on sewer network | SE4259125912 | 442591 | 425912 | GB104027062760 | Aire from River Calder to River Ouse | River | 3265 | Lower Aire | 3001 | Aire and Calder | RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 4:00 | 9 | 8.6 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00644
YWS00645 | Yorkshire Water | Live | JUBILEE TERRACE CSO | MARBLE ARCH/CSO | 2908 | 2908 | A1 | SO on sewer network | SE5970452016 | 459704 | 452016 | GB104027069593 | Ouse from River Nidd to Stillingfleet Beck | River | 3499 | Upper Ouse Yorkshire | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER OUSE | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0.33 | 2020 | 8.2 | Sensor failure / issue | Resolved - January after reporting year | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00645
YWS00646 | Yorkshire Water | Live | WESTFIELD LANE CSO | WESTFIELD LANE/CSO | 2913 | 2913 | A1 | SO on sewer network | SE4109030568 | 441090 | 430568 | GB104027062810 | Lin Dike from Source to River Aire | River | 3265 | Lower Aire | 3001 | Aire and Calder | HOLLINS BECK | Not Applicable | Not Applicable | Not Applicable | 0:30 | 1 | 0.2 | 2020 | 96.48 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00646
YWS00647 | Yorkshire Water | Live | YWS UNKNOWN SITES DEFAULT | RAVENSBRIDGE IND EST/CSO | 2921 | 2921 | A1 | SO on sewer network | SE2404020959 | 424040 | 420959 | GB104027062631 | Calder from River Colne to River Chald | River | 3268 | Lower Calder | 3001 | Aire and Calder | RIVER CALDER | Not Applicable | Not Applicable | Not Applicable | 108:45 | 32 | 40.2 | 2020 | 70.26 | Comms failure / issue | Scheduled | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS00647
YWS00648 | Yorkshire Water | Live | Not matched in EA Consents Database | SCOUTHILL R D/CSO | EPR/SB3590EA | EPR/SB3590EA | A1 | SO on sewer network | SE2404020959 | 424040 | 420959 | GB104027062631 | Calder from River Colne to River Chald | River | 3268 | Lower Calder | 3001 | Aire and Calder | Not matched in EA Consents Database | Not Applicable | Not Applicable | Not Applicable | 24:15 | 13 | 12.6 | 2020 | 95.07 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00648
YWS00649 | Yorkshire Water | Live | WILLIAMTHORPE STW | WILLIAMTHORPE/STW | 2941 | 2941 | A2 | Storm tank at WwTW | SK4316066500 | 443160 | 366500 | GB104027057640 | Spital/Calow/Muster Brook | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | WILLIAMTHORPE RESERVOIR | Not Applicable | Not Applicable | Not Applicable | 607:00 | 81 | 88.4 | 2020 | 99.97 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00649
YWS00650 | Yorkshire Water | Live | TULIP TREE CLOSE CSO | TULIP TREE CLOSE/CSO | 2943 | 2943 | A1 | SO on sewer network | SK4420684234 | 444206 | 384234 | GB104027057772 | Rother, Doe Lea to Don | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | RIVER ROTHER | Not Applicable | Not Applicable | Not Applicable | 11:15 | 6 | 13.8 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00650
YWS00651 | Yorkshire Water | Live | HEATHCOTE DRIVE CSO | HEATHCOTE DRIVE/CSO | 2952 | 2952 | 1 | SO on sewer network | SK3994070040 | 439949 | 370047 | GB104027057640 | Spital/Calow/Muster Brook | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | SPITAL BROOK | Not Applicable | Not Applicable | Not Applicable | 102:45 | 27 | 26 | 2020 | 99.42 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00651
YWS00652 | Yorkshire Water | Live | RAGLAN STREET CSO | RAGLAN STREET/CSO | 2989 | 2989 | A1 | SO on sewer network | SE0842025814 | 408420 | 425814 | GB104027062780 | Hebble Brook from Source to River Calder | River | 3310 | Middle Calder | 3001 | Aire and Calder | HEBBLE BROOK (CULVERTED) | Not Applicable | Not Applicable | Not Applicable | 182:45 | 74 | 82.6 | 2020 | 100 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | No investigation activity in reporting period | No improvement action in reporting period | SOAF investigation completed - No work required | YWS00652
YWS00653 | Yorkshire Water | Live | THURGOLAND SEWAGE PUMPING STATION | THURGOLAND/CSO | 2992 | 2992 | A1 | SO on sewer network | SE2927200075 | 429272 | 400075 | GB104027057490 | Don from Scout Dyke to the Little Don | River | 3490 | Upper Don | 3029 | Don and Rother | RIVER DON | Not Applicable | Not Applicable | Not Applicable | 868:45 | 123 | 155 | 2020 | 99.98 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | Operational investigation completed | No improvement action in reporting period | SOAF investigation completed - No work required | YWS00653
YWS00654 | Yorkshire Water | Live | OAKWORTH CSO | OAKWORTH/CSO | 2998 | 2998 | A1 | SO on sewer network | SE0421038430 | 404210 | 438430 | GB104027062891 | Worth from Bridgehouse Beck to R Aire | River | 3307 | Middle Aire | 3001 | Aire and Calder | RIVER WORTH | Not Applicable | Not Applicable | Not Applicable | 80:30 | 33 | 32.4 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00654
YWS00655 | Yorkshire Water | Live | OAKWORTH CSO | INGROW STATION/CSO | 2998 | EPR/VB3296RV | A1 | SO on sewer network | SE0568039770 | 405680 | 439770 | GB104027062891 | Worth from Bridgehouse Beck to R Aire | River | 3307 | Middle Aire | 3001 | Aire and Calder | RIVER WORTH | Not Applicable | Not Applicable | Not Applicable | 8:15 | 10 | 4 | 2020 | 99.98 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00655
YWS00656 | Yorkshire Water | Live | YWS UNKNOWN SITES DEFAULT | STANLEY WATER LANE/CSO | 3001 | 3001 | 5 | SO on sewer network | SE3495823780 | 434958 | 423780 | GB104027062632 | Calder from River Chald to River Aire | River | 3268 | Lower Calder | 3001 | Aire and Calder | NOT KNOWN | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00656
YWS00657 | Yorkshire Water | Live | THE MILL NO 2 CSO | THE MILL/NO 2 CSO | 3006 | 3006 | A1 | SO on sewer network | SK4354381608 | 443543 | 381608 | GB104027057772 | Rother, Doe Lea to Don | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | TRIB OF SHORT BROOK | Not Applicable | Not Applicable | Not Applicable | 54:45 | 29 | 32.4 | 2020 | 99.97 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00657
YWS00658 | Yorkshire Water | Live | SWILLINGTON SPS | SWILLINGTON WORKS/CSO | 3007 | 3007 | A2 | SO on sewer network | SE3891029900 | 438920 | 429910 | GB104027063032 | Aire from Gill Beck (Baildon) to River Calder | River | 3265 | Lower Aire | 3001 | Aire and Calder | FLEAKINGLEY BECK | Not Applicable | Not Applicable | Not Applicable | 175:15 | 43 | 51.8 | 2020 | 99.95 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00658
YWS00659 | Yorkshire Water | Live | INGROW LANE CSO | INGROW LANE/CSO | 3054 | 3054 | A1 | SO on sewer network | SE0565539764 | 405655 | 439764 | GB104027062891 | Worth from Bridgehouse Beck to R Aire | River | 3307 | Middle Aire | 3001 | Aire and Calder | RIVER WORTH | Not Applicable | Not Applicable | Not Applicable | 12:15 | 12 | 47.2 | 2020 | 100 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00659
YWS00660 | Yorkshire Water | Live | LUMBROOK NO 2 CSO | LUMBROOK/NO 2 CSO | 306 | 306 | A1 | SO on sewer network | SE1214426904 | 412144 | 426904 | GB104027062700 | Clifton Beck from Source to River Calder | River | 3310 | Middle Calder | 3001 | Aire and Calder | LUMB BROOK CULVERTED | Not Applicable | Not Applicable | Not Applicable | 2:30 | 3 | 2 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00660
YWS00661 | Yorkshire Water | Live | FALDING STREET CSO | FALDING STREET/CSO | 3094 | 3094 | A1 | SO on sewer network | SK3562896047 | 435628 | 396047 | GB104027057440 | Blackburn Brook from Source to River Don | River | 3312 | Middle Don | 3029 | Don and Rother | BLACKBURN BROOK | Not Applicable | Not Applicable | Not Applicable | 35:30 | 13 | 4.8 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00661
YWS00662 | Yorkshire Water | Live | BUTTERTHWAITE LANE CSO | BUTTERTHWAITE LANE/CSO | 3095 | 3095 | A1 | SO on sewer network | SK3656793974 | 436567 | 393974 | GB104027057440 | Blackburn Brook from Source to River Don | River | 3312 | Middle Don | 3029 | Don and Rother | BLACKBURN BROOK | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00662
YWS00663 | Yorkshire Water | Live | WHEEL LANE CSO | WHEEL LANE/CSO | 3096 | 3096 | A1 | SO on sewer network | SK3437893971 | 434378 | 393971 | GB104027057440 | Blackburn Brook from Source to River Don | River | 3312 | Middle Don | 3029 | Don and Rother | TRIB BLACKBURN BROOK | Not Applicable | Not Applicable | Not Applicable | 13:00 | 16 | 14.4 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00663
YWS00664 | Yorkshire Water | Live | FINCH PARK CSO | FINCH PARK/CSO | 3105 | 3105 | 1 | SO on sewer network | TA0273041260 | 502732 | 441193 | GB104026066841 | High Hunsley to Arram Area | River | 3274 | Lower Hull | 3039 | Hull and East Riding | PIGHILL LANE SEWER (DRAIN) | Not Applicable | Not Applicable | Not Applicable | 1:15 | 5 | 5 | 2023 | 99.93 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00664
YWS00665 | Yorkshire Water | Live | ELLAND LOWFIELDS SPS | ELLAND LOWFIELDS/SPS | 3111 | 3111(SS) | 1 | Storm discharge at pumping station | SE1126021800 | 411260 | 421800 | GB104027062642 | Calder from Ryburn Confluence to River Colne | River | 3310 | Middle Calder | 3001 | Aire and Calder | RIVER CALDER | Not Applicable | Not Applicable | Not Applicable | 120:15 | 52 | 63.75 | 2020 | 99.91 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00665
YWS00666 | Yorkshire Water | Live | ELLAND LOWFIELDS SPS | ELLAND LOWFIELDS/SPS | 3111 | 3111(SS) | 2 | Storm discharge at pumping station | SE1126021800 | 411260 | 421800 | GB104027062642 | Calder from Ryburn Confluence to River Colne | River | 3310 | Middle Calder | 3001 | Aire and Calder | RIVER CALDER | Not Applicable | Not Applicable | Not Applicable | 19:00 | 3 | 34.6 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00666
YWS00667 | Yorkshire Water | Live | WEST VALE | ELLAND WEST VALE/SPS | 3112 | 3112 | 1 | Storm discharge at pumping station | SE1000821129 | 410007 | 421124 | GB104027062642 | Calder from Ryburn Confluence to River Colne | River | 3310 | Middle Calder | 3001 | Aire and Calder | RIVER CALDER | Not Applicable | Not Applicable | Not Applicable | 11:45 | 4 | 43 | 2020 | 99.99 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS00667
YWS00668 | Yorkshire Water | Live | WEST VALE | ELLAND WEST VALE/SPS | 3112 | 3112 | 2 | Storm discharge at pumping station | SE1000821129 | 410007 | 421124 | GB104027062642 | Calder from Ryburn Confluence to River Colne | River | 3310 | Middle Calder | 3001 | Aire and Calder | RIVER CALDER | Not Applicable | Not Applicable | Not Applicable | 81:30 | 30 | 43.25 | 2020 | 99.95 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS00668
YWS00669 | Yorkshire Water | Live | CATTERICK SEWAGE TREATMENT WORKS | CATTERICK VILLAGE/STW | 3132(SS) | 3132 | A2 | Storm tank at WwTW | SE2465097730 | 424650 | 497730 | GB104027069122 | Swale from Clapgate Beck to Bedale Beck | River | 3317 | Middle Swale | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER SWALE | Not Applicable | Not Applicable | Not Applicable | 0:45 | 1 | 17.4 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00669
YWS00670 | Yorkshire Water | Live | TUPTON WWTW | TUPTON/STW | 3139(SS) | 3139(SS) | 2 | Storm tank at WwTW | SK3982066810 | 439820 | 366810 | GB104027057620 | Redleadmill Brook | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | REDLEADMILL BROOK | Not Applicable | Not Applicable | Not Applicable | 767:30 | 82 | 94.6 | 2020 | 99.56 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS00670
YWS00671 | Yorkshire Water | Live | CONEYSTHORPE SEWAGE TREATMENT WORKS | CONEYSTHORPE/STW | 3143(SS) | 3143 | 2 | Inlet SO at WwTW | SE7171071000 | 471710 | 471000 | GB104027063570 | Cram Beck catch (trib of Derwent) | River | 3311 | Middle Derwent Yorkshire | 3027 | Derwent Humber | MILL HILLS BECK | Not Applicable | Not Applicable | Not Applicable | 490:45 | 31 | 22 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00671
YWS00672 | Yorkshire Water | Live | HAIGH HALL CSO | HAIGH HALL/CSO | 3152 | 3152 | A1 | SO on sewer network | SE2814523684 | 428145 | 423684 | GB104027062620 | Chald from Source to River Calder | River | 3268 | Lower Calder | 3001 | Aire and Calder | HEY BECK | Not Applicable | Not Applicable | Not Applicable | 23:15 | 13 | 13.6 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00672
YWS00673 | Yorkshire Water | Live | BEDALE WPC WORKS STORM TANKS | BROOKSIDE CLOSE/CSO | 3159 | 3159 | 1 | SO on sewer network | SE2738087810 | 427195 | 487962 | GB104027068910 | Bedale/Newton/Burton Bk from Rand Bk to R Swale | River | 3317 | Middle Swale | 3088 | Swale, Ure, Nidd and Upper Ouse | BEDALE BK/SWALE | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 2 | 2020 | 95.42 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00673
YWS00674 | Yorkshire Water | Live | RIVADALE VIEW CSO | RIVADALE VIEW/CSO | 3166(SS) | 3166(SS) | A1 | SO on sewer network | SE1170048000 | 411924 | 448068 | GB104027064257 | Wharfe from Barben Beck/River Dibb to Hundwith Beck | River | 3318 | Middle Wharfe and Washburn | 3115 | Wharfe and Lower Ouse | RIVER WHARFE | Not Applicable | Wharfe at Cromwheel, Ilkley | Not Applicable | 107:45 | 40 | 54.2 | 2020 | 100 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00674
YWS00675 | Yorkshire Water | Live | JORDAN CSO | JORDAN/CSO | 3167 | 3167(SS) | A1 | SO on sewer network | SK4079092250 | 440810 | 392245 | GB104027057452 | Don from River Rother to River Dearne | River | 3312 | Middle Don | 3029 | Don and Rother | HOLMES GOIT | Not Applicable | Not Applicable | Not Applicable | 38:15 | 26 | 22.6 | 2020 | 86.28 | Comms failure / issue | Resolved - May | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00675
YWS00676 | Yorkshire Water | Live | WATERSMEET ROAD NO1 CSO | WATERSMEET ROAD/NO 1 CSO | 318 | 318 | A1 | SO on sewer network | SK3266089308 | 432660 | 389308 | GB104027057370 | Loxley from Strines Dyke to River Don | River | 3490 | Upper Don | 3029 | Don and Rother | RIVER LOXLEY | Not Applicable | Not Applicable | Not Applicable | 127:45 | 53 | 48.8 | 2020 | 99.62 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | No investigation activity in reporting period | No improvement action in reporting period | SOAF investigation completed - No work required | YWS00676
YWS00677 | Yorkshire Water | Live | SUMMERBRIDGE CSO | SUMMERBRIDGE/CSO | 32 | 32 | A1 | SO on sewer network | SE2004362333 | 420043 | 462333 | GB104027068295 | Nidd from Ashfoldside Beck to Birstwith | River | 3497 | Upper Nidd | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER NIIDD | Not Applicable | Not Applicable | Not Applicable | 387:15 | 55 | 42.4 | 2020 | 99.99 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation completed | No improvement action in reporting period | SOAF investigation completed - No work required | YWS00677
YWS00678 | Yorkshire Water | Live | BROMPTON ROAD CSO | BROMPTON ROAD/CSO | 3201 | 3201(SS) | A1 | SO on sewer network | SK3802089390 | 438020 | 389390 | GB104027057412 | Don from River Loxley confl to River Don Works | River | 3312 | Middle Don | 3029 | Don and Rother | RIVER DON | Not Applicable | Not Applicable | Not Applicable | 0:30 | 1 | 6.6 | 2020 | 99.88 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00678
YWS00679 | Yorkshire Water | Live | CUCKSTOOL BOTTOM CSO | CUCKSTOOL BOTTOM/CSO | 3205 | 3205(SS) | A1 | SO on sewer network | SE2360108924 | 423601 | 408924 | GB104027063220 | Dearne from Source to Bentley Brook | River | 3125 | Dearne | 3029 | Don and Rother | RIVER DEARNE | Not Applicable | Not Applicable | Not Applicable | 287:00 | 68 | 68 | 2020 | 99.19 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | No investigation activity in reporting period | No improvement action in reporting period | SOAF investigation completed - No work required | YWS00679
YWS00680 | Yorkshire Water | Live | HASLAND HORNS BRIDGE CSO | HASLAND HORNS BRIDGE/CSO | 3209 | 3209(SS) | A1 | SO on sewer network | SK3882070520 | 438820 | 370525 | GB104027057771 | Rother, Spittal Brook to Doe Lea | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | RIVER ROTHER | Not Applicable | Not Applicable | Not Applicable | 95:30 | 28 | 9.8 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00680
YWS00681 | Yorkshire Water | Live | PARK MILL CSO | PARK MILL/CSO | 3212(SS) | 3212(SS) | A1 | SO on sewer network | SE2599911667 | 425999 | 411667 | GB104027063220 | Dearne from Source to Bentley Brook | River | 3125 | Dearne | 3029 | Don and Rother | RIVER DEARNE | Not Applicable | Not Applicable | Not Applicable | 317:15 | 54 | 52.2 | 2020 | 99.99 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | No investigation activity in reporting period | No improvement action in reporting period | SOAF investigation completed - No work required | YWS00681
YWS00682 | Yorkshire Water | Live | CARLISLE STREET CSO | CARLISLE STREET/CSO | 3232 | 3232(SS) | A1 | SO on sewer network | SK4638298985 | 446382 | 398985 | GB104027057452 | Don from River Rother to River Dearne | River | 3312 | Middle Don | 3029 | Don and Rother | SHEFF & SOUTH YORKS NAV CANAL | Not Applicable | Not Applicable | Not Applicable | 104:45 | 43 | 44.8 | 2020 | 90.35 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation completed | No improvement action in reporting period | SOAF investigation completed - No work required | YWS00682
YWS00683 | Yorkshire Water | Live | LITTLE LONDON ROAD CSO | LITTLE LONDON XXX/CSO | 3239 | 3239(SS) | A1 | SO on sewer network | SK3500084800 | 435002 | 384805 | GB104027057750 | Sheaf from Source to River Don | River | 3312 | Middle Don | 3029 | Don and Rother | MEERS BROOK | Not Applicable | Not Applicable | Not Applicable | 100:15 | 43 | 42.6 | 2020 | 96.15 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | No investigation activity in reporting period | No improvement action in reporting period | SOAF investigation completed - No work required | YWS00683
YWS00684 | Yorkshire Water | Live | SSO AT JUNCTION OF ASHGATE ROAD AND | ASHGATE ROAD/CSO | 3243 | 3243(SS) | 1 | SO on sewer network | SK3707071490 | 437070 | 371489 | GB104027057670 | Holme Brook/Linacre Beck | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | HOLME BROOK | Not Applicable | Not Applicable | Not Applicable | 158:00 | 70 | 59.8 | 2020 | 72.02 | Sensor failure / issue | Resolved - Dec | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement completed | SOAF investigation ongoing | YWS00684
YWS00685 | Yorkshire Water | Live | YWS UNKNOWN SITES DEFAULT | STATION ROAD W22M/CSO | 3253 | 3253(SS) | 1 | SO on sewer network | SK3562096860 | 435623 | 396861 | GB104027057440 | Blackburn Brook from Source to River Don | River | 3312 | Middle Don | 3029 | Don and Rother | BLACKBURN BROOK | Not Applicable | Not Applicable | Not Applicable | 24:00 | 10 | 7.4 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00685
YWS00686 | Yorkshire Water | Live | SHEFFIELD ROAD KILMARSH CSO | SHEFF RD KILLAMARSH/CSO | 3268 | 3268(SS) | A1 | SO on sewer network | SK4527781187 | 445277 | 381187 | GB104027057772 | Rother, Doe Lea to Don | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | RIVER ROTHER | Not Applicable | Not Applicable | Not Applicable | 78:30 | 19 | 13.8 | 2020 | 99.97 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00686
YWS00687 | Yorkshire Water | Live | WATH DONCASTER ROAD CSO | WATH DONCASTER ROAD/CSO | 3276 | 3276 | A1 | SO on sewer network | SE4417801044 | 444178 | 401044 | GB104027063173 | Dearne Darfield STW to River Don | River | 3125 | Dearne | 3029 | Don and Rother | BROOK DIKE | Not Applicable | Not Applicable | Not Applicable | 33:15 | 34 | 44.6 | 2020 | 99.98 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS00687
YWS00688 | Yorkshire Water | Live | SWINTON (KILNHURST-HOOTON RD) SPS | HOOTON ROAD/CSO | 3277(SS) | 3277(SS) | 1 | Storm discharge at pumping station | SK4662097400 | 446610 | 397390 | GB104027057452 | Don from River Rother to River Dearne | River | 3312 | Middle Don | 3029 | Don and Rother | RIVER DON | Not Applicable | Not Applicable | Not Applicable | 32:45 | 17 | 32.2 | 2020 | 69.15 | Comms failure / issue | Resolved - Apr | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00688
YWS00689 | Yorkshire Water | Live | WOOD STREET DEWSBURY CSO | WOOD STREET DEWSBURY/CSO | 3281 | 3281(SS) | A1 | SO on sewer network | SE2459021990 | 424605 | 421998 | GB104027062670 | Batley Beck from Source to River Calder | River | 3268 | Lower Calder | 3001 | Aire and Calder | DEWSBURY BECK | Not Applicable | Not Applicable | Not Applicable | 0:15 | 1 | 0.6 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00689
YWS00690 | Yorkshire Water | Live | KEIGHLEY ROAD 76 CSO | KEIGHLEY ROAD 76/CSO | 3282 | 3282(SS) | A1 | SO on sewer network | SE0387545136 | 403875 | 445136 | GB104027063033 | Aire (Eshton Beck to R Worth) | River | 3484 | Upper Aire | 3001 | Aire and Calder | RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 250:45 | 63 | 74.2 | 2020 | 99.47 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00690
YWS00691 | Yorkshire Water | Live | BRADGATE LANE NO 2 CSO | BRADGATE LANE/NO 2 CSO | 3284 | 3284(SS) | A1 | SO on sewer network | SK4089293270 | 440892 | 393270 | GB104027057452 | Don from River Rother to River Dearne | River | 3312 | Middle Don | 3029 | Don and Rother | RIVER MOSS | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 1.6 | 2020 | 95.65 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00691
YWS00692 | Yorkshire Water | Live | SHEAF BANK COMBINED SEWER OVERFLOW | SHEAF BANK/CSO | 3285 | 3285(SS) | A1 | SO on sewer network | SK3527085190 | 435270 | 385193 | GB104027057750 | Sheaf from Source to River Don | River | 3312 | Middle Don | 3029 | Don and Rother | RIVER SHEAF | Not Applicable | Not Applicable | Not Applicable | 82:45 | 40 | 35.6 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00692
YWS00693 | Yorkshire Water | Live | MANSE LANE 57 CSO | MANSE LANE 57/CSO | 3286(SS) | 3286(SS) | A1 | SO on sewer network | SE3647556545 | 436475 | 456545 | GB104027068298 | Nidd from Low Bridge on Briggate (Knaresborough) to Crimple Beck | River | 3308 | Middle and Lower Nidd | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER NIDD | Not Applicable | Not Applicable | Not Applicable | 236:45 | 56 | 26.4 | 2020 | 96.4 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00693
YWS00694 | Yorkshire Water | Live | STADIUM WAY CSO | STADIUM WAY/CSO | 3295 | 3295(SS) | A1 | SO on sewer network | SK4350894264 | 443508 | 394264 | GB104027057452 | Don from River Rother to River Dearne | River | 3312 | Middle Don | 3029 | Don and Rother | PARISH DYKE (CULVERTED) | Not Applicable | Not Applicable | Not Applicable | 23:30 | 10 | 4.75 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00694
YWS00695 | Yorkshire Water | Live | STOCKSBRIDGE CSO | STOCKSBRIDGE/CSO | 3300(SS) | 3300(SS) | 1 | SO on sewer network | SK2905097790 | 429053 | 397798 | GB104027057411 | Don from Little Don to River Loxley confluence | River | 3490 | Upper Don | 3029 | Don and Rother | RIVER DON | Not Applicable | Not Applicable | Not Applicable | 80:30 | 28 | 35.4 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00695
YWS00696 | Yorkshire Water | Live | THE MALTINGS CSO | THE MALTINGS/CSO | 3317 | 3317(SS) | A1 | SO on sewer network | SK4250992197 | 442509 | 392197 | GB104027057772 | Rother, Doe Lea to Don | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | RIVER ROTHER | Not Applicable | Not Applicable | Not Applicable | 0:45 | 1 | 2.75 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00696
YWS00697 | Yorkshire Water | Live | GRANGE ROAD 7 CSO | GRANGE ROAD 7/CSO | 3319 | 3319(SS) | A1 | SO on sewer network | SE0739142246 | 407391 | 442246 | GB104027063033 | Aire (Eshton Beck to R Worth) | River | 3484 | Upper Aire | 3001 | Aire and Calder | RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 39:30 | 28 | 37.2 | 2020 | 99.92 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00697
YWS00698 | Yorkshire Water | Live | WARM LANE, YEADON CSO | WARM LANE YEADON/CSO | 3326 | 3326(SS) | 1 | SO on sewer network | SE1980040100 | 419798 | 440181 | GB104027062910 | Gill Beck Guisley from Source to River Aire | River | 3265 | Lower Aire | 3001 | Aire and Calder | YEADON GILL | Not Applicable | Not Applicable | Not Applicable | 53:00 | 23 | 26 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00698
YWS00699 | Yorkshire Water | Live | BOLTON ON DEARNE STW | BOLTON ON DEARNE/STW/3XDWF OVERFLOW | 3331 | 3331 | A2 | Storm tank at WwTW | SE4584902021 | 445849 | 402021 | GB104027063173 | Dearne Darfield STW to River Don | River | 3125 | Dearne | 3029 | Don and Rother | RIVER DEARNE | Not Applicable | Not Applicable | Not Applicable | 425:15 | 53 | 53.4 | 2020 | 96.58 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00699
YWS00700 | Yorkshire Water | Live | BOLTON ON DEARNE STW | BOLTON ON DEARNE/STW/6XDWF OVERFLOW | 3331 | 3331 | A3 | Inlet SO at WwTW | SE4584902021 | 445849 | 402021 | GB104027063173 | Dearne Darfield STW to River Don | River | 3125 | Dearne | 3029 | Don and Rother | RIVER DEARNE | Not Applicable | Not Applicable | Not Applicable | 12:00 | 11 | 12.4 | 2020 | 99.98 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00700
YWS00701 | Yorkshire Water | Live | THORNE STW | THORNE/STW | 3332 | 3332(SS) | A2 | Storm tank at WwTW | SE6746014680 | 467460 | 414680 | GB104027064243 | Don from Mill Dyke to River Ouse | River | 3272 | Lower Don | 3029 | Don and Rother | RIVER DON (TIDAL) | Not Applicable | Not Applicable | Not Applicable | 192:15 | 31 | 40 | 2020 | 91.84 |  |  | High spill threshold not met | High spill threshold not met | UWWTR investigation ongoing, Operational investigation ongoing | Operational improvement ongoing | SOAF investigation ongoing | YWS00701
YWS00702 | Yorkshire Water | Live | WOODHOUSE MILL WWTW | WOODHOUSE MILL/NO 2 STW | 3334(SS) | 3334(SS) | 2 | Storm tank at WwTW | SK4336086240 | 443360 | 386240 | GB104027057772 | Rother, Doe Lea to Don | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | RIVER ROTHER | Not Applicable | Not Applicable | Not Applicable | 306:30 | 45 | 51.6 | 2020 | 100 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00702
YWS00703 | Yorkshire Water | Live | WOODHOUSE MILL WWTW | WOODHOUSE MILL/NO 2 STW | 3334(SS) | 3334(SS) | 3 | Inlet SO at WwTW | SK4319085820 | 443190 | 385820 | GB104027057772 | Rother, Doe Lea to Don | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | RIVER ROTHER | Not Applicable | Not Applicable | Not Applicable | 233:45 | 23 | 22.4 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00703
YWS00704 | Yorkshire Water | Live | DEWSBURY MOOR CSO | DEWSBURY MOOR/CSO | 3342 | 3342(SS) | A1 | SO on sewer network | SE2232621626 | 422326 | 421626 | GB104027062710 | Spen Beck from Source to River Calder | River | 3268 | Lower Calder | 3001 | Aire and Calder | RIVER SPEN (VIA PUBLIC SEWER) | Not Applicable | Not Applicable | Not Applicable | 86:30 | 39 | 39.4 | 2020 | 98.07 |  |  | High spill threshold not met | High spill threshold not met | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00704
YWS00705 | Yorkshire Water | Live | UPPER DUNSFORTH CSO | UPPER DUNSFORTH/CSO | 3349(SS) | 3349(SS) | A1 | SO on sewer network | SE4467063464 | 444670 | 463464 | GB104027069592 | Ouse from River Ure to River Nidd | River | 3309 | Middle and Lower Ure | 3088 | Swale, Ure, Nidd and Upper Ouse | CAULKHILL BECK | Not Applicable | Not Applicable | Not Applicable | 0:30 | 1 | 1.4 | 2020 | 86.8 | Comms failure / issue | Resolved - Feb | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00705
YWS00706 | Yorkshire Water | Live | SSO AT GREAT OUSEBURN(EAST) | GREAT OUSEBURN EAST/CSO | 3352(SS) | 3352(SS) | A1 | SO on sewer network | SE4480061400 | 444710 | 461420 | GB104027063800 | Ouse from Source to River Ure | River | 3309 | Middle and Lower Ure | 3088 | Swale, Ure, Nidd and Upper Ouse | TRIB OUSE GILL BECK | Not Applicable | Not Applicable | Not Applicable | 262:15 | 75 | 63.25 | 2020 | 85.81 | Comms failure / issue | Resolved - Nov | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement ongoing | SOAF investigation ongoing | YWS00706
YWS00707 | Yorkshire Water | Live | DALTON GREEN LANE CSO | DALTON GREEN LANE/CSO | 336 | 336 | A1 | SO on sewer network | SE1708017320 | 417082 | 417324 | GB104027063340 | Fenay beck from Source to River Colne | River | 3097 | Colne and Holme | 3001 | Aire and Calder | CALDER | Not Applicable | Not Applicable | Not Applicable | 90:30 | 51 | 33 | 2020 | 99.97 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00707
YWS00708 | Yorkshire Water | Live | CLOCK TOWER CSO | CLOCK TOWER/CSO | 3368(SS) | 3368(SS) | A1 | SO on sewer network | SE3196571946 | 431965 | 471946 | GB104027069461 | Ure from Thornton Steward Beck to River Skell | River | 3309 | Middle and Lower Ure | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER URE | Not Applicable | Not Applicable | Not Applicable | 137:30 | 35 | 69.2 | 2020 | 41.21 | Sensor failure / issue | Scheduled | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement ongoing | SOAF investigation ongoing | YWS00708
YWS00709 | Yorkshire Water | Live | FOUNDRY LANE CSO | FOUNDRY LANE/NO 2 CSO | 337 | 337 | 1 | SO on sewer network | SE3390035010 | 433906 | 435019 | GB104027062880 | Wyke Beck from Source to River Aire | River | 3265 | Lower Aire | 3001 | Aire and Calder | WYKE BECK | Not Applicable | Not Applicable | Not Applicable | 166:00 | 44 | 42.4 | 2020 | 100 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00709
YWS00710 | Yorkshire Water | Live | UNION STREET CSO | UNION STREET/CSO | 3374 | 3374(SS) | A1 | SO on sewer network | SK4176092810 | 441760 | 392810 | GB104027057452 | Don from River Rother to River Dearne | River | 3312 | Middle Don | 3029 | Don and Rother | RIVER MAS CULVERTED | Not Applicable | Not Applicable | Not Applicable | 47:00 | 33 | 35.6 | 2020 | 99.97 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00710
YWS00711 | Yorkshire Water | Live | MASBROUGH STREET CSO | MASBROUGH STREET/CSO | 3375 | 3375(SS) | A1 | SO on sewer network | SK4206092600 | 442066 | 392590 | GB104027057452 | Don from River Rother to River Dearne | River | 3312 | Middle Don | 3029 | Don and Rother | HOLMES TAIL GOIT | Not Applicable | Not Applicable | Not Applicable | 66:15 | 35 | 7.2 | 2020 | 98.19 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00711
YWS00712 | Yorkshire Water | Live | FOSTERS GARAGE SPS | FOSTERS GARAGE/CSO | 3384 | 3384(SS) | A2 | Storm discharge at pumping station | SK4645095280 | 446450 | 395280 | GB104027057452 | Don from River Rother to River Dearne | River | 3312 | Middle Don | 3029 | Don and Rother | TRIBUTARY OF THE RIVER DON | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 5 | 2020 | 11.89 | Sensor failure / issue | Resolved - Nov | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00712
YWS00713 | Yorkshire Water | Live | BRINSWORTH SEWAGE PUMPING STATION | BRINSWORTH/CSO | 3390 | 3390 | A1 | SO on sewer network | SK4231090400 | 442310 | 390400 | GB104027057772 | Rother, Doe Lea to Don | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | TRIB OF RIVER ROTHER | Not Applicable | Not Applicable | Not Applicable | 167:45 | 54 | 51 | 2020 | 99.99 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00713
YWS00714 | Yorkshire Water | Live | BEVERLEY WORKS CSO | BEVERLEY WORKS/CSO | 3392 | 3392(SS) | A1 | SO on sewer network | TA0582139337 | 505821 | 439337 | GB104026067212 | Hull from Arram Beck to Humber | River | 3274 | Lower Hull | 3039 | Hull and East Riding | RIVER HULL TIDAL | Not Applicable | Not Applicable | Not Applicable | 0:30 | 1 | 0.8 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00714
YWS00715 | Yorkshire Water | Live | SHOW GROUND CSO | SHOW GROUND/CSO | 3422(SS) | 3422(SS) | A1 | SO on sewer network | SE1577465498 | 415774 | 465498 | GB104027068295 | Nidd from Ashfoldside Beck to Birstwith | River | 3497 | Upper Nidd | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER NIDD | Not Applicable | Not Applicable | Not Applicable | 97:30 | 22 | 19.2 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00715
YWS00716 | Yorkshire Water | Live | GLASSHOUSES BRIDGE CSO | GLASSHOUSES BRIDGE/CSO | 3423(SS) | 3423(SS) | A1 | SO on sewer network | SE1714064360 | 417140 | 464360 | GB104027068295 | Nidd from Ashfoldside Beck to Birstwith | River | 3497 | Upper Nidd | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER NIDD | Not Applicable | Not Applicable | Not Applicable | 76:15 | 28 | 44 | 2020 | 99.97 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation completed | No improvement action in reporting period | SOAF investigation completed - No work required | YWS00716
YWS00717 | Yorkshire Water | Live | BURNABY CRESCENT CSO | BURNABY CRESCENT/CSO | 3430 | 3430(SS) | A1 | SO on sewer network | SK3408489449 | 434084 | 389449 | GB104027057370 | Loxley from Strines Dyke to River Don | River | 3490 | Upper Don | 3029 | Don and Rother | RIVER DON | Not Applicable | Not Applicable | Not Applicable | 3:00 | 8 | 8.8 | 2020 | 99.72 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00717
YWS00718 | Yorkshire Water | Live | BURGOYNE ROAD CSO | BURGOYNE ROAD/CSO | 3431 | 3431(SS) | A1 | SO on sewer network | SK3422988852 | 434229 | 388852 | GB104027057412 | Don from River Loxley confl to River Don Works | River | 3312 | Middle Don | 3029 | Don and Rother | RIVER DON | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0 | 2020 | 97.47 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00718
YWS00719 | Yorkshire Water | Live | WESTBURY PLACE CSO | WESTBURY PLACE/CSO | 3435 | 3435(SS) | 1 | SO on sewer network | SE3188031360 | 431880 | 430598 | GB104027063032 | Aire from Gill Beck (Baildon) to River Calder | River | 3265 | Lower Aire | 3001 | Aire and Calder | BALM BECK | Not Applicable | Not Applicable | Not Applicable | 0:15 | 1 | 55.25 | 2020 | 99.76 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS00719
YWS00720 | Yorkshire Water | Live | MEADOW CRESCENT CSO | MEADOWS CRESCENT/CSO | 3436 | 3436(SS) | A1 | SO on sewer network | SE3689511481 | 436895 | 411481 | GB104027063230 | Cudworth Dyke from Source to River Dearne | River | 3125 | Dearne | 3029 | Don and Rother | TRIBUTARY OF POOLS DIKE | Not Applicable | Not Applicable | Not Applicable | 22:30 | 18 | 15 | 2020 | 99.84 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00720
YWS00722 | Yorkshire Water | Live | KING STREET CSO | KING STREET/CSO | 3482 | 3482 | A1 | SO on sewer network | SE0984025247 | 409840 | 425247 | GB104027062780 | Hebble Brook from Source to River Calder | River | 3310 | Middle Calder | 3001 | Aire and Calder | HEBBLE BROOK | Not Applicable | Not Applicable | Not Applicable | 9:15 | 13 | 15.6 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00722
YWS00723 | Yorkshire Water | Live | SKELMANTHORPE CSO | SKELMANTHORPE/CSO | 3494 | 3494(SS) | A1 | SO on sewer network | SE2364211161 | 423642 | 411161 | GB104027063220 | Dearne from Source to Bentley Brook | River | 3125 | Dearne | 3029 | Don and Rother | TRIB OF PARK GATE DIKE | Not Applicable | Not Applicable | Not Applicable | 187:15 | 33 | 28.2 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00723
YWS00724 | Yorkshire Water | Live | GHYLL ROYD CSO | GHYLL ROYD/CSO | 3495 | 3495(SS) | A1 | SO on sewer network | SE1953041320 | 419530 | 441320 | GB104027062910 | Gill Beck Guisley from Source to River Aire | River | 3265 | Lower Aire | 3001 | Aire and Calder | NUNROYD BECK | Not Applicable | Not Applicable | Not Applicable | 46:15 | 28 | 29 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00724
YWS00725 | Yorkshire Water | Live | SSO AT OAKFIELD AVENUE | OAKFIELD AVENUE/CSO | 3509 | 3509(SS) | 1 | SO on sewer network | SK3584070300 | 435850 | 370280 | GB104027057660 | Hipper from Source to River Rother | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | RIVER HIPPER | Not Applicable | Not Applicable | Not Applicable | 264:30 | 75 | 70.8 | 2020 | 97.52 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement ongoing | SOAF investigation ongoing | YWS00725
YWS00726 | Yorkshire Water | Live | ALEXANDER STREET PUMPING STATION | ALEXANDER STREET/CSO | 3512 | 3512(SS) | 1 | Storm discharge at pumping station | SE5743006180 | 457430 | 406180 | GB104027057541 | Bentley Mill Stream | River | 3272 | Lower Don | 3029 | Don and Rother | BENTLEY MILL STREAM | Not Applicable | Not Applicable | Not Applicable | 9:00 | 9 | 1.8 | 2020 | 99.97 |  |  | High spill threshold not met | High spill threshold not met | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00726
YWS00728 | Yorkshire Water | Live | SCARCROFT CSO | SCARCROFT/CSO | 3528(SS) | 3528(SS) | A1 | SO on sewer network | SE3660042100 | 436703 | 442030 | GB104027063970 | Collingham Bk Catchment (trib of Wharfe) | River | 3318 | Middle Wharfe and Washburn | 3115 | Wharfe and Lower Ouse | SYKE BECK | Not Applicable | Not Applicable | Not Applicable | 99:00 | 30 | 19.2 | 2020 | 99.97 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00728
YWS00729 | Yorkshire Water | Live | HIPPER STREET SOUTH CSO | HIPPER STREET SOUTH/CSO | 3533 | 3533(SS) | A1 | SO on sewer network | SK3831070755 | 438310 | 370755 | GB104027057660 | Hipper from Source to River Rother | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | RIVER HIPPER | Not Applicable | Not Applicable | Not Applicable | 0:30 | 1 | 1 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00729
YWS00730 | Yorkshire Water | Live | SSO AT STAVELEY | STAVELEY QUARRY/NO 2 CSO | 3539(SS) | 3539(SS) | 1 | SO on sewer network | SE3620063200 | 436262 | 463202 | GB104027064100 | Tutt Catchment (Trib of Ure) | River | 3309 | Middle and Lower Ure | 3088 | Swale, Ure, Nidd and Upper Ouse | TANNER BECK | Not Applicable | Not Applicable | Not Applicable | 10:00 | 1 | 21.8 | 2020 | 10.65 | Comms failure / issue | Resolved - January after reporting year | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00730
YWS00731 | Yorkshire Water | Live | THORPE HESLEY CSO | THORPE HESLEY/CSO | 3541 | 3541(SS) | A1 | SO on sewer network | SK3816196204 | 438161 | 396204 | GB104027057420 | Greasbrough Dike from Source to River Don | River | 3312 | Middle Don | 3029 | Don and Rother | THORPE DYKE | Not Applicable | Not Applicable | Not Applicable | 83:30 | 43 | 36.2 | 2020 | 99.97 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | SOAF investigation completed - No work required | YWS00731
YWS00732 | Yorkshire Water | Live | MILLSHAW NO. 2 CSO | MILLSHAW/NO 2 CSO | 3544 | 3544 | 1 | SO on sewer network | SE2804030022 | 428045 | 430030 | GB104027062750 | Milshaw Beck from Source to Low/Wortley/Pudsey Bks | River | 3265 | Lower Aire | 3001 | Aire and Calder | MILL SHAW BECK | Not Applicable | Not Applicable | Not Applicable | 41:15 | 24 | 30.6 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00732
YWS00734 | Yorkshire Water | Live | NEWLAY WOOD CRESCENT CSO | NEWLAY WOOD CRESCENT/CSO | 3560 | 3560(SS) | A1 | SO on sewer network | SE2417736993 | 424177 | 436993 | GB104027063032 | Aire from Gill Beck (Baildon) to River Calder | River | 3265 | Lower Aire | 3001 | Aire and Calder | KIRKSTALL FORGE GOIT VIA SWS | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0 | 2020 | 98.85 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00734
YWS00735 | Yorkshire Water | Live | WRENTHORPE CSO | WRENTHORPE/CSO | 3594 | 3594(SS) | A1 | SO on sewer network | SE3192621788 | 431926 | 421788 | GB104027062620 | Chald from Source to River Calder | River | 3268 | Lower Calder | 3001 | Aire and Calder | BALNE BECK | Not Applicable | Not Applicable | Not Applicable | 30:00 | 10 | 11.8 | 2020 | 99.82 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00735
YWS00736 | Yorkshire Water | Live | WEST PARK RING ROAD CSO | WEST PARK RING ROAD/CSO | 36 | 36 | A1 | SO on sewer network | SE2537437881 | 425374 | 437881 | GB104027062920 | Carlton Beck from Source to River Aire | River | 3265 | Lower Aire | 3001 | Aire and Calder | CULVERT TRIB OF OIL MILL BECK | Not Applicable | Not Applicable | Not Applicable | 17:30 | 19 | 31 | 2020 | 99.84 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00736
YWS00737 | Yorkshire Water | Live | SSO AT NORTON PUMPING STATION | NORTON STATION RD/CSO | 3600 | 3600(SS) | 1 | Storm discharge at pumping station | SE5530015300 | 455300 | 415200 | GB104027063360 | Went from Hoyle Mill Stream to Blowell Drain | River | 3272 | Lower Don | 3029 | Don and Rother | TRIB OF SWAN SIKE DRAIN | Not Applicable | Not Applicable | Not Applicable | 680:15 | 57 | 67.6 | 2020 | 99.99 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement ongoing | SOAF investigation ongoing | YWS00737
YWS00738 | Yorkshire Water | Live | HIGH GREAVE NO 2 CSO | HIGH GREAVE/NO 2 CSO | 361 | 361 | A1 | SO on sewer network | SK3626093252 | 436260 | 393252 | GB104027057440 | Blackburn Brook from Source to River Don | River | 3312 | Middle Don | 3029 | Don and Rother | HARTLEY BROOK DIKE | Not Applicable | Not Applicable | Not Applicable | 36:30 | 16 | 10 | 2020 | 99.85 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00738
YWS00739 | Yorkshire Water | Live | FURLONG POND NO 2 CSO | FURLONG POND/NO 2 CSO | 3640 | 3640(SS) | A1 | SO on sewer network | SE4616103358 | 446161 | 403358 | GB104027063173 | Dearne Darfield STW to River Don | River | 3125 | Dearne | 3029 | Don and Rother | FAR MOOR DYKE | Not Applicable | Not Applicable | Not Applicable | 41:30 | 19 | 21.8 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00739
YWS00740 | Yorkshire Water | Live | SSO AT FARROW MILL LANE, HALIFAX | FARRAR MILL LANE/CSO | 3654 | 3654(SS) | 1 | SO on sewer network | SE0990023200 | 409974 | 423213 | GB104027062780 | Hebble Brook from Source to River Calder | River | 3310 | Middle Calder | 3001 | Aire and Calder | HEBBLE BROOK | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00740
YWS00741 | Yorkshire Water | Live | BRUNSWICK PRIMARY SCHOOL CSO | BRUNSWICK SCHOOL/CSO | 3655 | 3655(SS) | A1 | SO on sewer network | SK4244885418 | 442448 | 385418 | GB104027057772 | Rother, Doe Lea to Don | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | SHIRTCLIFF BROOK | Not Applicable | Not Applicable | Not Applicable | 2:45 | 6 | 8.4 | 2020 | 99.88 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00741
YWS00742 | Yorkshire Water | Live | ARMITAGE FOLD CSO | ARMITAGE FOLD/CSO | 3658 | 3658(SS) | A1 | SO on sewer network | SE1336213819 | 413362 | 413819 | GB104027063301 | Holme from New Mill Dike to R Colne | River | 3097 | Colne and Holme | 3001 | Aire and Calder | RIVER HOLME | Not Applicable | Not Applicable | Not Applicable | 88:30 | 57 | 64 | 2020 | 98.56 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | No investigation activity in reporting period | No improvement action in reporting period | SOAF investigation completed - No work required | YWS00742
YWS00743 | Yorkshire Water | Live | STOCKWELL HILL CSO | STOCKWELL HILL/CSO | 3659 | 3659(SS) | A1 | SO on sewer network | SE1360013700 | 413573 | 413662 | GB104027063301 | Holme from New Mill Dike to R Colne | River | 3097 | Colne and Holme | 3001 | Aire and Calder | RIVER HOLME | Not Applicable | Not Applicable | Not Applicable | 110:00 | 40 | 49.2 | 2020 | 100 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | No investigation activity in reporting period | No improvement action in reporting period | SOAF investigation completed - No work required | YWS00743
YWS00744 | Yorkshire Water | Live | GREASBROUGH CSO | GREASBROUGH/CSO | 3670 | 3670(SS) | A1 | SO on sewer network | SK4228495559 | 442284 | 395559 | GB104027057420 | Greasbrough Dike from Source to River Don | River | 3312 | Middle Don | 3029 | Don and Rother | TRIBUTARY OF OCHRE DYKE | Not Applicable | Not Applicable | Not Applicable | 122:00 | 53 | 62 | 2020 | 100 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | No investigation activity in reporting period | No improvement action in reporting period | SOAF investigation completed - No work required | YWS00744
YWS00745 | Yorkshire Water | Live | BARNSLEY MFI CSO | BARNSLEY MFI/CSO | 3671 | 3671(SS) | A1 | SO on sewer network | SE3510007200 | 435100 | 407200 | GB104027063171 | Dearne from Cawthorne Dyke to Lundwood STW | River | 3125 | Dearne | 3029 | Don and Rother | RIVER DEARNE | Not Applicable | Not Applicable | Not Applicable | 28:00 | 14 | 15 | 2020 | 98.41 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00745
YWS00746 | Yorkshire Water | Live | ECCLESALL ROAD CSO | ECCLESALL ROAD/CSO | 3675 | 3675(SS) | A1 | SO on sewer network | SK3446586256 | 434465 | 386256 | GB104027057760 | Porter from Source to River Sheaf | River | 3312 | Middle Don | 3029 | Don and Rother | RIVER PORTER | Not Applicable | Not Applicable | Not Applicable | 8:00 | 7 | 18.8 | 2020 | 21.21 | Sensor failure / issue | Resolved - Oct | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00746
YWS00747 | Yorkshire Water | Live | LAKE SIDE LANE SSO | KIRKHEATON TANK/CSO | 3681 | 3681(SS) | 1 | SO on sewer network | SE1815017250 | 418153 | 417262 | GB104027063340 | Fenay beck from Source to River Colne | River | 3097 | Colne and Holme | 3001 | Aire and Calder | OXFIELD BECK | Not Applicable | Not Applicable | Not Applicable | 43:15 | 9 | 9.2 | 2020 | 99.95 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00747
YWS00748 | Yorkshire Water | Live | SHIBDEN PARK CSO | SHIBDEN PARK/CSO | 3682 | 3682(SS) | A1 | SO on sewer network | SE1089626040 | 410896 | 426040 | GB104027062720 | Red Beck, Source to Calder and Hebble Navigation | River | 3310 | Middle Calder | 3001 | Aire and Calder | RED BECK | Not Applicable | Not Applicable | Not Applicable | 2:30 | 4 | 4.2 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00748
YWS00749 | Yorkshire Water | Live | GLAPWELL BACK LANE CSO | GLAPWELL BACK LANE/CSO | 3697 | 3697(SS) | A1 | SO on sewer network | SK4768066120 | 447683 | 366120 | GB104027057290 | Doe Lea from Source to Hawke Brook | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | TRIB OF STOCKLEY BROOK | Not Applicable | Not Applicable | Not Applicable | 5:45 | 5 | 4.8 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00749
YWS00750 | Yorkshire Water | Live | GREENHILL PARK PAVILLION CSO | GREENHILL PARK PAV/CSO | 3714 | 3714(SS) | A1 | SO on sewer network | SK3442080320 | 434422 | 380320 | GB104027057710 | Drone/Whitting from Source to River Rother | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | TRIBUTARY OF RIVER DRONE | Not Applicable | Not Applicable | Not Applicable | 16:00 | 7 | 3.2 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00750
YWS00751 | Yorkshire Water | Live | GREENHILL PARK CSO | GREENHILL PARK/CSO | 3715 | 3715(SS) | A1 | SO on sewer network | SK3502080340 | 435028 | 380341 | GB104027057710 | Drone/Whitting from Source to River Rother | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | TRIBUTARY OF RIVER DRONE | Not Applicable | Not Applicable | Not Applicable | 10:00 | 4 | 2.6 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00751
YWS00752 | Yorkshire Water | Live | WORTLEY EAST WWTW | WORTLEY EAST/STW | 3717(SS) | 3717(SS) | A2 | Inlet SO at WwTW | SK3130099700 | 431369 | 399794 | GB104027057480 | Rockley Dike from Source to River Dove | River | 3125 | Dearne | 3029 | Don and Rother | HIGHWOOD DIKE | Not Applicable | Not Applicable | Not Applicable | 183:00 | 66 | 76.2 | 2020 | 99.55 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00752
YWS00753 | Yorkshire Water | Live | DOCK LANE CSO | DOCK LANE/CSO | 3720 | 3720(SS) | A1 | SO on sewer network | SE1516037580 | 415160 | 437590 | GB104027062862 | Bradford Beck (Clayton Bk to R Aire) | River | 3307 | Middle Aire | 3001 | Aire and Calder | BRADFORD BECK | Not Applicable | Not Applicable | Not Applicable | 205:00 | 77 | 77 | 2020 | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | No investigation activity in reporting period | No improvement action in reporting period | SOAF investigation completed - No work required | YWS00753
YWS00754 | Yorkshire Water | Live | THURNSCOE CSO | THURNSCOE/CSO | 3728 | 3728(SS) | A1 | SO on sewer network | SE4462605335 | 444626 | 405335 | GB104027057550 | Ings/Carr/Thurnscoe Dikes from Source to Dearne | River | 3125 | Dearne | 3029 | Don and Rother | THURNSCOE DIKE | Not Applicable | Not Applicable | Not Applicable | 227:00 | 45 | 65.6 | 2020 | 100 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | Operational investigation completed | Operational improvement ongoing | SOAF investigation completed - No work required | YWS00754
YWS00755 | Yorkshire Water | Live | BURNTWOOD CLOSE CSO | BURNTWOOD CLOSE/CSO | 3729 | 3729(SS) | A1 | SO on sewer network | SE4503204820 | 445032 | 404820 | GB104027057550 | Ings/Carr/Thurnscoe Dikes from Source to Dearne | River | 3125 | Dearne | 3029 | Don and Rother | TRIBUTARY OF THURNSCOE DIKE | Not Applicable | Not Applicable | Not Applicable | 87:15 | 36 | 32.8 | 2020 | 99.95 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00755
YWS00756 | Yorkshire Water | Live | DALTON BROOK CSO | DALTON BROOK/CSO | 3742 | 3742(SS) | A1 | SO on sewer network | SK4559094480 | 445590 | 394480 | GB104027057452 | Don from River Rother to River Dearne | River | 3312 | Middle Don | 3029 | Don and Rother | DALTON BROOK | Not Applicable | Not Applicable | Not Applicable | 226:15 | 39 | 37.4 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00756
YWS00757 | Yorkshire Water | Live | EARBY SEWAGE TREATMENT WORKS | EARBY/STW | 3761(SS) | 3761 | A2 | Inlet SO at WwTW | SD9095047240 | 390959 | 447248 | GB104027062980 | Earby Beck from source to River Aire | River | 3484 | Upper Aire | 3001 | Aire and Calder | EARBY BECK | Not Applicable | Not Applicable | Not Applicable | 260:15 | 83 | 72 | 2020 | 100 |  |  | Performance - Infiltration | Performance - Infiltration | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS00757
YWS00758 | Yorkshire Water | Live | EARBY SEWAGE TREATMENT WORKS | EARBY/STW | 3761(SS) | 3761 | A3 | Inlet SO at WwTW | SD9095047240 | 390959 | 447248 | GB104027062980 | Earby Beck from source to River Aire | River | 3484 | Upper Aire | 3001 | Aire and Calder | EARBY BECK | Not Applicable | Not Applicable | Not Applicable | 458:00 | 95 | 106 | 2020 | 100 |  |  | Performance - Infiltration | Performance - Infiltration | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS00758
YWS00759 | Yorkshire Water | Live | RAWMARSH ROAD SPS | RAWMARSH ROAD/CSO | 3777 | 3777(SS) | 1 | Storm discharge at pumping station | SK4311093760 | 443110 | 393760 | GB104027057452 | Don from River Rother to River Dearne | River | 3312 | Middle Don | 3029 | Don and Rother | RIVER DON | Not Applicable | Not Applicable | Not Applicable | 21:30 | 17 | 24.6 | 2020 | 99.93 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00759
YWS00760 | Yorkshire Water | Live | LITTLEMOOR NEWBOLD CSO | LITTLEMOOR NEWBOLD/CSO | 3778 | 3778(SS) | A1 | SO on sewer network | SK3740873988 | 437408 | 373988 | GB104027057710 | Drone/Whitting from Source to River Rother | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | RIDDING BROOK CLVRT VIA SWS | Not Applicable | Not Applicable | Not Applicable | 117:00 | 52 | 55.2 | 2020 | 99.99 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS00760
YWS00761 | Yorkshire Water | Live | SEDBURGH ROAD CSO | SEDBURGH ROAD/CSO | 3779 | 3779(SS) | 1 | SO on sewer network | SE0974024240 | 409744 | 424242 | GB104027062780 | Hebble Brook from Source to River Calder | River | 3310 | Middle Calder | 3001 | Aire and Calder | HEBBLE BROOK | Not Applicable | Not Applicable | Not Applicable | 0:45 | 2 | 26.6 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00761
YWS00762 | Yorkshire Water | Live | LEBBERSTON BALANCING TANK | LEBBERSTON TANK/CSO | 3791(SS) | 3791(SS) | A1 | SO on sewer network | TA0820082800 | 508157 | 482685 | GB104027067811 | Hertford from Source to River Derwent | River | 3489 | Upper Derwent Yorkshire | 3027 | Derwent Humber | TRIB RIVER HERTFORD | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 37.2 | 2020 | 99.95 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00762
YWS00763 | Yorkshire Water | Live | GRISTHORPE TANK CSO | GRISTHORPE TANK/CSO | 3792 | 3792(SS) | A1 | SO on sewer network | TA0889781885 | 508897 | 481885 | GB104027067811 | Hertford from Source to River Derwent | River | 3489 | Upper Derwent Yorkshire | 3027 | Derwent Humber | TRIB OF RIVER HERTFORD | Not Applicable | Not Applicable | Not Applicable | 62:00 | 10 | 8.4 | 2020 | 86.34 | Comms failure / issue | Resolved - Jun | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00763
YWS00764 | Yorkshire Water | Live | WOODHALL WAY | BEVERLEY WOODHALL WAY/CSO | 3793(SS) | 3793(SS) | 1 | SO on sewer network | TA0295040550 | 502700 | 441200 | GB104026066841 | High Hunsley to Arram Area | River | 3274 | Lower Hull | 3039 | Hull and East Riding | UN-NAMED TRIB OF SISTER BECK | Not Applicable | Not Applicable | Not Applicable | 207:30 | 23 | 11 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00764
YWS00765 | Yorkshire Water | Live | WOODHALL WAY | BURNEY CLOSE/CSO | 3793(SS) | 3793(SS) | 2 | SO on sewer network | TA0295040550 | 502700 | 441200 | GB104026066841 | High Hunsley to Arram Area | River | 3274 | Lower Hull | 3039 | Hull and East Riding | UN-NAMED TRIB OF SISTER BECK | Not Applicable | Not Applicable | Not Applicable | 132:15 | 15 | 9.4 | 2020 | 99.94 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00765
YWS00766 | Yorkshire Water | Live | THORNTON ROAD 209 CSO | THORNTON ROAD 209/CSO | 3801 | 3801(SS) | A1 | SO on sewer network | SE1167832964 | 411678 | 432964 | GB104027062861 | Clayton Beck (Source to Bradford Bk) | River | 3307 | Middle Aire | 3001 | Aire and Calder | PITTY BECK | Not Applicable | Not Applicable | Not Applicable | 357:45 | 88 | 83.2 | 2020 | 100 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS00766
YWS00767 | Yorkshire Water | Live | O/S 53 STATION ROAD | PANNAL BRIDGE/CSO | 3803(SS) | 3803(SS) | A1 | SO on sewer network | SE3060051600 | 430629 | 451588 | GB104027063741 | Crimple Beck from Source to Park Beck | River | 3308 | Middle and Lower Nidd | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER CRIMPLE VIA SEWER | Not Applicable | Not Applicable | Not Applicable | 113:15 | 30 | 36.2 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00767
YWS00768 | Yorkshire Water | Live | CLAYTON WEST STW | CLAYTON WEST/STW | 3809(SS) | 3809(SS) | A2 | Storm tank at WwTW | SE2678212075 | 426700 | 411948 | GB104027063220 | Dearne from Source to Bentley Brook | River | 3125 | Dearne | 3029 | Don and Rother | RIVER DEARNE | Not Applicable | Not Applicable | Not Applicable | 952:15 | 98 | 98.8 | 2020 | 100 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS00768
YWS00769 | Yorkshire Water | Live | CARLETON NO 2 STW | CARLETON/NO 2 STW | 381 | 381 | A2 | Storm tank at WwTW | SE4632019380 | 446320 | 419380 | GB104027063360 | Went from Hoyle Mill Stream to Blowell Drain | River | 3272 | Lower Don | 3029 | Don and Rother | RIVER LITTLE WENT | Not Applicable | Not Applicable | Not Applicable | 392:15 | 47 | 67 | 2020 | 99.99 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00769
YWS00770 | Yorkshire Water | Live | CARLETON NO 2 STW | CARLETON/NO 2 STW | 381 | 381 | A3 | Inlet SO at WwTW | SE4632019380 | 446320 | 419380 | GB104027063360 | Went from Hoyle Mill Stream to Blowell Drain | River | 3272 | Lower Don | 3029 | Don and Rother | RIVER LITTLE WENT | Not Applicable | Not Applicable | Not Applicable | 253:30 | 68 | 74 | 2020 | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00770
YWS00771 | Yorkshire Water | Live | NORTON NO. 2 STW | NORTON/NO 2 STW | 3816(SS) | 3816(SS) | A2 | Storm tank at WwTW | SE5490016200 | 454950 | 416200 | GB104027063360 | Went from Hoyle Mill Stream to Blowell Drain | River | 3272 | Lower Don | 3029 | Don and Rother | RIVER WENT | Not Applicable | Not Applicable | Not Applicable | 234:16 | 26 | 24.2 | 2020 | 99.76 |  |  | High spill threshold not met | High spill threshold not met | Operational investigation completed | Operational improvement completed | No SOAF investigation required | YWS00771
YWS00772 | Yorkshire Water | Live | ASKERN SEWAGE PUMPING STATION | ASKERN/CSO | 3817 | 3817(SS) | A1 | Storm discharge at pumping station | SE5656014370 | 456560 | 414370 | GB104027063360 | Went from Hoyle Mill Stream to Blowell Drain | River | 3272 | Lower Don | 3029 | Don and Rother | GREAT COMMON DRAIN | Not Applicable | Not Applicable | Not Applicable | 53:15 | 22 | 28.8 | 2020 | 99.8 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00772
YWS00773 | Yorkshire Water | Live | MYTHOLMES LANE CSO | MYTHOLMES LANE/CSO | 3827 | 3827(SS) | A1 | SO on sewer network | SE0360538083 | 403605 | 438083 | GB104027062891 | Worth from Bridgehouse Beck to R Aire | River | 3307 | Middle Aire | 3001 | Aire and Calder | RIVER WORTH | Not Applicable | Not Applicable | Not Applicable | 195:30 | 52 | 65.2 | 2020 | 99.99 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00773
YWS00774 | Yorkshire Water | Live | AGBRIGG GARAGE CSO | AGBRIGG GARAGE/CSO | 3828 | 3828(SS) | A1 | SO on sewer network | SE3494419253 | 434944 | 419253 | GB104027062560 | Oakenshaw Beck from Source to River Calder | River | 3268 | Lower Calder | 3001 | Aire and Calder | OAKENSHAW BECK | Not Applicable | Not Applicable | Not Applicable | 4:45 | 7 | 15.6 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00774
YWS00775 | Yorkshire Water | Live | MONTAGUE STREET CSO | MONTAGUE STREET/CSO | 3829 | 3829(SS) | A1 | SO on sewer network | SE3475018964 | 434750 | 418964 | GB104027062560 | Oakenshaw Beck from Source to River Calder | River | 3268 | Lower Calder | 3001 | Aire and Calder | OAKENSHAW BECK | Not Applicable | Not Applicable | Not Applicable | 60:00 | 20 | 23.4 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00775
YWS00776 | Yorkshire Water | Live | BECK STREET SEWAGE PUMPING STATION | EASINGTON BECK STREET/CSO | 3834 | 3834(SS) | 1 | Storm discharge at pumping station | TA4002018870 | 540020 | 418870 | Not part of a WFD catchment | Not part of a WFD catchment | River | N/A | N/A | N/A | N/A | EASINGTON DRAIN | Not Applicable | Not Applicable | Not Applicable | 15:00 | 3 | 5.2 | 2020 | 99.95 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00776
YWS00777 | Yorkshire Water | Live | ENGINE LANE SEWAGE PUMPING STATION | ENGINE LANE/CSO | 3836 | 3836(SS) | A1 | Storm discharge at pumping station | SE4073008830 | 440734 | 408821 | GB104027063180 | Grimethorpe Dike from Source to River Dearne | River | 3125 | Dearne | 3029 | Don and Rother | GRIMETHORPE DYKE | Not Applicable | Not Applicable | Not Applicable | 96:30 | 33 | 23 | 2020 | 99.98 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00777
YWS00778 | Yorkshire Water | Live | ENGINE LANE SEWAGE PUMPING STATION | ENGINE LANE/CSO | 3836 | 3836(SS) | A2 | Storm discharge at pumping station | SE4075008860 | 440748 | 408850 | GB104027063180 | Grimethorpe Dike from Source to River Dearne | River | 3125 | Dearne | 3029 | Don and Rother | GRIMETHORPE DYKE | Not Applicable | Not Applicable | Not Applicable | 13:45 | 3 | 4 | 2020 | 9.99 | Sensor failure / issue | Resolved - Nov | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00778
YWS00779 | Yorkshire Water | Live | LUNDWOOD SEWAGE PUMPING STATION | LUNDWOOD/CSO | 3841 | 3841(SS) | A2 | SO on sewer network | SE3770606519 | 437706 | 406519 | GB104027063171 | Dearne from Cawthorne Dyke to Lundwood STW | River | 3125 | Dearne | 3029 | Don and Rother | RIVER DEARNE | Not Applicable | Not Applicable | Not Applicable | 167:30 | 47 | 51.8 | 2020 | 99.96 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | No investigation activity in reporting period | No improvement action in reporting period | SOAF investigation completed - No work required | YWS00779
YWS00780 | Yorkshire Water | Live | FARRER LANE CSO | FARRER LANE/CSO | 3849 | 3849(SS) | 1 | SO on sewer network | SE3647028100 | 436470 | 428096 | GB104027062680 | Oulton Beck from Source to River Aire | River | 3265 | Lower Aire | 3001 | Aire and Calder | OULTON BECK | Not Applicable | Not Applicable | Not Applicable | 24:00 | 16 | 14.4 | 2020 | 99.98 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00780
YWS00781 | Yorkshire Water | Live | COLLIERY LANE CSO | COLLIERY LANE/CSO | 390 | 390 | A1 | SO on sewer network | SE1691019750 | 416910 | 419750 | GB70410176 | Huddersfield Broad Canal | Canal | 2007 | Calder Canals | 2001 | Humber AWB | CINDERFIELD DIKE | Not Applicable | Not Applicable | Not Applicable | 4:00 | 4 | 6 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00781
YWS00782 | Yorkshire Water | Live | SICKLINGHALL CSO | SICKLINGHALL/CSO | 4 | 4 | A1 | SO on sewer network | SE3654648397 | 436546 | 448397 | GB104027063700 | Park Beck Catch (trib of Crimple Beck) | River | 3308 | Middle and Lower Nidd | 3088 | Swale, Ure, Nidd and Upper Ouse | TRIBUTARY OF TOAD HALL BECK | Not Applicable | Not Applicable | Not Applicable |  |  | 0.5 | 2020 | 0 | Sensor failure / issue | Scheduled | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00782
YWS00783 | Yorkshire Water | Live | ACKWORTH STW | ACKWORTH/STW | 430 | 430 | A2 | Storm tank at WwTW | SE4663016680 | 446560 | 416660 | GB104027063360 | Went from Hoyle Mill Stream to Blowell Drain | River | 3272 | Lower Don | 3029 | Don and Rother | RIVER WENT | Not Applicable | Not Applicable | Not Applicable | 1757:30 | 130 | 144.6 | 2020 | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement ongoing | SOAF investigation ongoing | YWS00783
YWS00784 | Yorkshire Water | Live | COLD HIENDLEY STW | COLD HIENDLEY/STW | 431 | 431 | A2 | Storm tank at WwTW | SE3701014540 | 437010 | 414540 | GB70410051 | Barnsley Canal | Canal | 2018 | Don and Rother Canals | 2001 | Humber AWB | COLD HIENDLEY RESERVOIR | Not Applicable | Not Applicable | Not Applicable | 433:45 | 63 | 164.67 | 2020 | 99.56 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS00784
YWS00785 | Yorkshire Water | Live | YWS UNKNOWN SITES DEFAULT | NORTON HIGH STREET/CSO | 478 | 478 | 1 | SO on sewer network | SE5484015150 | 454843 | 415158 | GB104027063360 | Went from Hoyle Mill Stream to Blowell Drain | River | 3272 | Lower Don | 3029 | Don and Rother | GREAT COMMON DRAIN | Not Applicable | Not Applicable | Not Applicable | 236:00 | 25 | 24.8 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00785
YWS00786 | Yorkshire Water | Live | Not matched in EA Consents Database | HARBOUR VIEW BEDALE/CSO | 528 | 528 | 1 | SO on sewer network | SE2700088059 | 427000 | 488059 | GB104027068910 | Bedale/Newton/Burton Bk from Rand Bk to R Swale | River | 3317 | Middle Swale | 3088 | Swale, Ure, Nidd and Upper Ouse | Not matched in EA Consents Database | Not Applicable | Not Applicable | Not Applicable | 21:15 | 20 | 17.2 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00786
YWS00787 | Yorkshire Water | Live | JOHNNY MOORES HILL CSO | JOHNNY MOORES HILL/CSO | 54 | 54 | A1 | SO on sewer network | SE1271016000 | 412712 | 416008 | GB104027063330 | Colne from Wessenden Brook to R Holme | River | 3097 | Colne and Holme | 3001 | Aire and Calder | RIVER COLNE | Not Applicable | Not Applicable | Not Applicable | 113:45 | 65 | 74.4 | 2020 | 98.96 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | No investigation activity in reporting period | No improvement action in reporting period | SOAF investigation completed - No work required | YWS00787
YWS00788 | Yorkshire Water | Live | WILLOW LANE CSO | WILLOW LANE/CSO | 55 | 55 | A1 | SO on sewer network | SE1520017527 | 415200 | 417527 | GB104027062550 | Colne from River Holme to River Calder | River | 3097 | Colne and Holme | 3001 | Aire and Calder | RIVER COLNE(VIA BIRKBY RELIEF) | Not Applicable | Not Applicable | Not Applicable | 40:15 | 37 | 40 | 2020 | 99.93 |  |  | High spill threshold not met | High spill threshold not met | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00788
YWS00789 | Yorkshire Water | Live | HEBBLE BROOK CSO | HEBBLE BROOK/CSO | 555 | 555 | A1 | SO on sewer network | SE0645029000 | 406456 | 429998 | GB104027062780 | Hebble Brook from Source to River Calder | River | 3310 | Middle Calder | 3001 | Aire and Calder | HEBBLE BROOK | Not Applicable | Not Applicable | Not Applicable | 131:15 | 48 | 60.4 | 2020 | 98.33 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00789
YWS00790 | Yorkshire Water | Live | CRANE MOOR STW | CRANE MOOR/STW | 557 | 557 | 2 | Storm tank at WwTW | SE3082001440 | 430820 | 401440 | GB104027057480 | Rockley Dike from Source to River Dove | River | 3125 | Dearne | 3029 | Don and Rother | CRANE MOOR DIKE | Not Applicable | Not Applicable | Not Applicable | 1159:30 | 100 | 82.4 | 2020 | 97.22 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00790
YWS00791 | Yorkshire Water | Live | WELLFIELD TERRACE CSO | WELLFIELD TERRACE/2 CSO | 56 | 56 | 1 | SO on sewer network | SE2450029370 | 424503 | 429411 | GB104027062830 | Low/Wortley/Pudsey Bks | River | 3265 | Lower Aire | 3001 | Aire and Calder | TRIB OF FARNLEY WOOD BECK | Not Applicable | Not Applicable | Not Applicable | 63:15 | 38 | 36.4 | 2020 | 99.62 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00791
YWS00792 | Yorkshire Water | Permit Application Submitted | TBC When Permit Issued | GILLING EAST/STW | Permit applied for | 617 | TBC | Storm tank at WwTW | SE6220077300 | 462200 | 477400 | GB104027068420 | Holbeck from Source to Wath Beck | River | 3387 | Rye | 3027 | Derwent Humber | HOLBECK | Not Applicable | Not Applicable | Not Applicable | 469:45 | 41 | 54 | 2020 | 100 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00792
YWS00793 | Yorkshire Water | Live | YWS UNKNOWN SITES DEFAULT | STAINBECK LANE/CSO | 618 | 618 | 1 | SO on sewer network | SE2947037260 | 429474 | 437262 | GB104027062900 | Meanwood Beck from Source to River Aire | River | 3265 | Lower Aire | 3001 | Aire and Calder | STAIN BECK | Not Applicable | Not Applicable | Not Applicable | 0:30 | 2 | 2.25 | 2020 | 99.58 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00793
YWS00794 | Yorkshire Water | Live | BARWICK IN ELMET SEWAGE WORKS | BARWICK IN ELMET/STW | 65 | 65 | 2 | Storm tank at WwTW | SE4083037380 | 440670 | 437340 | GB104027063940 | Cock Beck Catchment (trib of Wharfe) | River | 3287 | Lower Wharfe | 3115 | Wharfe and Lower Ouse | TRIB OF COCK BECK | Not Applicable | Not Applicable | Not Applicable | 866:00 | 101 | 102 | 2020 | 99.57 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00794
YWS00795 | Yorkshire Water | Live | BARWICK IN ELMET SEWAGE WORKS | BARWICK IN ELMET/STW | 65 | 65 | 3 | Inlet SO at WwTW | SE4083037380 | 440670 | 437350 | GB104027063940 | Cock Beck Catchment (trib of Wharfe) | River | 3287 | Lower Wharfe | 3115 | Wharfe and Lower Ouse | TRIB OF COCK BECK | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0.4 | 2020 | 99.59 |  |  | High spill threshold not met | High spill threshold not met | Operational investigation completed | No improvement action in reporting period | No SOAF investigation required | YWS00795
YWS00796 | Yorkshire Water | Live | YWS UNKNOWN SITES DEFAULT | FENCE/CSO | 655 | 655 | 1 | Storm discharge at pumping station | SK4333086170 | 443330 | 386170 | GB104027057772 | Rother, Doe Lea to Don | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | ROTHER | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0.4 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00796
YWS00797 | Yorkshire Water | Live | HOOTON ROBERTS STW | HOOTON ROBERTS/STW | 664 | 664 | 2 | Inlet SO at WwTW | SK4780096900 | 447890 | 396970 | GB104027057430 | Hooton Brook from Source to River Don | River | 3312 | Middle Don | 3029 | Don and Rother | HOOTON BROOK | Not Applicable | Not Applicable | Not Applicable | 294:45 | 38 | 74.8 | 2020 | 99.99 |  |  | High spill threshold not met | Performance - Asset configuration (e.g. PS/rising main/storm tanks) | UWWTR investigation ongoing, Operational investigation ongoing | Operational improvement ongoing | SOAF investigation ongoing | YWS00797
YWS00798 | Yorkshire Water | Live | TOWN STREET SHEFFIELD CSO | TOWN STREET SHEFFLD/CSO | 665 | 665 | A1 | SO on sewer network | SK4014091540 | 439855 | 391074 | GB104027057413 | Don from River Don Works to River Rother | River | 3312 | Middle Don | 3029 | Don and Rother | DON | Not Applicable | Not Applicable | Not Applicable | 43:45 | 23 | 7.2 | 2020 | 75.35 | Comms failure / issue | Resolved - Dec | High spill threshold not met | High spill threshold not met | Operational investigation completed | Operational improvement completed | No SOAF investigation required | YWS00798
YWS00799 | Yorkshire Water | Live | TOWN STREET SHEFFIELD CSO | RABY STREET/CSO | 665 | EPR/ZB3690EL | A1 | SO on sewer network | SK4014091540 | 440140 | 391545 | GB104027057413 | Don from River Don Works to River Rother | River | 3312 | Middle Don | 3029 | Don and Rother | DON | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 1.2 | 2020 | 48.25 | Comms failure / issue | Scheduled | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00799
YWS00800 | Yorkshire Water | Live | TOWN STREET SHEFFIELD CSO | SHEFFIELD RD TINSLEY/CSO | 665 | EPR/ZB3690RV | A1 | SO on sewer network | SK4014091540 | 440140 | 391545 | GB104027057413 | Don from River Don Works to River Rother | River | 3312 | Middle Don | 3029 | Don and Rother | DON | Not Applicable | Not Applicable | Not Applicable | 30:45 | 24 | 25.2 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00800
YWS00801 | Yorkshire Water | Live | TOWN STREET SHEFFIELD CSO | ST LAWRENCE ROAD/CSO | 665 | EPR/ZB3690AQ | A1 | SO on sewer network | SK4014091540 | 440140 | 391545 | GB104027057413 | Don from River Don Works to River Rother | River | 3312 | Middle Don | 3029 | Don and Rother | DON | Not Applicable | Not Applicable | Not Applicable | 21:15 | 14 | 6.2 | 2020 | 99.91 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00801
YWS00802 | Yorkshire Water | Live | TOWN STREET SHEFFIELD CSO | FERRARS ROAD/CSO | 665 | EPR/ZB3599WZ | A1 | SO on sewer network | SK4014091540 | 440140 | 391545 | GB104027057413 | Don from River Don Works to River Rother | River | 3312 | Middle Don | 3029 | Don and Rother | DON | Not Applicable | Not Applicable | Not Applicable | 39:30 | 26 | 22.8 | 2020 | 98.86 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00802
YWS00803 | Yorkshire Water | Live | TOWN STREET SHEFFIELD CSO | SHEFFIELD ROAD WORKS/CSO | 665 | EPR/ZB3690DS | A1 | SO on sewer network | SK4014091540 | 440140 | 391545 | GB104027057413 | Don from River Don Works to River Rother | River | 3312 | Middle Don | 3029 | Don and Rother | DON | Not Applicable | Not Applicable | Not Applicable | 48:30 | 27 | 7 | 2020 | 99.31 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00803
YWS00804 | Yorkshire Water | Live | Not matched in EA Consents Database | STANNINGTON ROAD/NO 2 CSO | 735 | 735 | 1 | SO on sewer network | SK3250789293 | 432507 | 389293 | GB104027057340 | Rivelin from Source to River Loxley | River | 3490 | Upper Don | 3029 | Don and Rother | Not matched in EA Consents Database | Not Applicable | Not Applicable | Not Applicable | 92:15 | 53 | 69 | 2020 | 99.14 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | No investigation activity in reporting period | No improvement action in reporting period | SOAF investigation completed - No work required | YWS00804
YWS00805 | Yorkshire Water | Live | HORSFORTH RING ROAD CSO | HORSFORTH RING ROAD/CSO | 779 | 779 | A1 | SO on sewer network | SE2531237683 | 425312 | 437683 | GB104027062920 | Carlton Beck from Source to River Aire | River | 3265 | Lower Aire | 3001 | Aire and Calder | OIL MILL BECK | Not Applicable | Not Applicable | Not Applicable | 80:45 | 57 | 68.2 | 2020 | 99.99 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS00805
YWS00806 | Yorkshire Water | Live | BIRDS EDGE CSO | BIRDS EDGE/CSO | 791 | 791 | A1 | SO on sewer network | SE2041007970 | 420416 | 407972 | GB104027063220 | Dearne from Source to Bentley Brook | River | 3125 | Dearne | 3029 | Don and Rother | RIVER DEARNE | Not Applicable | Not Applicable | Not Applicable | 25:15 | 9 | 8.8 | 2020 | 99.9 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00806
YWS00807 | Yorkshire Water | Live | BRAMHAM LOW WAY CSO | BRAMHAM LOW WAY/CSO | 86 | 86 | A1 | SO on sewer network | SE4257842985 | 442578 | 442985 | GB104027063950 | Thorner Beck Catchment (trib of Wharfe) | River | 3287 | Lower Wharfe | 3115 | Wharfe and Lower Ouse | CARR BECK | Not Applicable | Not Applicable | Not Applicable | 42:45 | 29 | 16 | 2020 | 99.81 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00807
YWS00808 | Yorkshire Water | Live | HOLMESFIELD STW | HOLMESFIELD/STW | 876 | 876 | 3 | Storm tank at WwTW | SK3280077900 | 432800 | 377900 | GB104027057700 | Barlow Brook from Source to River Drone | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | HOLMESFIELD BROOK | Not Applicable | Not Applicable | Not Applicable | 571:00 | 75 | 75.6 | 2020 | 100 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement completed | SOAF investigation ongoing | YWS00808
YWS00809 | Yorkshire Water | Live | YWS UNKNOWN SITES DEFAULT | FORGE LANE DEWSBURY/CSO | 878 | 878 | 1 | SO on sewer network | SE2375019790 | 423753 | 419798 | GB104027062631 | Calder from River Colne to River Chald | River | 3268 | Lower Calder | 3001 | Aire and Calder | CALDER | Not Applicable | Not Applicable | Not Applicable | 159:15 | 40 | 13.6 | 2020 | 99.57 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00809
YWS00810 | Yorkshire Water | Live | CLAREMONT CRESCENT NO.2 CSO | CLAREMONT CRES/NO 2 CSO | EPRHB3894NX | EPR/HB3894NX | A1 | SO on sewer network | SE2897036403 | 429224 | 436174 | GB104027062900 | Meanwood Beck from Source to River Aire | River | 3265 | Lower Aire | 3001 | Aire and Calder | MEANWOOD BECK & STAIN BECK | Not Applicable | Not Applicable | Not Applicable | 85:15 | 56 | 51.4 | 2020 | 99.96 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00810
YWS00811 | Yorkshire Water | Live | MEANWOOD ROAD CSO | MEANWOOD ROAD/CSO | 909 | 909 | A1 | SO on sewer network | SE2922436174 | 429224 | 436174 | GB104027062900 | Meanwood Beck from Source to River Aire | River | 3265 | Lower Aire | 3001 | Aire and Calder | MEANWOOD BECK | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 7.6 | 2020 | 98.55 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00811
YWS00812 | Yorkshire Water | Permit Application Submitted | TBC When Permit Issued | BRAWBY/STW | Permit applied for | 92 | TBC | Inlet SO at WwTW | SE7400078200 | 474000 | 478200 | GB104027068440 | Seven from Catter Beck to River Rye | River | 3387 | Rye | 3027 | Derwent Humber | TRIB OF RIVER SEVEN | Not Applicable | Not Applicable | Not Applicable | 642:30 | 68 | 57 | 2020 | 99.93 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement ongoing | SOAF investigation ongoing | YWS00812
YWS00813 | Yorkshire Water | Live | YWS UNKNOWN SITES DEFAULT | ABBEYDALE ROAD 62/1 CSO | 920 | 920 | 1 | SO on sewer network | SK3444084450 | 434440 | 384451 | GB104027057750 | Sheaf from Source to River Don | River | 3312 | Middle Don | 3029 | Don and Rother | RIVER SHEAF | Not Applicable | Not Applicable | Not Applicable | 83:30 | 36 | 22.8 | 2020 | 96.44 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00813
YWS00814 | Yorkshire Water | Live | FULFORD MAIN CSO | FULFORD MAIN STREET/CSO | 952 | 952 | A1 | SO on sewer network | SE6109248703 | 461092 | 448703 | GB104027069593 | Ouse from River Nidd to Stillingfleet Beck | River | 3499 | Upper Ouse Yorkshire | 3088 | Swale, Ure, Nidd and Upper Ouse | GERMANY BECK | Not Applicable | Not Applicable | Not Applicable | 76:02 | 56 | 52 | 2020 | 99.99 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement ongoing | SOAF investigation ongoing | YWS00814
YWS00815 | Yorkshire Water | Live | HIGH ROYD SEWAGE TREATMENT WORKS | HIGH ROYD/NO 2 STW/3XDWF OVERFLOW | 967 | 967 | A2 | Storm tank at WwTW | SE0469223871 | 404692 | 423871 | GB104027062641 | Calder from Colden Water to Ryburn Confluence | River | 3310 | Middle Calder | 3001 | Aire and Calder | RIVER CALDER | Not Applicable | Not Applicable | Not Applicable | 1051:40 | 91 | 82.4 | 2020 | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS00815
YWS00816 | Yorkshire Water | Live | HIGH ROYD SEWAGE TREATMENT WORKS | HIGH ROYD TOWPATH/CSO | 967 | 967 | A3 | SO on sewer network | SE0469023880 | 404632 | 423943 | GB104027062641 | Calder from Colden Water to Ryburn Confluence | River | 3310 | Middle Calder | 3001 | Aire and Calder | RIVER CALDER | Not Applicable | Not Applicable | Not Applicable | 490:34 | 67 | 66.2 | 2020 | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00816
YWS00817 | Yorkshire Water | Live | HIGH ROYD SEWAGE TREATMENT WORKS | ROSE GROVE LANE/CSO | 967 | 967 | A4 | SO on sewer network | SE0457823968 | 404578 | 423968 | GB104027062641 | Calder from Colden Water to Ryburn Confluence | River | 3310 | Middle Calder | 3001 | Aire and Calder | RIVER CALDER | Not Applicable | Not Applicable | Not Applicable | 141:22 | 61 | 37.2 | 2020 | 99.56 |  |  | Not asset maintenance - Hydraulic capacity | High spill threshold not met | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS00817
YWS00819 | Yorkshire Water | Live | PLEDWICK CSO | PLEDWICK/CSO | 987 | 987 | A1 | SO on sewer network | SE3339916866 | 433399 | 416866 | GB104027062530 | Owler Beck from Source to River Calder | River | 3268 | Lower Calder | 3001 | Aire and Calder | OWLER BECK VIA SURFACE WTR SW | Not Applicable | Not Applicable | Not Applicable | 8:30 | 19 | 14.4 | 2020 | 99.87 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00819
YWS00820 | Yorkshire Water | Live | HETTON WWTW | HETTON/STW | 994 | 994 | A2 | Storm tank at WwTW | SD9617058410 | 396170 | 458410 | GB104027063080 | Flasby Beck from Source to Eshton Beck | River | 3484 | Upper Aire | 3001 | Aire and Calder | HETTON BECK | Not Applicable | Not Applicable | Not Applicable | 1820:00 | 110 | 104.6 | 2020 | 92.77 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation ongoing | Operational improvement ongoing | SOAF investigation ongoing | YWS00820
YWS00821 | Yorkshire Water | Live | Not matched in EA Consents Database | RAINTON ROAD/NO 1 CSO | B/8073 | B/8073 | 1(1) | SO on sewer network | SE5834602270 | 458346 | 402270 | GB104028058440 | Mother Drain from Source to Torne | River | 3234 | Isle of Axholme | 3041 | Idle and Torne | Not matched in EA Consents Database | Not Applicable | Not Applicable | Not Applicable | 1:30 | 2 | 3.6 | 2020 | 99.97 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00821
YWS00822 | Yorkshire Water | Live | Not matched in EA Consents Database | RAINTON ROAD/NO 2 CSO | B/8073 | B/8073 | 1(2) | SO on sewer network | SE5834602270 | 458346 | 402270 | GB104028058440 | Mother Drain from Source to Torne | River | 3234 | Isle of Axholme | 3041 | Idle and Torne | Not matched in EA Consents Database | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0.2 | 2020 | 98.14 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00822
YWS00823 | Yorkshire Water | Live | Not matched in EA Consents Database | WHITBURN ROAD/CSO | B/8073 | B/8073 | 1(3) | SO on sewer network | SE5834602270 | 458346 | 402270 | GB104028058440 | Mother Drain from Source to Torne | River | 3234 | Isle of Axholme | 3041 | Idle and Torne | Not matched in EA Consents Database | Not Applicable | Not Applicable | Not Applicable | 1:15 | 3 | 1 | 2020 | 99.89 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00823
YWS00824 | Yorkshire Water | Live | Not matched in EA Consents Database | STOCKIL ROAD/CSO | B/8073 | B/8073 | 1(4) | SO on sewer network | SE5834602270 | 458346 | 402270 | GB104028058440 | Mother Drain from Source to Torne | River | 3234 | Isle of Axholme | 3041 | Idle and Torne | Not matched in EA Consents Database | Not Applicable | Not Applicable | Not Applicable | 0:15 | 1 | 0.6 | 2020 | 99.94 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00824
YWS00825 | Yorkshire Water | Live | RODLEY BAGLEY LANE CSO | RODLEY BAGLEY LANE/CSO | C3954 | C3954 | A1 | SO on sewer network | SE2229036300 | 422299 | 436309 | GB104027063032 | Aire from Gill Beck (Baildon) to River Calder | River | 3265 | Lower Aire | 3001 | Aire and Calder | BAGLEY BECK | Not Applicable | Not Applicable | Not Applicable | 187:45 | 73 | 73.4 | 2020 | 99.89 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00825
YWS00826 | Yorkshire Water | Live | KENT ROAD CSO | KENT ROAD/CSO | C3961 | C3961 | A1 | SO on sewer network | SE2302032610 | 423026 | 432612 | GB104027062830 | Low/Wortley/Pudsey Bks | River | 3265 | Lower Aire | 3001 | Aire and Calder | TRIBUTARY OF PUDSEY BECK | Not Applicable | Not Applicable | Not Applicable | 27:45 | 25 | 27.5 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00826
YWS00827 | Yorkshire Water | Live | THORNES LANE WHARFE CSO | THORNES WHARFE/CSO | C3967 | C3967 | 1 | SO on sewer network | SE3360019900 | 433617 | 419898 | GB104027062631 | Calder from River Colne to River Chald | River | 3268 | Lower Calder | 3001 | Aire and Calder | RIVER CALDER | Not Applicable | Not Applicable | Not Applicable | 95:30 | 31 | 34 | 2020 | 99.98 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00827
YWS00828 | Yorkshire Water | Live | BOLTON BRIDGE SPS | BOLTON BRIDGE/CSO | C4062 | C4062 | A2 | Storm discharge at pumping station | SE0721452838 | 407214 | 452838 | GB104027064257 | Wharfe from Barben Beck/River Dibb to Hundwith Beck | River | 3318 | Middle Wharfe and Washburn | 3115 | Wharfe and Lower Ouse | RIVER WHARFE | Not Applicable | Wharfe at Cromwheel, Ilkley | Not Applicable | 29:15 | 10 | 12.75 | 2020 | 99.9 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00828
YWS00829 | Yorkshire Water | Live | CLIFTON PARK CSO | CLIFTON PARK/CSO | C4074 | C4074(SS) | A1 | SO on sewer network | SK4310693708 | 443106 | 393708 | GB104027057452 | Don from River Rother to River Dearne | River | 3312 | Middle Don | 3029 | Don and Rother | TRIBUTARY OF THE RIVER DON | Not Applicable | Not Applicable | Not Applicable | 60:00 | 31 | 45 | 2020 | 99.99 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00829
YWS00830 | Yorkshire Water | Live | CALDERVALE (WAKEFIELD) STW | CALDER VALE/STW/3XDWF OVERFLOW | C4106 | C4106 | 2 | Storm tank at WwTW | SE3506020400 | 435060 | 420400 | GB104027062632 | Calder from River Chald to River Aire | River | 3268 | Lower Calder | 3001 | Aire and Calder | RIVER CALDER | Not Applicable | Not Applicable | Not Applicable | 373:15 | 41 | 57 | 2020 | 99.98 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00830
YWS00831 | Yorkshire Water | Live | CALDERVALE (WAKEFIELD) STW | CALDER VALE/STW/6XDWF OVERFLOW | C4106 | C4106 | 3 | Inlet SO at WwTW | SE3574021350 | 435740 | 421350 | GB104027062632 | Calder from River Chald to River Aire | River | 3268 | Lower Calder | 3001 | Aire and Calder | RIVER CALDER | Not Applicable | Not Applicable | Not Applicable | 329:30 | 75 | 54.2 | 2020 | 99.93 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00831
YWS00832 | Yorkshire Water | Live | HORBURY STW | HORBURY/STW | C4107 | C4107 | A2 | Storm tank at WwTW | SE3000017070 | 430000 | 417070 | GB104027062631 | Calder from River Colne to River Chald | River | 3268 | Lower Calder | 3001 | Aire and Calder | RIVER CALDER | Not Applicable | Not Applicable | Not Applicable | 820:30 | 90 | 94 | 2020 | 100 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation ongoing | Operational improvement ongoing | SOAF investigation ongoing | YWS00832
YWS00833 | Yorkshire Water | Live | HORBURY STW | HORBURY/STW/6XDWF OVERFLOW | C4107 | C4107 | A3 | Inlet SO at WwTW | SE3017017420 | 430170 | 417420 | GB104027062631 | Calder from River Colne to River Chald | River | 3268 | Lower Calder | 3001 | Aire and Calder | RIVER CALDER | Not Applicable | Not Applicable | Not Applicable | 177:45 | 53 | 60.8 | 2020 | 99.99 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00833
YWS00834 | Yorkshire Water | Live | CARR GREEN CSO | CARR GREEN/CSO | C4139 | C4139 | A1 | SO on sewer network | SE3308209288 | 433082 | 409288 | GB104027063171 | Dearne from Cawthorne Dyke to Lundwood STW | River | 3125 | Dearne | 3029 | Don and Rother | DYKE TO RIVER DEARNE | Not Applicable | Not Applicable | Not Applicable | 87:45 | 42 | 39.2 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | UWWTR investigation ongoing, Operational investigation completed | Operational improvement ongoing | SOAF investigation ongoing | YWS00834
YWS00835 | Yorkshire Water | Live | BRAMLEY PARK CLOSE CSO | BRAMLEY PARK CLOSE/CSO | C4153 | C4153(SS) | A1 | SO on sewer network | SK4064085840 | 440640 | 385840 | GB104027057772 | Rother, Doe Lea to Don | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | SHIRTCLIFF BROOK | Not Applicable | Not Applicable | Not Applicable | 108:30 | 49 | 55.8 | 2020 | 100 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS00835
YWS00836 | Yorkshire Water | Live | PLANTATION DRIVE CSO | PLANTATION DRIVE/CSO | C4158 | C4158 | A1 | SO on sewer network | SE5752152711 | 457520 | 452730 | GB104027069593 | Ouse from River Nidd to Stillingfleet Beck | River | 3499 | Upper Ouse Yorkshire | 3088 | Swale, Ure, Nidd and Upper Ouse | ING CLIFFS DRAIN | Not Applicable | Not Applicable | Not Applicable | 35:10 | 39 | 31 | 2020 | 92.8 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00836
YWS00837 | Yorkshire Water | Live | DEEP LANE SHEFFIELD CSO | DEEP LANE SHEFFIELD/CSO | C4159 | C4159(SS) | A1 | SO on sewer network | SK3757093580 | 437567 | 393582 | GB104027057440 | Blackburn Brook from Source to River Don | River | 3312 | Middle Don | 3029 | Don and Rother | BLACKBURN BROOK | Not Applicable | Not Applicable | Not Applicable | 75:45 | 27 | 13.4 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00837
YWS00838 | Yorkshire Water | Live | BUTTERTHWAITE ROAD CSO | BUTTERTHWAITE ROAD/CSO | C4163 | C4163(SS) | A1 | SO on sewer network | SK3708993703 | 437089 | 393703 | GB104027057440 | Blackburn Brook from Source to River Don | River | 3312 | Middle Don | 3029 | Don and Rother | BLACKBURN BROOK | Not Applicable | Not Applicable | Not Applicable | 22:15 | 17 | 35.4 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS00838
YWS00839 | Yorkshire Water | Live | COXWOLD SEWAGE TREATMENT PLANT | COXWOLD/STW | C4234 | C4234 | A2 | Inlet SO at WwTW | SE5350077000 | 453480 | 476950 | GB104027068790 | Birdforth/Green's Bks Catch (trib of Swale) | River | 3283 | Lower Swale | 3088 | Swale, Ure, Nidd and Upper Ouse | GREEN'S BECK | Not Applicable | Not Applicable | Not Applicable | 6:30 | 5 | 6.4 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00839
YWS00840 | Yorkshire Water | Live | THE FALLS SPS | ARDSLEY FALLS/CSO | C4235 | C4235(SS) | A1 | Storm discharge at pumping station | SE3147025970 | 431470 | 425970 | GB104027062680 | Oulton Beck from Source to River Aire | River | 3265 | Lower Aire | 3001 | Aire and Calder | BOWLING BECK | Not Applicable | Not Applicable | Not Applicable | 56:45 | 16 | 31.2 | 2020 | 80.56 | Sensor failure / issue | Resolved - Jul | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00840
YWS00841 | Yorkshire Water | Live | FLOCKTON TANK CSO | FLOCKTON PINFOLD LANE/CSO | C4236 | C4236(SS) | A1 | SO on sewer network | SE2441514787 | 424415 | 414787 | GB104027063310 | Bentley Brook from Source to River Dearne | River | 3125 | Dearne | 3029 | Don and Rother | FLOCKTON BECK | Not Applicable | Not Applicable | Not Applicable | 9:00 | 4 | 4.8 | 2020 | 77.12 | Comms failure / issue | Resolved - Jul | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00841
YWS00842 | Yorkshire Water | Live | WATH MOOR ROAD CSO | WATH MOOR ROAD/CSO | C4237 | C4237(SS) | A1 | SO on sewer network | SE4366001130 | 443662 | 401136 | GB104027057470 | Knoll Beck from Source to River Dearne | River | 3125 | Dearne | 3029 | Don and Rother | BROOK DIKE | Not Applicable | Not Applicable | Not Applicable | 23:15 | 23 | 26 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00842
YWS00843 | Yorkshire Water | Live | CHAPELTHORPE CSO | CHAPELTHORPE/CSO | C4238 | C4238(SS) | A1 | SO on sewer network | SE3226715699 | 432267 | 415699 | GB104027062530 | Owler Beck from Source to River Calder | River | 3268 | Lower Calder | 3001 | Aire and Calder | CHAPELTHORPE BANK TRIB OWLER B | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0.4 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00843
YWS00844 | Yorkshire Water | Live | KIRKGATE CHANTRY BRIDGE CSO | KIRKGATE CHANTRY BRDG/CSO | C4245 | C4245 | A1 | SO on sewer network | SE3378320018 | 433783 | 420186 | GB104027062631 | Calder from River Colne to River Chald | River | 3268 | Lower Calder | 3001 | Aire and Calder | RIVER CALDER VIA PUMPED OUTLET | Not Applicable | Not Applicable | Not Applicable | 20:15 | 10 | 16.6 | 2020 | 27.69 | Sensor failure / issue | Resolved - Sep | High spill threshold not met | High spill threshold not met | Operational investigation completed | Operational improvement completed | No SOAF investigation required | YWS00844
YWS00845 | Yorkshire Water | Live | MEADOW FIELD CSO | MEADOW FIELD/CSO | C4266 | C4266(SS) | A1 | Storm discharge at pumping station | SE6121654424 | 461216 | 454424 | GB104027063520 | Foss from the Syke to the River Ouse | River | 3190 | Foss | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER FOSS | Not Applicable | Not Applicable | Not Applicable | 76:30 | 21 | 15.6 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00845
YWS00846 | Yorkshire Water | Live | ECKINGTON CSO | ECKINGTON/CSO | C4277 | C4277 | A1 | SO on sewer network | SK4376079910 | 443780 | 379910 | GB104027057720 | The Moss from Source to River Rother | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | RIVER MOSS | Not Applicable | Not Applicable | Not Applicable | 31:45 | 20 | 37.8 | 2020 | 99.35 |  |  | High spill threshold not met | High spill threshold not met | UWWTR investigation ongoing, Operational investigation completed | Operational improvement completed | SOAF investigation ongoing | YWS00846
YWS00847 | Yorkshire Water | Live | BECTIVE MILLS CSO | BECTIVE MILLS/CSO | C4278 | C4278(SS) | A1 | SO on sewer network | SE3121821027 | 431218 | 421027 | GB104027062620 | Chald from Source to River Calder | River | 3268 | Lower Calder | 3001 | Aire and Calder | ALVERTHORPE BECK | Not Applicable | Not Applicable | Not Applicable | 59:30 | 37 | 60.8 | 2020 | 100 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00847
YWS00848 | Yorkshire Water | Live | CHATSWORTH ROAD N471 CSO | CHATSWORTH ROAD N471/CSO | C4388 | C4388(SS) | 1 | SO on sewer network | SK3632070550 | 436325 | 370554 | GB104027057660 | Hipper from Source to River Rother | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | RIVER HIPPER | Not Applicable | Not Applicable | Not Applicable | 101:30 | 45 | 45.8 | 2020 | 88.82 | Comms failure / issue | Resolved - Feb | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement completed | SOAF investigation ongoing | YWS00848
YWS00849 | Yorkshire Water | Live | TOLL HOUSE STORMWATER OUTFALL | TOLL HOUSE/SPS | C4409 | C4409 | A1 | Storm discharge at pumping station | TA0528489001 | 505284 | 489001 | GB650401500004 | Yorkshire North | Coastal Water | 3179 | Esk TraC | 3040 | Humber TraC | NORTH SEA | Not Applicable | Scarborough South Bay | Not Applicable | 20:02 | 25 | 27.25 | 2021 | 100 |  |  | High spill threshold not met | High spill threshold not met | Operational investigation ongoing | Operational improvement ongoing | No SOAF investigation required | YWS00849
YWS00850 | Yorkshire Water | Live | AQUARIUM TOP STORMWATER OUTFALL | AQUARIUM TOP/CSO | C4411 | C4411 | 1 | SO on sewer network | TA0443088280 | 504439 | 488301 | GB650401500004 | Yorkshire North | Coastal Water | 3179 | Esk TraC | 3040 | Humber TraC | NORTH SEA | Not Applicable | Scarborough South Bay | Not Applicable | 0:00 | 0 | 0.8 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00850
YWS00851 | Yorkshire Water | Live | GRANGE MOOR CSO | GRANGE MOOR/CSO | C4480 | C4480(SS) | A1 | SO on sewer network | SE2190116933 | 421901 | 416933 | GB104027062510 | Smithy Brook from Source to River Calder | River | 3268 | Lower Calder | 3001 | Aire and Calder | FALHOUSE BECK | Not Applicable | Not Applicable | Not Applicable | 5:15 | 5 | 5.33 | 2020 | 79.7 | Comms failure / issue | Resolved - Sep | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | SOAF investigation completed - operational solution completed | YWS00851
YWS00852 | Yorkshire Water | Live | WHITLEY ROAD STORM BALANCING TANK | WHITLEY TANK/CSO | C4481 | C4481(SS) | 1 | SO on sewer network | SE2252018000 | 422518 | 417998 | GB104027062510 | Smithy Brook from Source to River Calder | River | 3268 | Lower Calder | 3001 | Aire and Calder | TRIBUTARY OF HOWROYD BECK | Not Applicable | Not Applicable | Not Applicable | 0:45 | 1 | 1.8 | 2020 | 75.57 | Comms failure / issue | Resolved - Apr | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00852
YWS00854 | Yorkshire Water | Live | YORKSHIRE WATER AUTHORITY STORM OVE | MORLEY STATION ROAD/CSO | C4578 | C4578(SS) | 1 | SO on sewer network | SE2780028600 | 426973 | 428195 | GB104027062750 | Milshaw Beck from Source to Low/Wortley/Pudsey Bks | River | 3265 | Lower Aire | 3001 | Aire and Calder | COTTON MILL BECK | Not Applicable | Not Applicable | Not Applicable | 0:45 | 2 | 0.4 | 2020 | 99.91 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00854
YWS00855 | Yorkshire Water | Live | PASTURES ROAD SPS | PASTURES ROAD/NO 2 CSO | C4614 | C4614 | 1 | Storm discharge at pumping station | SE4897000120 | 448970 | 400120 | GB104027057452 | Don from River Rother to River Dearne | River | 3312 | Middle Don | 3029 | Don and Rother | TRIBUTARY OF THE RIVER DEARNE | Not Applicable | Not Applicable | Not Applicable | 56:30 | 13 | 13.6 | 2020 | 99.42 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00855
YWS00856 | Yorkshire Water | Live | PARK ROAD CSO | PARK ROAD/CSO | C4856 | C4856 | A1 | SO on sewer network | SE1124421795 | 411244 | 421795 | GB104027062642 | Calder from Ryburn Confluence to River Colne | River | 3310 | Middle Calder | 3001 | Aire and Calder | RIVER CALDER | Not Applicable | Not Applicable | Not Applicable | 0:45 | 3 | 1.8 | 2020 | 99.94 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00856
YWS00857 | Yorkshire Water | Live | POOLS LANE CSO | POOLS LANE/CSO | C4871 | C4871 | A1 | SO on sewer network | SE3765710923 | 437657 | 410923 | GB104027063230 | Cudworth Dyke from Source to River Dearne | River | 3125 | Dearne | 3029 | Don and Rother | POOLS DIKE | Not Applicable | Not Applicable | Not Applicable | 80:15 | 18 | 23.5 | 2020 | 99.69 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00857
YWS00858 | Yorkshire Water | Live | KENDRAY DONCASTER ROAD CSO | KENDRAY DONCASTER RD/CSO | C4872 | C4872 | A1 | SO on sewer network | SE3726206236 | 437262 | 406236 | GB104027063171 | Dearne from Cawthorne Dyke to Lundwood STW | River | 3125 | Dearne | 3029 | Don and Rother | RIVER DEARNE | Not Applicable | Not Applicable | Not Applicable | 25:15 | 14 | 17.6 | 2020 | 99.91 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00858
YWS00859 | Yorkshire Water | Live | HOUGH SIDE WORKS CSO | HOUGH SIDE WORKS/CSO | C4917 | C4917 | A1 | SO on sewer network | SE2365433149 | 423654 | 433149 | GB104027062830 | Low/Wortley/Pudsey Bks | River | 3265 | Lower Aire | 3001 | Aire and Calder | FARNLEY BECK | Not Applicable | Not Applicable | Not Applicable | 686:30 | 103 | 93.6 | 2020 | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00859
YWS00860 | Yorkshire Water | Live | BACON LANE CSO | BACON LANE/CSO | C4919 | C4919 | A1 | SO on sewer network | SK3729088260 | 437295 | 388270 | GB104027057412 | Don from River Loxley confl to River Don Works | River | 3312 | Middle Don | 3029 | Don and Rother | RIVER DON | Not Applicable | Not Applicable | Not Applicable | 37:45 | 19 | 27 | 2020 | 58.6 | Sensor failure / issue | Resolved - Sep | High spill threshold not met | High spill threshold not met | Operational investigation completed | Operational improvement completed | No SOAF investigation required | YWS00860
YWS00861 | Yorkshire Water | Live | FEATHERSTONE LANE (NORTH) SPS | FEATHERSTONE LNE TANK/CSO | C4935 | C4935 | 1 | Storm discharge at pumping station | SE4255021580 | 442550 | 421580 | GB104027062590 | Choke Churl Bk from Source to River Calder | River | 3268 | Lower Calder | 3001 | Aire and Calder | SEWERBRIDGE BECK | Not Applicable | Not Applicable | Not Applicable | 61:30 | 35 | 22.2 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00861
YWS00862 | Yorkshire Water | Live | SEWERBRIDGE LANE CSO | SEWERBRIDGE LANE/CSO | C4936 | C4936 | A1 | SO on sewer network | SE4130121355 | 441301 | 421355 | GB104027062590 | Choke Churl Bk from Source to River Calder | River | 3268 | Lower Calder | 3001 | Aire and Calder | SEWERBRIDGE BECK | Not Applicable | Not Applicable | Not Applicable | 111:45 | 22 | 33 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00862
YWS00863 | Yorkshire Water | Live | NIDD WALK CSO | NIDD WALK/CSO | C4937 | C4937 | A1 | SO on sewer network | SE1632264933 | 416322 | 464933 | GB104027068295 | Nidd from Ashfoldside Beck to Birstwith | River | 3497 | Upper Nidd | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER NIDD VIA SWS | Not Applicable | Not Applicable | Not Applicable | 516:45 | 58 | 69.2 | 2020 | 96.25 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation completed, Operational investigation completed | Operational improvement ongoing | SOAF investigation completed - No work required | YWS00863
YWS00864 | Yorkshire Water | Live | ALDWARKE WWTW | ALDWARKE/STW | C4954 | C4954 | A2 | Storm tank at WwTW | SK4506094470 | 445060 | 394470 | GB104027057452 | Don from River Rother to River Dearne | River | 3312 | Middle Don | 3029 | Don and Rother | RIVER DON | Not Applicable | Not Applicable | Not Applicable | 425:00 | 43 | 51.8 | 2020 | 95.98 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS00864
YWS00865 | Yorkshire Water | Live | MARYGATE LANDING CSO (NO2) | MARYGATE LANDING/CSO | C4957 | C4957 | A1 | SO on sewer network | SE5973152034 | 459731 | 452034 | GB104027069593 | Ouse from River Nidd to Stillingfleet Beck | River | 3499 | Upper Ouse Yorkshire | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER OUSE | Not Applicable | Not Applicable | Not Applicable | 1581:24 | 128 | 102.6 | 2020 | 99.96 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00865
YWS00866 | Yorkshire Water | Live | JUBILEE TERRACE CSO | JUBILEE TERRACE/CSO | C4958 | C4958 | A1 | SO on sewer network | SE5899052540 | 458990 | 452540 | GB104027069593 | Ouse from River Nidd to Stillingfleet Beck | River | 3499 | Upper Ouse Yorkshire | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER OUSE | Not Applicable | Not Applicable | Not Applicable | 67:44 | 17 | 28.8 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | SOAF investigation completed - No work required | YWS00866
YWS00867 | Yorkshire Water | Live | BRIDGE END PENISTONE CSO | BRIDGE END PENISTONE/CSO | C4960 | C4960 | A1 | SO on sewer network | SE2443003700 | 424433 | 403703 | GB104027057500 | Don from Source to Scout Dyke | River | 3490 | Upper Don | 3029 | Don and Rother | RIVER DON | Not Applicable | Not Applicable | Not Applicable | 314:15 | 59 | 76.8 | 2020 | 100 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00867
YWS00868 | Yorkshire Water | Live | EDMUNDS ROAD CSO | EDMUNDS ROAD/CSO | C4961 | C4961 | A1 | SO on sewer network | SE3611003520 | 436113 | 403521 | GB104027057510 | Dove from Source to River Dearne | River | 3125 | Dearne | 3029 | Don and Rother | RIVER DOVE | Not Applicable | Not Applicable | Not Applicable | 39:30 | 15 | 39 | 2020 | 93.67 |  |  | High spill threshold not met | High spill threshold not met | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS00868
YWS00869 | Yorkshire Water | Live | REETON TERRACE NO 1 CSO | REETON TERRACE/NO 1 CSO | C4963 | C4963 | A1 | SO on sewer network | SE8014771893 | 480147 | 471893 | GB104027068313 | Derwent from River Rye to Kirkham | River | 3311 | Middle Derwent Yorkshire | 3027 | Derwent Humber | PRIORPOT BECK | Not Applicable | Not Applicable | Not Applicable | 0:10 | 2 | 1.6 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00869
YWS00870 | Yorkshire Water | Live | REETON TERRACE NO 2 CSO | REETON TERRACE/NO 2 CSO | C4964 | C4964 | A1 | SO on sewer network | SE8012471888 | 480124 | 471888 | GB104027068313 | Derwent from River Rye to Kirkham | River | 3311 | Middle Derwent Yorkshire | 3027 | Derwent Humber | PRIORPOT BECK | Not Applicable | Not Applicable | Not Applicable | 0:48 | 3 | 2.75 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00870
YWS00871 | Yorkshire Water | Live | FARNLEY RING ROAD CSO | FARNLEY RING ROAD/CSO | C4966 | C4966 | A1 | SO on sewer network | SE2467533549 | 424675 | 433549 | GB104027062830 | Low/Wortley/Pudsey Bks | River | 3265 | Lower Aire | 3001 | Aire and Calder | FARNLEY BECK | Not Applicable | Not Applicable | Not Applicable | 54:15 | 26 | 29.8 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00871
YWS00872 | Yorkshire Water | Live | GLENHOLME ROAD CSO | GLENHOLME ROAD/CSO | C4967 | C4967 | 1 | SO on sewer network | SK4067085390 | 440785 | 385394 | GB104027057772 | Rother, Doe Lea to Don | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | TRIB OF SHIRTCLIFF BROOK | Not Applicable | Not Applicable | Not Applicable | 201:15 | 53 | 49 | 2020 | 100 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00872
YWS00873 | Yorkshire Water | Live | GRANVILLE ROAD CSO | GRANVILLE ROAD/CSO | C4968 | C4968 | A1 | SO on sewer network | SK3585086550 | 435851 | 386557 | GB104027057750 | Sheaf from Source to River Don | River | 3312 | Middle Don | 3029 | Don and Rother | RIVER SHEAF | Not Applicable | Not Applicable | Not Applicable | 43:30 | 26 | 25.2 | 2020 | 99.71 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00873
YWS00874 | Yorkshire Water | Live | THORNTON-LE-BEANS CSO | THORNTON LE BEANS/CSO | C5056 | C5056 | A1 | SO on sewer network | SE3966590312 | 439665 | 490312 | GB104027069450 | Otterington Beck catchment (trib of Wiske) | River | 3541 | Wiske | 3088 | Swale, Ure, Nidd and Upper Ouse | THORNTON LE BEANS BECK | Not Applicable | Not Applicable | Not Applicable | 34:45 | 17 | 13.2 | 2020 | 99.93 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00874
YWS00875 | Yorkshire Water | Live | ELLAND LANE CSO | ELLAND LANE/CSO | C5059 | C5059 | A1 | SO on sewer network | SE1109421538 | 411094 | 421538 | GB104027062642 | Calder from Ryburn Confluence to River Colne | River | 3310 | Middle Calder | 3001 | Aire and Calder | RIVER CALDER | Not Applicable | Not Applicable | Not Applicable | 3:45 | 5 | 4.6 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00875
YWS00876 | Yorkshire Water | Live | YORKSHIRE WATER FRIZLEY GARDENS BRA | FRIZLEY GARDENS/CSO | C5060 | C5060 | 1 | SO on sewer network | SE1541035920 | 415420 | 435900 | GB104027062862 | Bradford Beck (Clayton Bk to R Aire) | River | 3307 | Middle Aire | 3001 | Aire and Calder | BRADFORD BECK | Not Applicable | Not Applicable | Not Applicable | 39:15 | 29 | 27.4 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00876
YWS00877 | Yorkshire Water | Live | MORRISONS CAR PARK CSO | MORRISONS CAR PARK/CSO | C5094 | C5094 | A1 | SO on sewer network | SE2135223321 | 421352 | 423321 | GB104027062710 | Spen Beck from Source to River Calder | River | 3268 | Lower Calder | 3001 | Aire and Calder | RIVER SPEN | Not Applicable | Not Applicable | Not Applicable | 228:45 | 59 | 72 | 2020 | 84.49 | Comms failure / issue | Scheduled | High spill threshold not met | Not asset maintenance - Hydraulic capacity | No investigation activity in reporting period | No improvement action in reporting period | SOAF investigation completed - No work required | YWS00877
YWS00878 | Yorkshire Water | Live | YORKSHIRE WATER CHURWELL SURFACE W | WESTWOODSIDE/CSO | C5254 | C5254 | 1 | Inlet SO at WwTW | SE4260042900 | 426996 | 430140 | GB104027062750 | Milshaw Beck from Source to Low/Wortley/Pudsey Bks | River | 3265 | Lower Aire | 3001 | Aire and Calder | FARNLEY WOOD BECK | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00878
YWS00879 | Yorkshire Water | Live | GREEN SPRING AVENUE CSO | GREENSPRING AVENUE/CSO | C5340 | C5340 | A1 | SO on sewer network | SE3487501884 | 434875 | 401884 | GB104027057510 | Dove from Source to River Dearne | River | 3125 | Dearne | 3029 | Don and Rother | TRIBUTARY OF SHORT WOOD DIKE | Not Applicable | Not Applicable | Not Applicable | 10:15 | 11 | 25.8 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00879
YWS00880 | Yorkshire Water | Live | SCROOBY STREET CSO | SCROOBY STREET/CSO | C5341 | C5341 | A1 | SO on sewer network | SK4275095420 | 442758 | 395426 | GB104027057420 | Greasbrough Dike from Source to River Don | River | 3312 | Middle Don | 3029 | Don and Rother | GREASBROUGH DYKE | Not Applicable | Not Applicable | Not Applicable | 269:15 | 58 | 50.4 | 2020 | 99.55 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement completed | SOAF investigation ongoing | YWS00880
YWS00881 | Yorkshire Water | Live | WEST BRETTON STW | WEST BRETTON/NO 2 STW | C5412 | C5412 | 2 | Storm tank at WwTW | SE2916013280 | 429150 | 413300 | GB104027063260 | Dearne from Bentley Brook to Cawthorne Dyke | River | 3125 | Dearne | 3029 | Don and Rother | BRETTON BROOK | Not Applicable | Not Applicable | Not Applicable | 884:15 | 78 | 91.8 | 2020 | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00881
YWS00882 | Yorkshire Water | Live | LOW LANE CSO | LOW LANE/CSO | C5413 | C5413 | A1 | SO on sewer network | SE2522038050 | 425228 | 438049 | GB104027062920 | Carlton Beck from Source to River Aire | River | 3265 | Lower Aire | 3001 | Aire and Calder | OIL MILL BECK | Not Applicable | Not Applicable | Not Applicable | 37:45 | 23 | 4.6 | 2020 | 54.61 | Sensor failure / issue | Resolved - Jul | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00882
YWS00883 | Yorkshire Water | Live | YORKSHIRE WATER HORSFORTH TRANSFER | HORSFORTH AGY/CSO | C5440 | C5440 | 1 | SO on sewer network | SE2456036980 | 424548 | 436983 | GB104027062920 | Carlton Beck from Source to River Aire | River | 3265 | Lower Aire | 3001 | Aire and Calder | COW BECK | Not Applicable | Not Applicable | Not Applicable | 76:45 | 47 | 49.2 | 2020 | 100 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00883
YWS00884 | Yorkshire Water | Live | OWLER LANE CSO | OWLER LANE/CSO | C5538 | C5538 | A1 | SO on sewer network | SK3730090210 | 437301 | 390218 | GB104027057412 | Don from River Loxley confl to River Don Works | River | 3312 | Middle Don | 3029 | Don and Rother | BAGLEY DYKE | Not Applicable | Not Applicable | Not Applicable | 236:45 | 62 | 61.4 | 2020 | 99.96 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00884
YWS00885 | Yorkshire Water | Live | GREENGATES LANE CSO | GREENGATE LANE/CSO | C5604 | C5604 | A1 | SO on sewer network | SK4376084575 | 443760 | 384575 | GB104027057773 | Shire Brook | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | TRIBUTARY OF THE RIVER ROTHER | Not Applicable | Not Applicable | Not Applicable | 7:45 | 8 | 9.2 | 2020 | 98.9 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00885
YWS00886 | Yorkshire Water | Live | GENN LANE CSO | GENN LANE/CSO | C5710 | C5710 | A1 | SO on sewer network | SE3453004400 | 434531 | 404398 | GB104027057520 | Dodworth Dyke from Source to River Dove | River | 3125 | Dearne | 3029 | Don and Rother | TRIB OF WORSBOROUGH RESERVOIR | Not Applicable | Not Applicable | Not Applicable | 79:30 | 32 | 37 | 2020 | 93.53 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00886
YWS00887 | Yorkshire Water | Live | RAMSKIR LANE NO 2 CSO | RAMSKIR LANE/NO 2 CSO | DT/2662 | DT/2662 | A1 | SO on sewer network | SE6473612031 | 464736 | 412031 | GB104028064350 | North Soak Drain Catchment (trib of Torne/Three Rivers) | River | 3234 | Isle of Axholme | 3041 | Idle and Torne | STAINFORTH DRAIN (DITCH) | Not Applicable | Not Applicable | Not Applicable | 2:45 | 4 | 6.2 | 2020 | 99.93 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00887
YWS00888 | Yorkshire Water | Live | LUNDWOOD WWTW | LUNDWOOD/STW | E10 | E10 | A2 | Storm tank at WwTW | SE3783006800 | 437940 | 406610 | GB104027063171 | Dearne from Cawthorne Dyke to Lundwood STW | River | 3125 | Dearne | 3029 | Don and Rother | RIVER DEARNE & CLIFFE BDG DYKE | Not Applicable | Not Applicable | Not Applicable | 979:45 | 88 | 69.2 | 2020 | 99.75 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00888
YWS00889 | Yorkshire Water | Live | MITCHELL LAITHES WWTW | DEWSBURY/STW/3XDWF OVERFLOW | E15 | E15 | 2 | Storm tank at WwTW | SE2646019490 | 426460 | 419490 | GB104027062631 | Calder from River Colne to River Chald | River | 3268 | Lower Calder | 3001 | Aire and Calder | RIVER CALDER | Not Applicable | Not Applicable | Not Applicable | 440:15 | 63 | 60.2 | 2020 | 99.63 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement completed | SOAF investigation ongoing | YWS00889
YWS00890 | Yorkshire Water | Live | MITCHELL LAITHES WWTW | DEWSBURY/STW/6XDWF OVERFLOW | E15 | E15 | 3 | Inlet SO at WwTW | SE2646019490 | 426460 | 419490 | GB104027062631 | Calder from River Colne to River Chald | River | 3268 | Lower Calder | 3001 | Aire and Calder | RIVER CALDER | Not Applicable | Not Applicable | Not Applicable | 65:00 | 12 | 30 | 2020 | 79.92 | Installation set-up/design issue | Resolved - Mar | High spill threshold not met | High spill threshold not met | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS00890
YWS00891 | Yorkshire Water | Live | RAWDON TRANSFER SPS | RAWDON/CSO | E152 | E152 | A1 | Storm discharge at pumping station | SE2123037870 | 421236 | 437871 | GB104027063032 | Aire from Gill Beck (Baildon) to River Calder | River | 3265 | Lower Aire | 3001 | Aire and Calder | RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 1038:45 | 69 | 81.8 | 2020 | 72.68 | Power failure / issue | Resolved - Jun | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS00891
YWS00892 | Yorkshire Water | Live | RAWDON TRANSFER SPS | RAWDON/CSO | E152 | E152 | A2 | Storm discharge at pumping station | SE2123037870 | 421236 | 437871 | GB104027063032 | Aire from Gill Beck (Baildon) to River Calder | River | 3265 | Lower Aire | 3001 | Aire and Calder | RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 173:30 | 33 | 49 | 2023 | 72.68 | Power failure / issue | Resolved - Jun | High spill threshold not met | High spill threshold not met | Operational investigation completed | No improvement action in reporting period | No SOAF investigation required | YWS00892
YWS00893 | Yorkshire Water | Live | BURLEY/MENSTON (SHEFFIELD) STW | BURLEY IN WHARFEDALE/STW | E164 | E164 | A2 | Storm tank at WwTW | SE1860045900 | 418410 | 446040 | GB104027064258 | Wharfe from Hundwith Beck to River Washburn | River | 3318 | Middle Wharfe and Washburn | 3115 | Wharfe and Lower Ouse | RIVER WHARFE | Not Applicable | Not Applicable | Not Applicable | 1951:00 | 126 | 105 | 2020 | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS00893
YWS00894 | Yorkshire Water | Live | LEE LANE STW | LEE LANE/STW | E18 | E18 | A2 | Inlet SO at WwTW | SE0971027440 | 409710 | 427440 | GB104027062720 | Red Beck, Source to Calder and Hebble Navigation | River | 3310 | Middle Calder | 3001 | Aire and Calder | TRIBUTARY OF SHIBDEN BECK | Not Applicable | Not Applicable | Not Applicable | 150:45 | 43 | 68.2 | 2020 | 99.99 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | Operational investigation completed | Operational improvement ongoing | SOAF investigation completed - No work required | YWS00894
YWS00895 | Yorkshire Water | Live | MALLYAN SPOUT CSO | MALLYAN SPOUT/CSO | EPRLB3596RC | EPR/LB3596RC | A1 | SO on sewer network | NZ8263000739 | 482630 | 500739 | GB104027068030 | Murk Esk from Wheeldale Gill to Eller Beck | River | 3177 | Esk | 3037 | Esk and Coast | TRIBUTARY OF WEST BECK | Not Applicable | Not Applicable | Not Applicable | 5:00 | 2 | 6.2 | 2020 | 99.83 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00895
YWS00896 | Yorkshire Water | Live | BAILIFF BRIDGE CSO | BROOKFOOT MILLS/CSO | E2 | E2 | 10 | SO on sewer network | SE1362123416 | 413621 | 423416 | GB104027062720 | Red Beck, Source to Calder and Hebble Navigation | River | 3310 | Middle Calder | 3001 | Aire and Calder | WYKE BECK | Not Applicable | Not Applicable | Not Applicable | 144:30 | 50 | 37.8 | 2020 | 91.55 |  |  | High spill threshold not met | High spill threshold not met | Operational investigation completed | No improvement action in reporting period | No SOAF investigation required | YWS00896
YWS00897 | Yorkshire Water | Live | BAILIFF BRIDGE CSO | SYKE LANE/CSO | E2 | E2 | 15 | SO on sewer network | SE1326326076 | 413263 | 426076 | GB104027062700 | Clifton Beck from Source to River Calder | River | 3310 | Middle Calder | 3001 | Aire and Calder | WYKE BECK | Not Applicable | Not Applicable | Not Applicable | 78:30 | 45 | 118.4 | 2020 | 99.89 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | Operational investigation completed | Operational improvement ongoing | SOAF investigation completed - Work required | YWS00897
YWS00898 | Yorkshire Water | Live | BAILIFF BRIDGE CSO | BOROUGH BOUNDARY/CSO | E2 | E2 | 5 | SO on sewer network | SE1466925807 | 414669 | 425807 | GB104027062700 | Clifton Beck from Source to River Calder | River | 3310 | Middle Calder | 3001 | Aire and Calder | WYKE BECK | Not Applicable | Not Applicable | Not Applicable | 19:15 | 19 | 16 | 2020 | 94.35 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00898
YWS00899 | Yorkshire Water | Live | COLEY BECK CSO | COLEY BECK/CSO | Not matched in Consents Database | EPR/AP3829PK | A1 | SO on sewer network | SE1382626283 | 413826 | 426283 | GB104027062700 | Clifton Beck from Source to River Calder | River | 3310 | Middle Calder | 3001 | Aire and Calder | WYKE BECK | Not Applicable | Not Applicable | Not Applicable | 150:00 | 50 | 49.4 | 2020 | 99.99 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement ongoing | SOAF investigation ongoing | YWS00899
YWS00900 | Yorkshire Water | Live | BAILIFF BRIDGE CSO | HALIFAX OLD ROAD/CSO | Not matched in Consents Database | EPR/AP3920PV | A1 | SO on sewer network | SE1147425554 | 411474 | 425554 | GB104027062720 | Red Beck, Source to Calder and Hebble Navigation | River | 3310 | Middle Calder | 3001 | Aire and Calder | WYKE BECK | Not Applicable | Not Applicable | Not Applicable | 133:30 | 42 | 35.4 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00900
YWS00901 | Yorkshire Water | Live | BLACKBURN MEADOWS WASTEWATER WORKS | BLACKBURN MEADOWS/STW | E25 | E25 | A2 | Storm tank at WwTW | SK4051092000 | 440510 | 392000 | GB104027057413 | Don from River Don Works to River Rother | River | 3312 | Middle Don | 3029 | Don and Rother | RIVER DON | Not Applicable | Not Applicable | Not Applicable | 913:15 | 64 | 64.2 | 2020 | 100 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00901
YWS00902 | Yorkshire Water | Live | BLACKBURN MEADOWS WASTEWATER WORKS | BLACKBURN MEADOWS/STW | E25 | E25 | A3 | Inlet SO at WwTW | SK4025092110 | 440250 | 392110 | GB104027057452 | Don from River Rother to River Dearne | River | 3312 | Middle Don | 3029 | Don and Rother | RIVER DON | Not Applicable | Not Applicable | Not Applicable | 344:30 | 33 | 32.6 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00902
YWS00903 | Yorkshire Water | Live | STOCKLEY WWTW | STOCKLEY/STW | E280 | E280 | A2 | Storm tank at WwTW | SK4592067970 | 445920 | 367970 | GB104027057290 | Doe Lea from Source to Hawke Brook | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | RIVER DOE LEA | Not Applicable | Not Applicable | Not Applicable | 570:30 | 62 | 74 | 2020 | 99.95 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS00903
YWS00904 | Yorkshire Water | Live | DARFIELD WWTW | DARFIELD/NO 2 STW | E281 | E281 | A2 | Storm tank at WwTW | SE4196303817 | 441960 | 403820 | GB104027063172 | Dearne from Lundwood to River Dove | River | 3125 | Dearne | 3029 | Don and Rother | RIVER DEARNE | Not Applicable | Not Applicable | Not Applicable | 226:00 | 46 | 43 | 2020 | 99.62 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00904
YWS00906 | Yorkshire Water | Live | TEMPLE NORMANTON STW | TEMPLE NORMANTON/STW | E294 | E294 | 2 | Storm tank at WwTW | SK4223067690 | 442230 | 367690 | GB104027057640 | Spital/Calow/Muster Brook | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | MUSTER BROOK | Not Applicable | Not Applicable | Not Applicable | 225:45 | 59 | 80.6 | 2020 | 99.99 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement ongoing | SOAF investigation ongoing | YWS00906
YWS00908 | Yorkshire Water | Live | CARLISLE STREET 129 CSO | CARLISLE STREET 129/CSO | E4 | E4 | A1 | SO on sewer network | SK3743789533 | 437437 | 389533 | GB104027057412 | Don from River Loxley confl to River Don Works | River | 3312 | Middle Don | 3029 | Don and Rother | DUKE OF NORFOLK'S CULVERT | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0 | 2020 | 15.36 | Comms failure / issue | Scheduled | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00908
YWS00909 | Yorkshire Water | Live | CARLISLE STREET 129 CSO | CARLISLE STREET EAST/CSO | E4 | E4 | 2 | SO on sewer network | SK3743789533 | 438818 | 390505 | GB104027057360 | Car Brook from Source to River Don | River | 3312 | Middle Don | 3029 | Don and Rother | DUKE OF NORFOLK'S CULVERT | Not Applicable | Not Applicable | Not Applicable | 1:45 | 6 | 5.8 | 2020 | 99.42 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00909
YWS00910 | Yorkshire Water | Live | EASTWOOD WWTW | EASTWOOD/STW | E61 | E61 | A2 | Storm tank at WwTW | SD9716026380 | 397180 | 426460 | GB104027062650 | Calder from Walsden Water to Colden Water | River | 3487 | Upper Calder | 3001 | Aire and Calder | RIVER CALDER | Not Applicable | Not Applicable | Not Applicable | 1980:45 | 138 | 136.8 | 2020 | 99.39 |  |  | Performance - Infiltration | Performance - Infiltration | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS00910
YWS00911 | Yorkshire Water | Permit Application Submitted | TBC When Permit Issued | OSWALDKIRK/STW | Permit applied for | E619(SS) | TBC | Inlet SO at WwTW | SE6220078800 | 462300 | 478600 | GB104027068420 | Holbeck from Source to Wath Beck | River | 3387 | Rye | 3027 | Derwent Humber | TRIB OF HOLBECK | Not Applicable | Not Applicable | Not Applicable | 1274:30 | 166 | 100.6 | 2020 | 99.84 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation ongoing | Operational improvement ongoing | SOAF investigation ongoing | YWS00911
YWS00912 | Yorkshire Water | Live | HARLEY STW | HARLEY/STW | E620(SS) | E620(SS) | A2 | Storm tank at WwTW | SK3727098360 | 437170 | 398360 | GB104027057470 | Knoll Beck from Source to River Dearne | River | 3125 | Dearne | 3029 | Don and Rother | HARLEY DIKE | Not Applicable | Not Applicable | Not Applicable | 233:00 | 42 | 40.2 | 2020 | 99.89 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00912
YWS00913 | Yorkshire Water | Permit Application Submitted | TBC When Permit Issued | WESTOW/STW | Permit applied for | E679(SS) | TBC | Storm tank at WwTW | SE7580065400 | 476600 | 465500 | GB104027068313 | Derwent from River Rye to Kirkham | River | 3311 | Middle Derwent Yorkshire | 3027 | Derwent Humber | HOWL BECK | Not Applicable | Not Applicable | Not Applicable | 2624:00 | 142 | 82.4 | 2020 | 99.96 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement ongoing | SOAF investigation ongoing | YWS00913
YWS00915 | Yorkshire Water | Live | TANKERSLEY SEWAGE TREATMENT WORKS | TANKERSLEY/STW/3XDWF OVERFLOW | E698(SS) | E698(SS) | A2 | Storm tank at WwTW | SE3426900791 | 434269 | 400791 | GB104027057480 | Rockley Dike from Source to River Dove | River | 3125 | Dearne | 3029 | Don and Rother | BIRDWELL DYKE | Not Applicable | Not Applicable | Not Applicable | 2191:45 | 165 | 127.6 | 2020 | 99.87 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS00915
YWS00916 | Yorkshire Water | Live | WENTWORTH STW | WENTWORTH/STW | E702(SS) | E702(SS) | A2 | Storm tank at WwTW | SK3797098910 | 437970 | 398910 | GB104027057470 | Knoll Beck from Source to River Dearne | River | 3125 | Dearne | 3029 | Don and Rother | UNNAMED TRIB. OF HARLEY DYKE | Not Applicable | Not Applicable | Not Applicable | 3553:00 | 191 | 175.8 | 2020 | 99.93 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS00916
YWS00917 | Yorkshire Water | Live | WHARNCLIFFE SIDE STW | WHARNCLIFFE SIDE/STW | E704(SS) | E704(SS) | A2 | Storm tank at WwTW | SK2997094440 | 429970 | 394440 | GB104027057411 | Don from Little Don to River Loxley confluence | River | 3490 | Upper Don | 3029 | Don and Rother | RIVER DON | Not Applicable | Not Applicable | Not Applicable | 853:30 | 114 | 99.4 | 2020 | 99.97 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement ongoing | SOAF investigation ongoing | YWS00917
YWS00918 | Yorkshire Water | Live | OXENHOPE NO.2 WWTW | OXENHOPE/NO 2 STW | E721(SS) | E721(SS) | A2 | Storm tank at WwTW | SE0355035670 | 403550 | 435680 | GB104027064200 | Bridgehouse Beck from Source to River Worth | River | 3307 | Middle Aire | 3001 | Aire and Calder | BRIDGE HOUSE BECK | Not Applicable | Not Applicable | Not Applicable | 1124:30 | 118 | 93.4 | 2020 | 99.96 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation ongoing | Operational improvement ongoing | SOAF investigation ongoing | YWS00918
YWS00919 | Yorkshire Water | Live | DENABY NO 2 STW | DENABY/NO 2 STW | E728(SS) | E728(SS) | A2 | Storm tank at WwTW | SK4946099920 | 449460 | 399920 | GB104027057452 | Don from River Rother to River Dearne | River | 3312 | Middle Don | 3029 | Don and Rother | RIVER DON | Not Applicable | Not Applicable | Not Applicable | 252:11 | 46 | 46.8 | 2020 | 97.42 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00919
YWS00920 | Yorkshire Water | Live | KIRK SMEATON STW | KIRK SMEATON/STW | E730 | E730(SS) | 2 | Storm tank at WwTW | SE5337016000 | 453370 | 416000 | GB104027063360 | Went from Hoyle Mill Stream to Blowell Drain | River | 3272 | Lower Don | 3029 | Don and Rother | RIVER WENT | Not Applicable | Not Applicable | Not Applicable | 672:30 | 42 | 27.2 | 2020 | 99.49 |  |  | High spill threshold not met | High spill threshold not met | Operational investigation completed | No improvement action in reporting period | No SOAF investigation required | YWS00920
YWS00921 | Yorkshire Water | Live | FITZWILLIAM SPS | FITZWILLIAM/CSO | E735(SS) | E735 | A1 | Storm discharge at pumping station | SE4193816408 | 441938 | 416408 | GB104027063380 | Went from Source to Hoyle Mill Stream | River | 3272 | Lower Don | 3029 | Don and Rother | HESSLE BECK | Not Applicable | Not Applicable | Not Applicable | 848:15 | 58 | 54.4 | 2020 | 100 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement ongoing | SOAF investigation ongoing | YWS00921
YWS00922 | Yorkshire Water | Live | REDACRE NO 2 STW | REDACRE/NO 2 STW/3XDWF OVERFLOW | E740(SS) | E740(SS) | A2 | Storm tank at WwTW | SE0102026180 | 401020 | 426180 | GB104027062641 | Calder from Colden Water to Ryburn Confluence | River | 3310 | Middle Calder | 3001 | Aire and Calder | RIVER CALDER | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 3 | 2020 | 99.76 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00922
YWS00923 | Yorkshire Water | Live | RIPPONDEN STW | RIPPONDEN/STW/3XDWF OVERFLOW | E741(SS) | E741(SS) | A2 | Storm tank at WwTW | SE0452020540 | 404520 | 420540 | GB104027062580 | Ryburn from Booth Dean Clough to R Calder | River | 3310 | Middle Calder | 3001 | Aire and Calder | RIVER RYBURN | Not Applicable | Not Applicable | Not Applicable | 478:30 | 80 | 210.25 | 2020 | 100 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS00923
YWS00925 | Yorkshire Water | Live | STANLEY STW | STANLEY/STW | E743(SS) | E743(SS) | A2 | Storm tank at WwTW | SE3523023920 | 435230 | 423920 | GB104027062632 | Calder from River Chald to River Aire | River | 3268 | Lower Calder | 3001 | Aire and Calder | RIVER CALDER & BRAMLEY'S BECK | Not Applicable | Not Applicable | Not Applicable | 407:15 | 44 | 65 | 2020 | 99.99 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS00925
YWS00926 | Yorkshire Water | Live | STANLEY STW | STANLEY/STW | E743(SS) | E743(SS) | A3 | Inlet SO at WwTW | SE3528023900 | 435280 | 423890 | GB104027062632 | Calder from River Chald to River Aire | River | 3268 | Lower Calder | 3001 | Aire and Calder | RIVER CALDER & BRAMLEY'S BECK | Not Applicable | Not Applicable | Not Applicable | 134:15 | 48 | 31.4 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00926
YWS00927 | Yorkshire Water | Live | WRANGBROOK STW | UPTON WRANGBROOK/STW/3XDWF OVERFLOW | E744 | E744 | A2 | Storm tank at WwTW | SE4959012540 | 449590 | 412540 | GB104027063280 | The Skell from Source to Ea Beck | River | 3272 | Lower Don | 3029 | Don and Rother | THE SKELL (WRANGBROOK DYKE) | Not Applicable | Not Applicable | Not Applicable | 330:45 | 31 | 40.6 | 2020 | 99.96 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00927
YWS00928 | Yorkshire Water | Live | RAVENFIELD VILLAGE STW | RAVENFIELD/STW | E756(SS) | E756 | 2 | Inlet SO at WwTW | SK4852095380 | 448510 | 395350 | GB104027057430 | Hooton Brook from Source to River Don | River | 3312 | Middle Don | 3029 | Don and Rother | TRIB OF HOOTON BROOK | Not Applicable | Not Applicable | Not Applicable | 1011:45 | 115 | 155.6 | 2020 | 99.81 |  |  | Performance - Infiltration | Performance - Infiltration | UWWTR investigation ongoing, Operational investigation ongoing | Operational improvement ongoing | SOAF investigation ongoing | YWS00928
YWS00929 | Yorkshire Water | Live | LONG MARSTON WPC WORKS STORM TANKS | LONG MARSTON/STW | E799 | E799(SS) | A2 | Storm tank at WwTW | SE5090051100 | 451610 | 451560 | GB104027063730 | The Foss | River | 3499 | Upper Ouse Yorkshire | 3088 | Swale, Ure, Nidd and Upper Ouse | MOOR DRAIN | Not Applicable | Not Applicable | Not Applicable | 1615:45 | 126 | 82.6 | 2020 | 100 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation ongoing | Operational improvement ongoing | SOAF investigation ongoing | YWS00929
YWS00930 | Yorkshire Water | Live | BELGRAVE ROAD BRIDGE CSO | BELGRAVE RD BRID/CSO | EPRAB3895RU | EPR/AB3895RU | A1 | SO on sewer network | TA1888065320 | 518880 | 465320 | GB640402491000 | Yorkshire South | Coastal Water | 3179 | Esk TraC | 3040 | Humber TraC | NORTH SEA | Not Applicable | Bridlington South Beach | Not Applicable | 71:34 | 34 | 7 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00930
YWS00931 | Yorkshire Water | Live | HILDERTHORPE ROAD CSO | HILDERTHORPE ROAD/CSO | EPRBB3194WR | EPR/BB3194WR | A1 | SO on sewer network | TA1888065320 | 518880 | 465320 | GB640402491000 | Yorkshire South | Coastal Water | 3179 | Esk TraC | 3040 | Humber TraC | NORTH SEA | Not Applicable | Bridlington South Beach | Not Applicable | 20:54 | 14 | 12.8 | 2020 | 99.97 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00931
YWS00932 | Yorkshire Water | Live | ABBEYDALE ROAD 62 NO2 CSO | ABBEYDALE ROAD 62/2 CSO | EPRCB3597EV | EPR/CB3597EV | A1 | SO on sewer network | SK3444284447 | 434439 | 384451 | GB104027057750 | Sheaf from Source to River Don | River | 3312 | Middle Don | 3029 | Don and Rother | RIVER SHEAF | Not Applicable | Not Applicable | Not Applicable | 64:45 | 10 | 15 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00932
YWS00933 | Yorkshire Water | Live | CUDDY BROWN CLOSE CSO | CUDDY BROWN CLOSE/CSO | EPRCB3597NB | EPR/CB3597NB | A1 | SO on sewer network | SE8056483368 | 480564 | 483368 | GB104027068460 | The Syme form Source to Thornton | River | 3489 | Upper Derwent Yorkshire | 3027 | Derwent Humber | TRIBUTARY OF THORNTON BECK | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 7.8 | 2020 | 99.95 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00933
YWS00934 | Yorkshire Water | Live | GLEADLESS ROAD HEELEY | GLEADLESS ROAD HEELEY/CSO | EPRCB3597RU | EPR/CB3597RU | A1 | SO on sewer network | SK3527085193 | 435270 | 385193 | GB104027057750 | Sheaf from Source to River Don | River | 3312 | Middle Don | 3029 | Don and Rother | RIVER SHEAF | Not Applicable | Not Applicable | Not Applicable | 0:30 | 2 | 2 | 2020 | 99.8 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00934
YWS00935 | Yorkshire Water | Live | HARLINGTON ROAD CSO | HARLINGTON ROAD/CSO | EPRCB3598AN | EPR/CB3598AN | A1 | SO on sewer network | SE4908401345 | 449084 | 401345 | GB104027063173 | Dearne Darfield STW to River Don | River | 3125 | Dearne | 3029 | Don and Rother | RIVER DEARNE | Not Applicable | Not Applicable | Not Applicable | 16:30 | 21 | 5.8 | 2020 | 99.68 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00935
YWS00936 | Yorkshire Water | Live | RAVENS HUDDERSFIELD RD CSO | RAVENS HUDDFLD RD/CSO | EPRCB3598RG | EPR/CB3598RG | A1 | SO on sewer network | SE2401320952 | 424013 | 420952 | GB104027062631 | Calder from River Colne to River Chald | River | 3268 | Lower Calder | 3001 | Aire and Calder | RIVER CALDER | Not Applicable | Not Applicable | Not Applicable | 86:30 | 26 | 27.4 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00936
YWS00937 | Yorkshire Water | Live | EFFINGHAM ROAD CSO | EFFINGHAM ROAD/CSO | EPRCB3892VU | EPR/CB3892VU | A1 | SO on sewer network | SK3729588270 | 437295 | 388270 | GB104027057412 | Don from River Loxley confl to River Don Works | River | 3312 | Middle Don | 3029 | Don and Rother | RIVER DON | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0 | 2020 | 99.77 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00937
YWS00938 | Yorkshire Water | Live | KIRK LANE NO 2 CSO | KIRK LANE/NO 2 CSO | EPRCB3892WX | EPR/CB3892WX | A1 | SO on sewer network | SE1956041349 | 419560 | 441349 | GB104027062910 | Gill Beck Guisley from Source to River Aire | River | 3265 | Lower Aire | 3001 | Aire and Calder | NUN ROYD BECK | Not Applicable | Not Applicable | Not Applicable | 0:45 | 2 | 1.6 | 2020 | 85.51 | Comms failure / issue | Resolved - Feb | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00938
YWS00939 | Yorkshire Water | Live | SKINNER LANE CSO | SKINNER LANE/CSO | EPRCB3893AH | EPR/CB3893AH | A1 | SO on sewer network | SE3091933975 | 430919 | 433975 | GB104027062900 | Meanwood Beck from Source to River Aire | River | 3265 | Lower Aire | 3001 | Aire and Calder | LADY BECK | Not Applicable | Not Applicable | Not Applicable | 16:30 | 8 | 12 | 2020 | 99.98 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00939
YWS00940 | Yorkshire Water | Live | ALMA STREET SHEFFIELD CSO | ALMA STREET SHEFFIELD/CSO | EPRDP3024GP | EPR/DP3024GP | A1 | SO on sewer network | SK3545288131 | 435452 | 388131 | GB104027057412 | Don from River Loxley confl to River Don Works | River | 3312 | Middle Don | 3029 | Don and Rother | RIVER DON | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00940
YWS00941 | Yorkshire Water | Live | INNFOLD FARM 3 NO 2 CSO | INNFOLD FARM 3/NO 2 CSO | EPREP3224XJ | EPR/EP3224XJ | A1 | SO on sewer network | SE2890213651 | 428902 | 413651 | GB104027063260 | Dearne from Bentley Brook to Cawthorne Dyke | River | 3125 | Dearne | 3029 | Don and Rother | BRETTON BROOK | Not Applicable | Not Applicable | Not Applicable | 5:00 | 3 | 3.4 | 2020 | 98.79 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00941
YWS00942 | Yorkshire Water | Live | BROADWAY STATION CSO | BROADWAY STATION RD/CSO | EPREP3225GG | EPR/EP3225GG | A1 | Storm discharge at pumping station | SE6499012610 | 464990 | 412610 | GB104027064243 | Don from Mill Dyke to River Ouse | River | 3272 | Lower Don | 3029 | Don and Rother | RIVER DON | Not Applicable | Not Applicable | Not Applicable | 1:45 | 1 | 4 | 2020 | 98.93 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00942
YWS00943 | Yorkshire Water | Live | BROADWAY STATION CSO | BROADWAY 35/CSO | EPREP3225GG | EPR/RB3796AU | A1 | Storm discharge at pumping station | SE6499012610 | 464990 | 412610 | GB104027064243 | Don from Mill Dyke to River Ouse | River | 3272 | Lower Don | 3029 | Don and Rother | RIVER DON | Not Applicable | Not Applicable | Not Applicable | 237:00 | 66 | 52.4 | 2020 | 95.38 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS00943
YWS00944 | Yorkshire Water | Live | BROADWAY STATION CSO | BROADWAY 62/CSO | EPREP3225GG | EPR/RB3796ET | A1 | Storm discharge at pumping station | SE6499012610 | 464990 | 412610 | GB104027064243 | Don from Mill Dyke to River Ouse | River | 3272 | Lower Don | 3029 | Don and Rother | RIVER DON | Not Applicable | Not Applicable | Not Applicable | 56:45 | 30 | 39.8 | 2020 | 99.93 |  |  | High spill threshold not met | High spill threshold not met | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00944
YWS00945 | Yorkshire Water | Live | BROADWAY STATION CSO | BEECHFIELD ROAD/CSO | EPREP3225GG | EPR/RB3796NA | A1 | Storm discharge at pumping station | SE6499012610 | 464990 | 412610 | GB104027064243 | Don from Mill Dyke to River Ouse | River | 3272 | Lower Don | 3029 | Don and Rother | RIVER DON | Not Applicable | Not Applicable | Not Applicable | 135:15 | 32 | 23 | 2020 | 99.82 |  |  | High spill threshold not met | High spill threshold not met | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00945
YWS00946 | Yorkshire Water | Live | BROADWAY STATION CSO | BROADWAY XXX/CSO | EPREP3225GG | EPR/RB3796RJ | A1 | Storm discharge at pumping station | SE6499012610 | 464990 | 412610 | GB104027064243 | Don from Mill Dyke to River Ouse | River | 3272 | Lower Don | 3029 | Don and Rother | RIVER DON | Not Applicable | Not Applicable | Not Applicable | 1:30 | 5 | 8.4 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00946
YWS00947 | Yorkshire Water | Live | BROADWAY STATION CSO | BROADWAY XXX/CSO | EPREP3225GG | EPR/RB3796VS | A1 | Storm discharge at pumping station | SE6499012610 | 464990 | 412610 | GB104027064243 | Don from Mill Dyke to River Ouse | River | 3272 | Lower Don | 3029 | Don and Rother | RIVER DON | Not Applicable | Not Applicable | Not Applicable | 46:15 | 24 | 5.2 | 2020 | 56.58 | Sensor failure / issue | Resolved - Jul | High spill threshold not met | High spill threshold not met | Operational investigation completed | Operational improvement completed | No SOAF investigation required | YWS00947
YWS00948 | Yorkshire Water | Live | BROADWAY STATION CSO | BROADWAY 248/CSO | EPREP3225GG | EPR/RB3796WL | A1 | Storm discharge at pumping station | SE6499012610 | 464990 | 412610 | GB104027064243 | Don from Mill Dyke to River Ouse | River | 3272 | Lower Don | 3029 | Don and Rother | RIVER DON | Not Applicable | Not Applicable | Not Applicable | 108:00 | 25 | 22.6 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00948
YWS00949 | Yorkshire Water | Live | BROADWAY STATION CSO | BROADWAY 374/CSO | EPREP3225GG | EPR/RB3797AG | A1 | Storm discharge at pumping station | SE6499012610 | 464990 | 412610 | GB104027064243 | Don from Mill Dyke to River Ouse | River | 3272 | Lower Don | 3029 | Don and Rother | RIVER DON | Not Applicable | Not Applicable | Not Applicable | 0:30 | 1 | 47.8 | 2020 | 99.58 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS00949
YWS00950 | Yorkshire Water | Live | GREEN BROOK PLACE CSO | GREEN BROOK PLACE/CSO | EPREP3225XP | EPR/EP3225XP | A1 | SO on sewer network | SE2498502799 | 424985 | 402799 | GB104027057490 | Don from Scout Dyke to the Little Don | River | 3490 | Upper Don | 3029 | Don and Rother | CUBLEY BROOK | Not Applicable | Not Applicable | Not Applicable | 5:15 | 4 | 3.2 | 2020 | 99.96 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00950
YWS00951 | Yorkshire Water | Live | SMITHS SQUARE CSO | SMITHS SQUARE/CSO | EPRFB3792NJ | EPR/FB3792NJ | A1 | SO on sewer network | SE5535301396 | 455353 | 401396 | GB104027064242 | Don from River Dearne to Mill Dyke | River | 3312 | Middle Don | 3029 | Don and Rother | RIVER DON | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0.2 | 2020 | 99.98 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00951
YWS00952 | Yorkshire Water | Live | BRAMSTON STREET CSO | BRAMSTON STREET/CSO | EPRFB3895WE | EPR/FB3895WE | A1 | SO on sewer network | SE1448822546 | 414488 | 422546 | GB104027062642 | Calder from Ryburn Confluence to River Colne | River | 3310 | Middle Calder | 3001 | Aire and Calder | RIVER CALDER | Not Applicable | Not Applicable | Not Applicable | 54:22 | 35 | 53.2 | 2020 | 45.08 | Comms failure / issue | Resolved - January after reporting year | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00952
YWS00953 | Yorkshire Water | Live | DYEHOUSE LANE CSO | DYHOUSE LANE/CSO | EPRFB3896AR | EPR/FB3896AR | A1 | SO on sewer network | SE1499722533 | 414997 | 422533 | GB104027062642 | Calder from Ryburn Confluence to River Colne | River | 3310 | Middle Calder | 3001 | Aire and Calder | RIVER CALDER | Not Applicable | Not Applicable | Not Applicable | 7:22 | 27 | 16.4 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00953
YWS00954 | Yorkshire Water | Live | Boundary Avenue Combined Sewer Overflow* | BOUNDARY AVENUE/CSO | Not matched in Consents Database | EPR/HB3892EW | A1 | SO on sewer network | SE59810617 | 459810 | 406170 | GB70410281 | Sheffield and South Yorkshire Navigation (New Junction and Stainforth and Keadby | Canal | 2018 | Don and Rother Canals | 2001 | Humber AWB | Not matched in EA Consents Database | Not Applicable | Not Applicable | Not Applicable | 3:15 | 8 | 3.4 | 2020 | 99.9 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00954
YWS00955 | Yorkshire Water | Live | NEW MILL LIBRARY CSO | NEW MILL LIBRARY/CSO | EPRHB3892NS | EPR/HB3892NS | A1 | SO on sewer network | SE1625008918 | 416250 | 408918 | GB104027057610 | New Mill Dike from Source to River Holme | River | 3097 | Colne and Holme | 3001 | Aire and Calder | NEW MILL DIKE | Not Applicable | Not Applicable | Not Applicable | 5:30 | 5 | 15 | 2020 | 10.33 | Comms failure / issue | Scheduled | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00955
YWS00956 | Yorkshire Water | Live | Brandsby Road No.2 Combined Sewer Overflow* | BRANDSBY ROAD/NO 2 CSO | Not matched in Consents Database | EPR/HB3892RX | A1 | SO on sewer network | SE5661671160 | 456616 | 471160 | GB104027067760 | Foss from Source to Farlington Beck | River | 3190 | Foss | 3088 | Swale, Ure, Nidd and Upper Ouse | Not matched in EA Consents Database | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0.2 | 2020 | 99.98 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00956
YWS00957 | Yorkshire Water | Live | EWDEN WWTW | EWDEN/STW | EPRMB3797WP | EPR/MB3797WP | A2 | Storm tank at WwTW | SK2984495786 | 429761 | 395920 | GB104027057411 | Don from Little Don to River Loxley confluence | River | 3490 | Upper Don | 3029 | Don and Rother | RIVER DON | Not Applicable | Not Applicable | Not Applicable | 725:30 | 60 | 50.8 | 2020 | 99.69 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS00957
YWS00958 | Yorkshire Water | Live | ALANDALE ROAD BRADLEY CSO | ALANDALE ROAD BRADLEY/CSO | EPRTP3823KH | EPR/TP3823KH | A1 | SO on sewer network | SE1638420521 | 416384 | 420521 | GB70410176 | Huddersfield Broad Canal | Canal | 2007 | Calder Canals | 2001 | Humber AWB | TRIBUTARY OF THE RIVER COLNE | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 2.8 | 2020 | 99.88 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00958
YWS00959 | Yorkshire Water | Live | ALBERT ROAD CSO | ALBERT ROAD/CSO | EPRTP3823XQ | EPR/TP3823XQ | A1 | SO on sewer network | SK4013075258 | 440130 | 375258 | GB104027057771 | Rother, Spittal Brook to Doe Lea | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | RIVER ROTHER | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0.6 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00959
YWS00960 | Yorkshire Water | Live | STATION LANE HEDON CSO | STATION LANE HEDON/CSO | EPRTP3824GK | EPR/TP3824GK | A1 | SO on sewer network | TA1893728963 | 518937 | 428963 | GB104026067200 | Burstwick Drain from Source to Humber | River | 3057 | Burstwick and Eastern Drains | 3039 | Hull and East Riding | REEDMERE SEWER | Not Applicable | Not Applicable | Not Applicable | 0:15 | 1 | 2 | 2020 | 99.9 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00960
YWS00961 | Yorkshire Water | Live | ANCHROAGE LANE CSO | ANCHORAGE LANE/ESO | EPRTP3824XB | EPR/TP3824XB | A1 | Storm discharge at pumping station | SE5626603904 | 456265 | 403903 | GB104027064243 | Don from Mill Dyke to River Ouse | River | 3272 | Lower Don | 3029 | Don and Rother | SWAITHE DIKE | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 15.6 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00961
YWS00962 | Yorkshire Water | Live | STONEBRIDGEGATE FIRE STATION CSO | STONEBRIDGEGTE FR STN/CSO | EPRTP3825GH | EPR/TP3825GH | A1 | SO on sewer network | SE3160371564 | 431603 | 471564 | GB104027069461 | Ure from Thornton Steward Beck to River Skell | River | 3309 | Middle and Lower Ure | 3088 | Swale, Ure, Nidd and Upper Ouse | SKITTERGATE GUTTER | Not Applicable | Not Applicable | Not Applicable | 241:15 | 54 | 42.6 | 2020 | 99.8 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | Operational investigation completed | No improvement action in reporting period | SOAF investigation completed - No work required | YWS00962
YWS00963 | Yorkshire Water | Live | APPLEGARTH BRIDGE CSO | APPLEGARTH BRIDGE/CSO | EPRTP3825XL | EPR/TP3825XL | A1 | SO on sewer network | SE3671594014 | 436715 | 494014 | GB104027069540 | Willow Beck Catchment (trib of Wiske) | River | 3541 | Wiske | 3088 | Swale, Ure, Nidd and Upper Ouse | SUN BECK | Not Applicable | Not Applicable | Not Applicable | 58:15 | 29 | 26.6 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00963
YWS00964 | Yorkshire Water | Live | WALES MANOR ROAD CSO | WALES MANOR ROAD/CSO | EPRTP3826GC | EPR/TP3826GC | A1 | SO on sewer network | SK4793583306 | 447935 | 383306 | GB104027057730 | Pigeon Bridge Brook from Source to River Rother | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | TRIBUTARY OF TODWICK BECK | Not Applicable | Not Applicable | Not Applicable | 4:00 | 3 | 4 | 2020 | 99.69 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00964
YWS00965 | Yorkshire Water | Live | SWALLOWS NEST CSO | SWALLOWS NEST/CSO | EPRTP3826XU | EPR/TP3826XU | A1 | SO on sewer network | SE2833218035 | 428332 | 418035 | GB104027062631 | Calder from River Colne to River Chald | River | 3268 | Lower Calder | 3001 | Aire and Calder | TRIB OF RIVER CALDER | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 3 | 2020 | 12.87 | Comms failure / issue | Resolved - Dec | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00965
YWS00966 | Yorkshire Water | Live | WATER LANE FLAMBOROUGH CSO | WATER LN FLAMBOROUGH/CSO | EPRTP3827GN | EPR/TP3827GN | A1 | SO on sewer network | TA2246069928 | 522460 | 469928 | Not part of a WFD catchment | Not part of a WFD catchment | River | N/A | N/A | N/A | N/A | HARTENDALE GUTTER | Not Applicable | Flamborough South Landing | Not Applicable | 5:34 | 2 | 1.6 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00966
YWS00967 | Yorkshire Water | Live | WATH WEST STREET CSO | WATH WEST STREET/NO 2 CSO | EPRTP3827XG | EPR/TP3827XG | A1 | SO on sewer network | SE4322300982 | 443223 | 400982 | GB104027057470 | Knoll Beck from Source to River Dearne | River | 3125 | Dearne | 3029 | Don and Rother | BROOK DIKE | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 3.8 | 2020 | 99.3 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00967
YWS00968 | Yorkshire Water | Live | OTLEY ROAD BAILDON CSO | OTLEY ROAD BAILDON/CSO | EPRTP3828GV | EPR/TP3828GV | A1 | SO on sewer network | SE1703639753 | 417036 | 439753 | GB104027063034 | Aire (R Worth to Gill Beck) | River | 3307 | Middle Aire | 3001 | Aire and Calder | CULVERTED TRIB OF GILL BECK | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00968
YWS00969 | Yorkshire Water | Live | TITANIC MILLS CSO | TITANIC MILLS/CSO | EPRTP3829GA | EPR/TP3829GA | A1 | SO on sewer network | SE0994714890 | 409947 | 414890 | GB104027063330 | Colne from Wessenden Brook to R Holme | River | 3097 | Colne and Holme | 3001 | Aire and Calder | RIVER COLNE | Not Applicable | Not Applicable | Not Applicable | 93:00 | 26 | 5.4 | 2020 | 70.66 | Comms failure / issue | Resolved - Apr | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00969
YWS00970 | Yorkshire Water | Live | SUNNY RORD COMBINED SEWER OVERFLOW | SUNNY ROYD/CSO | EPRTP3920GS | EPR/TP3920GS | A1 | SO on sewer network | SE0023348428 | 400233 | 448428 | GB104027063033 | Aire (Eshton Beck to R Worth) | River | 3484 | Upper Aire | 3001 | Aire and Calder | MIDDLE BECK | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0 | 2020 | 99.43 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00970
YWS00971 | Yorkshire Water | Live | COOPER BRIDGE CSO | COOPER BRIDGE/CSO | EPRTP3920XR | EPR/TP3920XR | A1 | SO on sewer network | SE1759920604 | 417599 | 420604 | GB104027062642 | Calder from Ryburn Confluence to River Colne | River | 3310 | Middle Calder | 3001 | Aire and Calder | RIVER CALDER | Not Applicable | Not Applicable | Not Applicable | 1:00 | 3 | 5.6 | 2020 | 76.02 | Sensor failure / issue | Resolved - Mar | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00971
YWS00972 | Yorkshire Water | Live | BOG GREEN LANE | BOG GREEN LANE/CSO | EPRUP3123GW | EPR/UP3123GW | A1 | SO on sewer network | SE1777620220 | 417776 | 420220 | GB104027062550 | Colne from River Holme to River Calder | River | 3097 | Colne and Holme | 3001 | Aire and Calder | RIVER COLNE | Not Applicable | Not Applicable | Not Applicable | 644:15 | 159 | 125.8 | 2020 | 87.87 | Sensor failure / issue | Resolved - Nov | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS00972
YWS00973 | Yorkshire Water | Live | BRANDY CARR ROAD 252 CSO | BRANDY CARR ROAD 252/CSO | EPRUP3123XH | EPR/UP3123XH | A1 | SO on sewer network | SE3098623567 | 430986 | 423567 | GB104027062620 | Chald from Source to River Calder | River | 3268 | Lower Calder | 3001 | Aire and Calder | CARR GATE BECK | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00973
YWS00974 | Yorkshire Water | Live | CANAL ROAD FRIZINGHALL CSO | CANAL RD FRIZINGHALL/CSO | EPRUP3125GY | EPR/UP3125GY | A1 | SO on sewer network | SE1557535594 | 415575 | 435594 | GB104027062862 | Bradford Beck (Clayton Bk to R Aire) | River | 3307 | Middle Aire | 3001 | Aire and Calder | BRADFORD BECK | Not Applicable | Not Applicable | Not Applicable | 306:45 | 69 | 24.6 | 2020 | 99.88 |  |  | Not asset maintenance - Hydraulic capacity | High spill threshold not met | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS00974
YWS00975 | Yorkshire Water | Live | CARRS LANE CUDWORTH | CARRS LANE CUDWORTH/CSO | EPRUP3126GQ | EPR/UP3126GQ | A1 | SO on sewer network | SE3896007850 | 438960 | 407850 | GB104027063230 | Cudworth Dyke from Source to River Dearne | River | 3125 | Dearne | 3029 | Don and Rother | SMALL BRIDGE DIKE | Not Applicable | Not Applicable | Not Applicable | 1:15 | 3 | 3.2 | 2020 | 94.2 |  |  | High spill threshold not met | High spill threshold not met | Operational investigation completed | Operational improvement completed | No SOAF investigation required | YWS00975
YWS00976 | Yorkshire Water | Live | DUDLEY ROAD CSO | DUDLEY ROAD/CSO | EPRUP3128XD | EPR/UP3128XD | A1 | SO on sewer network | SK3297390870 | 432973 | 390870 | GB104027057411 | Don from Little Don to River Loxley confluence | River | 3490 | Upper Don | 3029 | Don and Rother | RIVER DON | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0.8 | 2020 | 99.45 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00976
YWS00977 | Yorkshire Water | Live | ELLINGSTRING CSO | ELLINGSTRING/CSO | EPRUP3129XJ | EPR/UP3129XJ | A1 | SO on sewer network | SE1772383758 | 417723 | 483758 | GB40402G701900 | SUNO Millstone Grit and Carboniferous Limestone | Groundwater Body | 1209 | SUNO Millstone Grit and Carboniferous Limestone | 1006 | Humber GW | TRIBUTARY OF BROAD BECK | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0.4 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00977
YWS00978 | Yorkshire Water | Live | ELLISON STREET CSO | ELLISON STREET/CSO | EPRUP3220GZ | EPR/UP3220GZ | A1 | SO on sewer network | SE6893612620 | 468936 | 412620 | GB104028064350 | North Soak Drain Catchment (trib of Torne/Three Rivers) | River | 3234 | Isle of Axholme | 3041 | Idle and Torne | BOATING DIKE | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 1.4 | 2020 | 79.62 | Comms failure / issue | Resolved - Nov | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00978
YWS00979 | Yorkshire Water | Live | OAKDALE HARROGATE CSO | OAKDALE HARROGATE/CSO | EPRUP3221GE | EPR/UP3221GE | A1 | SO on sewer network | SE2937656228 | 429376 | 456228 | GB104027063760 | Oak Beck Catchment (Trib of Nidd) | River | 3308 | Middle and Lower Nidd | 3088 | Swale, Ure, Nidd and Upper Ouse | OAK BECK | Not Applicable | Not Applicable | Not Applicable | 27:00 | 6 | 5.6 | 2020 | 95.44 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00979
YWS00980 | Yorkshire Water | Live | FIDDLERS HILL | FIDDLERS HILL/CSO | EPRUP3221XK | EPR/UP3221XK | A1 | SO on sewer network | SE2384719547 | 423847 | 419547 | GB104027062631 | Calder from River Colne to River Chald | River | 3268 | Lower Calder | 3001 | Aire and Calder | TRIB OF RIVER CALDER | Not Applicable | Not Applicable | Not Applicable | 1:00 | 2 | 1 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00980
YWS00981 | Yorkshire Water | Live | GEORGE STREET DARFIELD NO 2 CSO | GEORGE ST DARFIELD/2 CSO | EPRUP3222GW | EPR/UP3222GW | A1 | SO on sewer network | SE4063303781 | 440633 | 403781 | GB104027057510 | Dove from Source to River Dearne | River | 3125 | Dearne | 3029 | Don and Rother | RIVER DOVE | Not Applicable | Not Applicable | Not Applicable | 20:15 | 3 | 9.6 | 2020 | 9.88 | Comms failure / issue | Resolved - Nov | High spill threshold not met | High spill threshold not met | Operational investigation ongoing | Operational improvement ongoing | No SOAF investigation required | YWS00981
YWS00982 | Yorkshire Water | Live | NUNMONKTON COMMON CSO | NUN MONKTON COMMON/CSO | EPRUP3222XH | EPR/UP3222XH | A1 | SO on sewer network | SE5082757995 | 450827 | 457995 | GB104027069592 | Ouse from River Ure to River Nidd | River | 3309 | Middle and Lower Ure | 3088 | Swale, Ure, Nidd and Upper Ouse | MILL SIKE | Not Applicable | Not Applicable | Not Applicable | 1:54 | 8 | 7 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00982
YWS00983 | Yorkshire Water | Live | WATH CEMETERY ROAD CSO | WATH CEMETERY ROAD/CSO | EPRUP3223GR | EPR/UP3223GR | A1 | SO on sewer network | SE4322000981 | 443220 | 400981 | GB104027057470 | Knoll Beck from Source to River Dearne | River | 3125 | Dearne | 3029 | Don and Rother | BROOK DIKE | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0.6 | 2020 | 98.45 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00983
YWS00984 | Yorkshire Water | Live | GREAT NORTH ROAD ADWICK CSO | GREAT NORTH RD ADWICK/CSO | EPRUP3223KQ | EPR/UP3223KQ | A1 | SO on sewer network | SE5404008936 | 454040 | 408936 | GB104027057591 | Ea Beck from the Skell to River Don | River | 3272 | Lower Don | 3029 | Don and Rother | MILL DIKE | Not Applicable | Not Applicable | Not Applicable | 154:45 | 21 | 4.8 | 2020 | 98.02 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00984
YWS00985 | Yorkshire Water | Live | STUMP CROSS ROAD CSO | STUMP CROSS ROAD/CSO | EPRUP3223XC | EPR/UP3223XC | A1 | SO on sewer network | SE4322000981 | 443220 | 400981 | GB104027057470 | Knoll Beck from Source to River Dearne | River | 3125 | Dearne | 3029 | Don and Rother | BROOK DIKE | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 1.4 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00985
YWS00986 | Yorkshire Water | Live | GINNY GREEN HOLES NATURE RESERVE | HARLAND WAY SPOFFORTH/CSO | EPRUP3224GY | EPR/UP3224GY | A1 | SO on sewer network | SE3687450818 | 436874 | 450818 | GB104027063742 | Crimple Beck from Park Beck to River Nidd | River | 3308 | Middle and Lower Nidd | 3088 | Swale, Ure, Nidd and Upper Ouse | CRIMPLE BECK OR RIVER CRIMPLE | Not Applicable | Not Applicable | Not Applicable | 4:15 | 4 | 5 | 2020 | 91.75 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00986
YWS00987 | Yorkshire Water | Live | NEW HILL PARK CSO | NEWHILL PARK/CSO | EPRUP3224XN | EPR/UP3224XN | A1 | SO on sewer network | SE4322000981 | 443220 | 400981 | GB104027057470 | Knoll Beck from Source to River Dearne | River | 3125 | Dearne | 3029 | Don and Rother | BROOK DIKE | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0.6 | 2020 | 99.95 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00987
YWS00988 | Yorkshire Water | Live | NETHER SILTON CSO | NETHER SILTON/CSO | EPRUP3225GQ | EPR/UP3225GQ | A1 | SO on sewer network | SE4548492079 | 445484 | 492079 | GB104027068950 | Broad Beck from Source to Cod Beck | River | 3283 | Lower Swale | 3088 | Swale, Ure, Nidd and Upper Ouse | TRIB OF OLD BECK | Not Applicable | Not Applicable | Not Applicable | 10:45 | 6 | 13 | 2020 | 99.76 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00988
YWS00989 | Yorkshire Water | Live | HARROWDEN CSO | HARROWDEN ROAD/CSO | EPRUP3225XV | EPR/UP3225XV | A1 | SO on sewer network | SE5829804936 | 458298 | 404936 | GB70410281 | Sheffield and South Yorkshire Navigation (New Junction and Stainforth and Keadby | Canal | 2018 | Don and Rother Canals | 2001 | Humber AWB | DRAIN LEADING TO THE RIVER DON | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0 | 2020 | 99.93 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00989
YWS00990 | Yorkshire Water | Live | MIDLAND ROAD CSO | MIDLAND ROAD/CSO | EPRUP3226GB | EPR/UP3226GB | A1 | SO on sewer network | SE1573038486 | 415730 | 438486 | GB104027063034 | Aire (R Worth to Gill Beck) | River | 3307 | Middle Aire | 3001 | Aire and Calder | RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 169:15 | 48 | 39.4 | 2020 | 98.42 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00990
YWS00991 | Yorkshire Water | Live | MARY LANE DARFIELD CSO | MARY LANE DARFIELD/CSO | EPRUP3227GL | EPR/UP3227GL | A1 | SO on sewer network | SE4164203820 | 441642 | 403820 | GB104027057510 | Dove from Source to River Dearne | River | 3125 | Dearne | 3029 | Don and Rother | RIVER DOVE | Not Applicable | Not Applicable | Not Applicable | 27:45 | 31 | 14.4 | 2020 | 99.97 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00991
YWS00992 | Yorkshire Water | Live | LOWTHER STREET CSO | LOWTHER STREET/CSO | EPRUP3228GU | EPR/UP3228GU | A1 | SO on sewer network | SE6088052563 | 460880 | 452563 | GB104027063520 | Foss from the Syke to the River Ouse | River | 3190 | Foss | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER FOSS | Not Applicable | Not Applicable | Not Applicable | 12:00 | 10 | 7.8 | 2020 | 99.93 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00992
YWS00993 | Yorkshire Water | Live | LORDS LANE BRIGHOUSE CSO | LORDS LANE BRIGHOUSE/CSO | EPRUP3229XP | EPR/UP3229XP | A1 | SO on sewer network | SE1499722533 | 414997 | 422533 | GB104027062642 | Calder from Ryburn Confluence to River Colne | River | 3310 | Middle Calder | 3001 | Aire and Calder | RIVER CALDER | Not Applicable | Not Applicable | Not Applicable | 0:40 | 1 | 0.8 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00993
YWS00994 | Yorkshire Water | Live | HOYLES MEMORIAL GARDENS CSO | HOYLES MEMORIAL GDNS/CSO | EPRUP3320GE | EPR/UP3320GE | A1 | SO on sewer network | SE0964221288 | 409642 | 421288 | GB104027062570 | Black Brook from Source to River Calder | River | 3310 | Middle Calder | 3001 | Aire and Calder | BLACK BROOK | Not Applicable | Not Applicable | Not Applicable | 39:00 | 28 | 32 | 2020 | 99.53 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00994
YWS00995 | Yorkshire Water | Live | INGROW BRIDGE CSO | INGROW BRIDGE/CSO | EPRUP3322GR | EPR/UP3322GR | A1 | SO on sewer network | SE0562839746 | 405628 | 439746 | GB104027062891 | Worth from Bridgehouse Beck to R Aire | River | 3307 | Middle Aire | 3001 | Aire and Calder | RIVER WORTH | Not Applicable | Not Applicable | Not Applicable | 2:00 | 4 | 1.8 | 2020 | 99.84 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00995
YWS00996 | Yorkshire Water | Live | YWS UNKNOWN SITES DEFAULT | BOWLAMS DYKE/CSO | H140 | H140 | 1 | Storm discharge at pumping station | TA1142045400 | 510660 | 444700 | GB104026066910 | Fordyke Stream Lower to Holderness Dr | River | 3274 | Lower Hull | 3039 | Hull and East Riding | LEVEN DRAIN | Not Applicable | Not Applicable | Not Applicable | 41:30 | 10 | 41 | 2020 | 99.08 |  |  | High spill threshold not met | N/A - Ongoing investigation | UWWTR investigation ongoing, Operational investigation completed | Operational improvement ongoing | SOAF investigation ongoing | YWS00996
YWS00997 | Yorkshire Water | Live | YWS UNKNOWN SITES DEFAULT | LEVEN WEST STREET/CSO | H140 | H140 | 2 | Storm discharge at pumping station | TA1142045400 | 510130 | 445450 | GB104026066910 | Fordyke Stream Lower to Holderness Dr | River | 3274 | Lower Hull | 3039 | Hull and East Riding | LEVEN DRAIN | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS00997
YWS01000 | Yorkshire Water | Live | BEVERLEY STW | BEVERLEY/STW | H174 | H174 | A2 | Storm tank at WwTW | TA0582039340 | 505822 | 439337 | GB104026067212 | Hull from Arram Beck to Humber | River | 3274 | Lower Hull | 3039 | Hull and East Riding | RIVER HULL | Not Applicable | Not Applicable | Not Applicable | 2620:15 | 136 | 73.8 | 2020 | 96.47 |  |  | Performance - GW inundation | Performance - GW inundation | UWWTR investigation ongoing, Operational investigation completed | Operational improvement completed | SOAF investigation ongoing | YWS01000
YWS01001 | Yorkshire Water | Live | MARKET WEIGHTON STW | MARKET WEIGHTON/NO 2 STW | H226 | H226 | 2 | Storm tank at WwTW | SE8681040700 | 486810 | 440700 | GB104026066690 | Foulness from Black Beck to Market Weighton Canal | River | 3191 | Foulness | 3039 | Hull and East Riding | MARKET WEIGHTON BECK | Not Applicable | Not Applicable | Not Applicable | 1225:00 | 104 | 58.4 | 2020 | 99.98 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS01001
YWS01002 | Yorkshire Water | Live | SANDS LANE SEWAGE PUMPING STATION | SANDS LANE BRID/CSO | NPSWQD000318 | NPSWQD000318 | 1 | SO on sewer network | TA1922067340 | 519220 | 467346 | GB640402491000 | Yorkshire South | Coastal Water | 3179 | Esk TraC | 3040 | Humber TraC | NORTH SEA | Not Applicable | Bridlington North Beach | Not Applicable | 10:24 | 16 | 17.8 | 2020 | 99.95 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01002
YWS01003 | Yorkshire Water | Live | ST ANNES ROAD CSO | ST ANNES ROAD/CSO | NPSWQD000319 | NPSWQD000319 | 1 | SO on sewer network | TA1922167340 | 519220 | 467346 | GB640402491000 | Yorkshire South | Coastal Water | 3179 | Esk TraC | 3040 | Humber TraC | NORTH SEA | Not Applicable | Bridlington North Beach | Not Applicable | 10:12 | 13 | 13.6 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01003
YWS01004 | Yorkshire Water | Live | MARKET STREET CS0 | MARKET ST ECKINGTON/CSO | NPSWQD000393 | NPSWQD000393 | 1 | SO on sewer network | SK4332079900 | 443325 | 379907 | GB104027057720 | The Moss from Source to River Rother | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | THE MOSS | Not Applicable | Not Applicable | Not Applicable | 13:15 | 5 | 20.2 | 2020 | 98.81 |  |  | High spill threshold not met | High spill threshold not met | Operational investigation completed | Operational improvement completed | No SOAF investigation required | YWS01004
YWS01005 | Yorkshire Water | Live | RYEHILL SEWAGE PUMPING STATION | RYEHILL/CSO | NPSWQD002504 | NPSWQD002504 | 1 | Storm discharge at pumping station | TA2184025910 | 521840 | 425910 | GB104026067230 | Sands/Keyingham/Roos Dr from Source to Humber | River | 3057 | Burstwick and Eastern Drains | 3039 | Hull and East Riding | GREEN MARSH DRAIN | Not Applicable | Not Applicable | Not Applicable | 0:30 | 1 | 0.4 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01005
YWS01006 | Yorkshire Water | Live | DOCKFIELD ROAD CSO | DOCKFIELD ROAD/CSO | NPSWQD004589 | NPSWQD004589 | A1 | SO on sewer network | SE1518937959 | 415189 | 437959 | GB104027063034 | Aire (R Worth to Gill Beck) | River | 3307 | Middle Aire | 3001 | Aire and Calder | RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 10:30 | 7 | 3.6 | 2020 | 53.65 | Comms failure / issue | Scheduled | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01006
YWS01007 | Yorkshire Water | Live | STATION RD BAILDON NO.2 CSO | STATION RD BAILDON/2 CSO | NPSWQD005364 | NPSWQD005364 | A1 | SO on sewer network | SE1556039230 | 415560 | 439228 | GB104027063034 | Aire (R Worth to Gill Beck) | River | 3307 | Middle Aire | 3001 | Aire and Calder | BARNSLEY BECK (CULVERTED) | Not Applicable | Not Applicable | Not Applicable | 3:00 | 6 | 7.2 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01007
YWS01008 | Yorkshire Water | Live | SPRING VALLEY NO2 CSO | SPRING VALLEY/NO 2 CSO | NPSWQD005795 | NPSWQD005795 | 1 | SO on sewer network | SE2203434396 | 422038 | 434393 | GB104027062830 | Low/Wortley/Pudsey Bks | River | 3265 | Lower Aire | 3001 | Aire and Calder | FARSLEY BECK | Not Applicable | Not Applicable | Not Applicable | 27:30 | 20 | 21 | 2020 | 94.25 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01008
YWS01009 | Yorkshire Water | Live | OLD MALTONGATE CSO | OLD MALTONGATE/CSO | NPSWQD005796 | NPSWQD005796 | A1 | SO on sewer network | SE7863271514 | 478632 | 471514 | GB104027068313 | Derwent from River Rye to Kirkham | River | 3311 | Middle Derwent Yorkshire | 3027 | Derwent Humber | THE RIVER DERWENT | Not Applicable | Not Applicable | Not Applicable | 0:38 | 2 | 2.4 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01009
YWS01010 | Yorkshire Water | Live | STATION RD STAVELEY CSO | STATION RD STAVELEY/CSO | NPSWQD005798 | NPSWQD005798 | 1 | SO on sewer network | SK4134275315 | 441340 | 375320 | GB104027057771 | Rother, Spittal Brook to Doe Lea | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | TROUGH BROOK TRIB OF R.ROTHER | Not Applicable | Not Applicable | Not Applicable | 5:30 | 2 | 9.6 | 2020 | 76.28 | Comms failure / issue | Resolved - Oct | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01010
YWS01011 | Yorkshire Water | Live | EASTGATE CSO | EASTGATE/CSO | NPSWQD005831 | NPSWQD005831 | 1 | SO on sewer network | SE8067082770 | 480566 | 483378 | GB104027068460 | The Syme form Source to Thornton | River | 3489 | Upper Derwent Yorkshire | 3027 | Derwent Humber | OUTGANG DRAIN | Not Applicable | Not Applicable | Not Applicable | 13:30 | 12 | 12.4 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01011
YWS01012 | Yorkshire Water | Live | NESFIELD CLOSE CSO | NESFIELD CLOSE/CSO | NPSWQD005849 | NPSWQD005849 | Α1 | SO on sewer network | TA0561783054 | 505617 | 483054 | GB104027073281 | Eastfield Drain Lower to River Hertford | River | 3489 | Upper Derwent Yorkshire | 3027 | Derwent Humber | UNNAMED DRAIN TRIB R.HERTFORD | Not Applicable | Not Applicable | Not Applicable | 106:30 | 17 | 12.4 | 2020 | 99.96 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01012
YWS01013 | Yorkshire Water | Live | RICHARDSHAW LANE NO2 CSO | RICHARDSHAW LANE/NO 2 CSO | NPSWQD005864 | NPSWQD005864 | A1 | SO on sewer network | SE2199734333 | 421997 | 434333 | GB104027062830 | Low/Wortley/Pudsey Bks | River | 3265 | Lower Aire | 3001 | Aire and Calder | FARSLEY BECK (CULVERTED) | Not Applicable | Not Applicable | Not Applicable | 1:15 | 3 | 3.2 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01013
YWS01014 | Yorkshire Water | Live | DEWSBURY ROAD 51 NO2 CSO | DEWSBURY ROAD 51/NO 2 CSO | NPSWQD005961 | NPSWQD005961 | A1 | SO on sewer network | SE2822928654 | 428229 | 428654 | GB104027062750 | Milshaw Beck from Source to Low/Wortley/Pudsey Bks | River | 3265 | Lower Aire | 3001 | Aire and Calder | COTTON MILL BECK | Not Applicable | Not Applicable | Not Applicable | 130:15 | 59 | 62.8 | 2020 | 100 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01014
YWS01015 | Yorkshire Water | Live | HARROGATE ROAD 297 CSO | HARROGATE ROAD 297/2 CSO | NPSWQD005963 | NPSWQD005963 | A1 | SO on sewer network | SE1949037900 | 419490 | 437900 | GB104027063032 | Aire from Gill Beck (Baildon) to River Calder | River | 3265 | Lower Aire | 3001 | Aire and Calder | THE RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 463:45 | 84 | 98.4 | 2020 | 83.7 | Comms failure / issue | Resolved - Dec | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement completed | SOAF investigation ongoing | YWS01015
YWS01016 | Yorkshire Water | Live | LOWER POPPLETON LANE SPS | LOWER POPPLETON/CSO | NPSWQD006095 | NPSWQD006095 | A2 | Storm discharge at pumping station | SE5690053582 | 456900 | 453580 | GB104027069593 | Ouse from River Nidd to Stillingfleet Beck | River | 3499 | Upper Ouse Yorkshire | 3088 | Swale, Ure, Nidd and Upper Ouse | UNNAMED TRIB OF RIVER OUSE | Not Applicable | Not Applicable | Not Applicable | 75:52 | 41 | 15 | 2020 | 87.15 | Sensor failure / issue | Resolved - Nov | High spill threshold not met | High spill threshold not met | UWWTR investigation ongoing, Operational investigation completed | Operational improvement completed | SOAF investigation ongoing | YWS01016
YWS01017 | Yorkshire Water | Live | HIGH STREET SWALLOWNEST CSO | HIGH ST SWALLOWNEST/CSO | NPSWQD006096 | NPSWQD006096 | A1 | SO on sewer network | SK4533085340 | 445332 | 385337 | GB104027057730 | Pigeon Bridge Brook from Source to River Rother | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | DON | Not Applicable | Not Applicable | Not Applicable | 142:00 | 43 | 40 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | SOAF investigation completed - operational solution completed | YWS01017
YWS01018 | Yorkshire Water | Live | HARDINGS LANE CSO | HARDINGS LANE/CSO | NPSWQD008018 | NPSWQD008018 | A1 | SO on sewer network | SE0144545292 | 401445 | 445292 | GB104027062960 | Eastburn Beck from Lothersdale Beck to River Aire | River | 3484 | Upper Aire | 3001 | Aire and Calder | CLVRT TRIBUTARY OF RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 126:00 | 38 | 41 | 2020 | 99.96 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | No investigation activity in reporting period | No improvement action in reporting period | SOAF investigation completed - No work required | YWS01018
YWS01019 | Yorkshire Water | Live | WHEATLY/NO 2 SPS | WHEATLEY/NO 2 CSO | NPSWQD008129 | NPSWQD008129 | 1 | SO on sewer network | SE5776604088 | 457766 | 404087 | GB70410281 | Sheffield and South Yorkshire Navigation (New Junction and Stainforth and Keadby | Canal | 2018 | Don and Rother Canals | 2001 | Humber AWB | AN UNNAMED TRIB SHEF & SY NAVI | Not Applicable | Not Applicable | Not Applicable | 25:30 | 9 | 5.2 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01019
YWS01020 | Yorkshire Water | Live | PACKHORSE LANE CSO | PACKHORSE LANE/CSO | NPSWQD008685 | NPSWQD008685 | A1 | SO on sewer network | SK3466197826 | 434661 | 397826 | GB104027057440 | Blackburn Brook from Source to River Don | River | 3312 | Middle Don | 3029 | Don and Rother | BLACKBURN BROOK | Not Applicable | Not Applicable | Not Applicable | 1:30 | 2 | 10 | 2020 | 99.65 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01020
YWS01021 | Yorkshire Water | Live | ENDCLIFFE PARK CSO | ENDCLIFFE PARK/CSO | NPSWQD008877 | NPSWQD008877 | A1 | SO on sewer network | SK3321285784 | 433212 | 385784 | GB104027057760 | Porter from Source to River Sheaf | River | 3312 | Middle Don | 3029 | Don and Rother | PORTER BROOK | Not Applicable | Not Applicable | Not Applicable | 41:00 | 26 | 27 | 2020 | 91.42 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01021
YWS01022 | Yorkshire Water | Live | BROOK PARK NO2 CSO | BROOK PARK/NO 2 CSO | NPSWQD009652 | NPSWQD009652 | A1 | SO on sewer network | NZ8690408259 | 486904 | 508259 | GB104027068150 | Esk from Sleddale Beck to Ruswarp | River | 3177 | Esk | 3037 | Esk and Coast | TRIBUTARY OF RIVER ESK | Not Applicable | Not Applicable | Not Applicable | 26:30 | 13 | 14.2 | 2020 | 99.26 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01022
YWS01023 | Yorkshire Water | Live | SPENBOROUGH SPS | SPENBOROUGH/SPS | NPSWQD009808 | NPSWQD009808 | A1 | Storm discharge at pumping station | SE2315020490 | 423150 | 420490 | GB104027062710 | Spen Beck from Source to River Calder | River | 3268 | Lower Calder | 3001 | Aire and Calder | RIVER CALDER AND RIVER SPEN | Not Applicable | Not Applicable | Not Applicable | 686:30 | 71 | 59.6 | 2020 | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS01023
YWS01024 | Yorkshire Water | Live | SPENBOROUGH SPS | SPENBOROUGH/SPS | NPSWQD009808 | NPSWQD009808 | A2 | Storm discharge at pumping station | SE2208022410 | 422080 | 422410 | GB104027062710 | Spen Beck from Source to River Calder | River | 3268 | Lower Calder | 3001 | Aire and Calder | RIVER CALDER AND RIVER SPEN | Not Applicable | Not Applicable | Not Applicable | 126:45 | 24 | 50.6 | 2020 | 99.99 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS01024
YWS01025 | Yorkshire Water | Live | SECKAR SEWAGE TREATMENT WORKS | SECKAR/STW/6XDWF OVERFLOW | NPSWQD009922 | NPSWQD009922 | A2 | Inlet SO at WwTW | SE3318714322 | 433187 | 414322 | GB104027062530 | Owler Beck from Source to River Calder | River | 3268 | Lower Calder | 3001 | Aire and Calder | LAWNS DIKE, TRIB NEWMILLER DAM | Not Applicable | Not Applicable | Not Applicable |  |  | 20 | 2020 | 0 | Installation set-up/design issue | Resolved - February after reporting year | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01025
YWS01026 | Yorkshire Water | Live | FRYSTON SEWAGE PUMPING STATION | FRYSTON/CSO | NPSWQD009929 | NPSWQD009929 | A2 | Storm discharge at pumping station | SE4564727178 | 445647 | 427178 | GB104027062760 | Aire from River Calder to River Ouse | River | 3265 | Lower Aire | 3001 | Aire and Calder | RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 21:00 | 9 | 10 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01026
YWS01027 | Yorkshire Water | Live | COLD KIRBY NO2 STW | COLD KIRBY/NO 2 STW | NPSWQD009944 | NPSWQD009944 | 2 | Inlet SO at WwTW | SE5352084630 | 453415 | 484551 | GB104027068450 | Spring Wood Catchment (Trib of Rye) | River | 3387 | Rye | 3027 | Derwent Humber | UNNAMED TRIB GRASS KELD | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0 | 2020 | 96.12 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01027
YWS01028 | Yorkshire Water | Live | BRICKYARD COTTAGE SPS | BRICK YARD COTTAGES/CSO | NPSWQD010167 | NPSWQD010167 | 1 | Storm discharge at pumping station | SE9920025280 | 499200 | 425280 | GB530402609202 | HUMBER MIDDLE | Transitional Water | 3228 | Humber Estuary TraC | 3040 | Humber TraC | RIVER HUMBER | Not Applicable | Not Applicable | Not Applicable | 181:30 | 42 | 27 | 2020 | 71.45 | Sensor failure / issue | Resolved - Oct | High spill threshold not met | High spill threshold not met | UWWTR investigation ongoing, Operational investigation completed | Operational improvement ongoing | SOAF investigation ongoing | YWS01028
YWS01029 | Yorkshire Water | Live | NORTH BIERLEY CSO | NORTH BIERLEY/CSO | NPSWQD010861 | NPSWQD010861 | A1 | SO on sewer network | SE1809027414 | 418090 | 427414 | GB104027062710 | Spen Beck from Source to River Calder | River | 3268 | Lower Calder | 3001 | Aire and Calder | HUNSWORTH BECK | Not Applicable | Not Applicable | Not Applicable | 71:00 | 28 | 17.6 | 2020 | 99.95 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01029
YWS01030 | Yorkshire Water | Live | EASTWOOD NO2 CSO | EASTWOOD/NO 2 CSO | NPSWQD011063 | NPSWQD011063 | A1 | Inlet SO at WwTW | SD9715126413 | 397151 | 426413 | GB104027062650 | Calder from Walsden Water to Colden Water | River | 3487 | Upper Calder | 3001 | Aire and Calder | RIVER CALDER | Not Applicable | Not Applicable | Not Applicable | 870:30 | 101 | 88.4 | 2020 | 99.97 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | No investigation activity in reporting period | No improvement action in reporting period | SOAF investigation completed - No work required | YWS01030
YWS01031 | Yorkshire Water | Live | WINKHOLME SEWAGE PUMPING STATION | WINKHOLME/CSO | NPSWQD011176 | NPSWQD011176 | A1 | SO on sewer network | SD9685043011 | 396850 | 443011 | GB104027062930 | Glusburn beck from source to Lothersdale Beck | River | 3484 | Upper Aire | 3001 | Aire and Calder | ICKORNSHAW BECK | Not Applicable | Not Applicable | Not Applicable | 71:45 | 23 | 29.2 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01031
YWS01032 | Yorkshire Water | Live | WHEATLEY LANE 2 CSO | WHEATLEY LANE/2 CSO | QC.27/19/0018 | QC.27/19/0018 | A1 | SO on sewer network | SE1360948128 | 413609 | 448128 | GB104027064257 | Wharfe from Barben Beck/River Dibb to Hundwith Beck | River | 3318 | Middle Wharfe and Washburn | 3115 | Wharfe and Lower Ouse | RIVER WHARFE | Not Applicable | Not Applicable | Not Applicable | 243:15 | 50 | 67.6 | 2020 | 100 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01032
YWS01033 | Yorkshire Water | Live | WYVILL ROAD CSO | WYVILL ROAD/CSO | QC.27/19/0025 | QC.27/19/0025 | A1 | SO on sewer network | SE1341348142 | 413413 | 448142 | GB104027064257 | Wharfe from Barben Beck/River Dibb to Hundwith Beck | River | 3318 | Middle Wharfe and Washburn | 3115 | Wharfe and Lower Ouse | THE RIVER WHARFE | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0.4 | 2020 | 86.61 | Comms failure / issue | Resolved - Jun | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01033
YWS01034 | Yorkshire Water | Live | CSO-HARROGATE STRAY | STRAY ROAD/CSO | QC.27/21/0026 | QC.27/21/0026 | 1 | SO on sewer network | SE3063054520 | 430631 | 454524 | GB104027063741 | Crimple Beck from Source to Park Beck | River | 3308 | Middle and Lower Nidd | 3088 | Swale, Ure, Nidd and Upper Ouse | HOOKSTONE BECK (NIDD CAT) | Not Applicable | Not Applicable | Not Applicable | 327:15 | 43 | 43.6 | 2020 | 99.93 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01034
YWS01035 | Yorkshire Water | Live | HAMBLETON ROAD CSO | HAMBLETON ROAD/CSO | QC.27/21/0050 | QC.27/21/0050 | A1 | SO on sewer network | SE3158957202 | 431589 | 457202 | GB104027068297 | Nidd from Oak Beck to Low Bridge on Briggate (Knaresborough) | River | 3308 | Middle and Lower Nidd | 3088 | Swale, Ure, Nidd and Upper Ouse | CLVRT TRIB OF BILTON BECK | Not Applicable | Not Applicable | Not Applicable | 3:45 | 2 | 3.4 | 2020 | 21.68 | Sensor failure / issue | Resolved - Nov | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01035
YWS01036 | Yorkshire Water | Live | RICHMOND BATHS CSO | RICHMOND BATHS/CSO | QC.27/23/0026 | QC.27/23/0026 | A1 | SO on sewer network | NZ1771200967 | 417712 | 500967 | GB104027069122 | Swale from Clapgate Beck to Bedale Beck | River | 3317 | Middle Swale | 3088 | Swale, Ure, Nidd and Upper Ouse | THE RIVER SWALE | Not Applicable | Not Applicable | Not Applicable | 5:15 | 7 | 16.6 | 2020 | 99.24 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01036
YWS01037 | Yorkshire Water | Live | CSO & PUMPING STATION | HUNGATE/NO 2 CSO | QC.27/25/0045 | QC.27/25/0045 | 1 | SO on sewer network | SE7964083900 | 479640 | 483901 | GB104027068470 | Pickering Beck from Source to Costa Beck | River | 3387 | Rye | 3027 | Derwent Humber | THE PICKERING BECK | Not Applicable | Not Applicable | Not Applicable | 5:45 | 2 | 32.4 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | Operational investigation completed | Operational improvement ongoing | No SOAF investigation required | YWS01037
YWS01038 | Yorkshire Water | Live | KNARESBOROUGH WPC WORKS | KNARESBOROUGH/STW | QR.27/21/0031 | QR.27/21/0031 | 2 | Storm tank at WwTW | SE3667056760 | 436510 | 456570 | GB104027068298 | Nidd from Low Bridge on Briggate (Knaresborough) to Crimple Beck | River | 3308 | Middle and Lower Nidd | 3088 | Swale, Ure, Nidd and Upper Ouse | THE RIVER NIDD | Not Applicable | Not Applicable | Not Applicable | 448:15 | 49 | 51.6 | 2020 | 99.99 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01038
YWS01039 | Yorkshire Water | Live | HARROGATE NORTH SEWAGE TREATMENT | HARROGATE NORTH/STW/3XDWF OVERFLOW | QR.27/21/0047 | QR.27/21/0047 | A2 | Storm tank at WwTW | SE3020057985 | 430200 | 457985 | GB104027063760 | Oak Beck Catchment (Trib of Nidd) | River | 3308 | Middle and Lower Nidd | 3088 | Swale, Ure, Nidd and Upper Ouse | OAK BECK (NIDD CAT) | Not Applicable | Not Applicable | Not Applicable | 686:15 | 69 | 70 | 2020 | 99.97 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01039
YWS01040 | Yorkshire Water | Live | HARROGATE NORTH SEWAGE TREATMENT | HARROGATE NORTH/STW/6XDWF OVERFLOW | QR.27/21/0047 | QR.27/21/0047 | A3 | Inlet SO at WwTW | SE3020057985 | 430184 | 457958 | GB104027063760 | Oak Beck Catchment (Trib of Nidd) | River | 3308 | Middle and Lower Nidd | 3088 | Swale, Ure, Nidd and Upper Ouse | OAK BECK (NIDD CAT) | Not Applicable | Not Applicable | Not Applicable | 190:00 | 53 | 50.8 | 2020 | 99.97 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01040
YWS01041 | Yorkshire Water | Live | HARROGATE SOUTH STW | HARROGATE SOUTH/STW | QR.27/21/0048 | QR.27/21/0048 | A2 | Storm tank at WwTW | SE3787051620 | 437870 | 451620 | GB104027063742 | Crimple Beck from Park Beck to River Nidd | River | 3308 | Middle and Lower Nidd | 3088 | Swale, Ure, Nidd and Upper Ouse | THE CRIMPLE BECK | Not Applicable | Not Applicable | Not Applicable | 833:41 | 72 | 74.4 | 2020 | 100 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01041
YWS01042 | Yorkshire Water | Live | STRAY REIN CSO | STRAY REIN/CSO | QR.27/21/0049 | QR.27/21/0049 | A1 | SO on sewer network | SE3085054396 | 430850 | 454396 | GB104027063741 | Crimple Beck from Source to Park Beck | River | 3308 | Middle and Lower Nidd | 3088 | Swale, Ure, Nidd and Upper Ouse | HOOHSTONE BECK (NIDD CAT) | Not Applicable | Not Applicable | Not Applicable | 0:15 | 1 | 0.6 | 2020 | 99.91 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01042
YWS01043 | Yorkshire Water | Live | HUNSINGORE STW | HUNSINGORE/STW | QR.27/21/0066 | QR.27/21/0066 | 2 | Inlet SO at WwTW | SE4270053100 | 442700 | 453100 | GB104027068292 | Nidd from Crimple Beck to River Ouse | River | 3308 | Middle and Lower Nidd | 3088 | Swale, Ure, Nidd and Upper Ouse | AN UNNAMED TRIBUTARY OF NIDD | Not Applicable | Not Applicable | Not Applicable | 13:15 | 16 | 14.6 | 2020 | 98.7 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01043
YWS01044 | Yorkshire Water | Live | ALDWARK MOOR SEWAGE TREATMENT WORKS | ALDWARK BAY HORSE/2 STW | QR.27/22/0039 | QR.27/22/0039 | A2 | Inlet SO at WwTW | SE4650063500 | 446500 | 463500 | GB104027069592 | Ouse from River Ure to River Nidd | River | 3309 | Middle and Lower Ure | 3088 | Swale, Ure, Nidd and Upper Ouse | UNNAMED TRIB OF RIVER URE | Not Applicable | Not Applicable | Not Applicable | 896:30 | 131 | 122.6 | 2020 | 99.91 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement completed | SOAF investigation ongoing | YWS01044
YWS01045 | Yorkshire Water | Live | FELIXKIRK SEWAGE TREATMENT WORKS | FELIXKIRK PIPER HILL/STW | QR.27/23/0100 | QR.27/23/0100 | 2 | Inlet SO at WwTW | SE4643084640 | 446432 | 484646 | GB104027068820 | Cod Beck from Spital Beck to River Swale | River | 3283 | Lower Swale | 3088 | Swale, Ure, Nidd and Upper Ouse | UNNAMED TRIB OF WHITELASS BECK | Not Applicable | Not Applicable | Not Applicable | 585:30 | 89 | 39.75 | 2020 | 99.64 |  |  | Performance - GW inundation | High spill threshold not met | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS01045
YWS01046 | Yorkshire Water | Live | THOLTHORPE STW (CONSENT REVIEWED) | THOLTHORPE/STW | QR27/24/0086 | QR.27/24/0086 | A2 | Inlet SO at WwTW | SE4740066900 | 447420 | 466980 | GB104027063920 | Derrings Beck from Source to River Kyle | River | 3499 | Upper Ouse Yorkshire | 3088 | Swale, Ure, Nidd and Upper Ouse | DERRINGS BECK | Not Applicable | Not Applicable | Not Applicable | 306:45 | 79 | 66.8 | 2020 | 100 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01046
YWS01047 | Yorkshire Water | Live | SELBY SEWAGE TREAMENT WORKS | SELBY/NO 2 STW | QR.27/24/0096 | QR.27/24/0096 | A2 | Storm tank at WwTW | SE6356031650 | 463560 | 431650 | GB104027064270 | Ouse from R Wharfe to Upper Humber | River | 3280 | Lower Ouse Yorkshire | 3115 | Wharfe and Lower Ouse | THE RIVER OUSE (TIDAL) | Not Applicable | Not Applicable | Not Applicable | 373:45 | 43 | 43 | 2020 | 99.38 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01047
YWS01048 | Yorkshire Water | Live | CORNER CAFE CSO | CORNER CAFE/NO 2 CSO | QR.27/26/0002 | QR.27/26/0002 | 1 | SO on sewer network | TA0390089900 | 503770 | 489800 | GB650401500004 | Yorkshire North | Coastal Water | 3179 | Esk TraC | 3040 | Humber TraC | THE NORTH SEA | Not Applicable | Scarborough North Bay | Not Applicable | 12:56 | 15 | 10 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01048
YWS01049 | Yorkshire Water | Live | BURNISTON GARDENS CSO | BURNISTON GARDENS/2 CSO | QR.27/26/0003 | QR.27/26/0003 | 1 | SO on sewer network | TA0156092570 | 501559 | 492579 | GB104027067980 | Burniston Beck/Sea Cut/Scalby Beck Catch to N Sea | River | 3489 | Upper Derwent Yorkshire | 3027 | Derwent Humber | BURNISTON BECK | Not Applicable | Scarborough North Bay | Not Applicable | 99:40 | 26 | 19.4 | 2020 | 98.92 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01049
YWS01050 | Yorkshire Water | Live | SEAMER SEWAGE TREATMENT WORKS | SEAMER/STW | QR.27/26/0011 | QR.27/26/0011 | A2 | Storm tank at WwTW | TA0085082890 | 500920 | 483020 | GB104027067880 | Seamer Drain from Source to River Hertford | River | 3489 | Upper Derwent Yorkshire | 3027 | Derwent Humber | SEAMER DRAIN | Not Applicable | Not Applicable | Not Applicable | 309:30 | 28 | 26.4 | 2020 | 99.97 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01050
YWS01051 | Yorkshire Water | Live | HUNMANBY SEWAGE TREATMENT WORKS - T | HUNMANBY/STW | QR27/27/0017 | QR.27/27/0017 | A2 | Storm tank at WwTW | TA1043077910 | 510440 | 477860 | GB104027067811 | Hertford from Source to River Derwent | River | 3489 | Upper Derwent Yorkshire | 3027 | Derwent Humber | TRIB OF RIVER HERTFORD | Not Applicable | Not Applicable | Not Applicable | 122:45 | 23 | 17 | 2020 | 99.8 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01051
YWS01052 | Yorkshire Water | Live | THE WHEATCROFT SHORT SEA OUTFALL | WHEATCROFT/CSO | QR.27/27/0029 | QR.27/27/0029 | A1 | Storm discharge at pumping station | TA0604086350 | 506040 | 486350 | GB650401500004 | Yorkshire North | Coastal Water | 3179 | Esk TraC | 3040 | Humber TraC | THE NORTH SEA | Not Applicable | Scarborough South Bay | Not Applicable | 258:12 | 21 | 31 | 2020 | 99.96 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01052
YWS01053 | Yorkshire Water | Live | CSO AT CLOCK TOWER/STONEBRIDGE/ | BORRAGE BRIDGE 80/CSO | S/B/50 | S/B/50 | 1 | SO on sewer network | SE3180071900 | 431046 | 470998 | GB104027064140 | Skell from River Laver to River Ure | River | 3309 | Middle and Lower Ure | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER URE | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0 | 2020 | 93.55 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01053
YWS01054 | Yorkshire Water | Live | CSO AT CLOCK TOWER/STONEBRIDGE/ | NEWBRIDGE/CSO | S/B/50 | S/B/50 | 2 | SO on sewer network | SE3180071900 | 431417 | 470956 | GB104027064140 | Skell from River Laver to River Ure | River | 3309 | Middle and Lower Ure | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER URE | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01054
YWS01055 | Yorkshire Water | Live | CSO AT CLOCK TOWER/STONEBRIDGE/ | LOW MILL ROAD/CSO | S/B/50 | EPR/CP3125PC | A1 | SO on sewer network | SE3180071900 | 431649 | 470902 | GB104027064140 | Skell from River Laver to River Ure | River | 3309 | Middle and Lower Ure | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER URE | Not Applicable | Not Applicable | Not Applicable | 0:30 | 1 | 0.2 | 2020 | 78.67 | Comms failure / issue | Resolved - Nov | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | SOAF investigation completed - No work required | YWS01055
YWS01056 | Yorkshire Water | Live | YWS UNKNOWN SITES DEFAULT | STEVENSON ROAD/CSO | S/CB/106 | S/CB/106 | 24 | SO on sewer network | SK3752489005 | 437524 | 389005 | GB104027057412 | Don from River Loxley confl to River Don Works | River | 3312 | Middle Don | 3029 | Don and Rother | VARIES WITH OUTLET | Not Applicable | Not Applicable | Not Applicable | 0:15 | 1 | 53.4 | 2020 | 100 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01056
YWS01057 | Yorkshire Water | Live | YWS UNKNOWN SITES DEFAULT | QUEENS ROAD SHEFFIELD/CSO | EPR/RB3154TM | EPR/RB3154TM | A1 | SO on sewer network | SK3580086409 | 435800 | 386409 | GB104027057750 | Sheaf from Source to River Don | River | 3312 | Middle Don | 3029 | Don and Rother | VARIES WITH OUTLET | Not Applicable | Not Applicable | Not Applicable | 31:15 | 22 | 20.6 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01057
YWS01058 | Yorkshire Water | Live | WOODHOUSE SEWER NETWORK - 3 CSOS | BADGER DRIVE/CSO | S/CB/132 | EPR/CP3029PA | A1 | SO on sewer network | SK4244985424 | 442448 | 385418 | GB104027057772 | Rother, Doe Lea to Don | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | SHIRTCLIFF BROOK | Not Applicable | Not Applicable | Not Applicable | 1:30 | 4 | 5.6 | 2020 | 90.61 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01058
YWS01059 | Yorkshire Water | Live | CHARTERIS ROAD CSO | CHATERIS ROAD/CSO | EPRKB3891VF | EPR/KB3891VF | A1 | SO on sewer network | SE1205933137 | 412059 | 433137 | GB104027062861 | Clayton Beck (Source to Bradford Bk) | River | 3307 | Middle Aire | 3001 | Aire and Calder | PITTY BECK | Not Applicable | Not Applicable | Not Applicable | 0:15 | 1 | 2 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01059
YWS01060 | Yorkshire Water | Live | YWS UNKNOWN SITES DEFAULT | BECKETT NOOK/NO 1 CSO | S/CB/48 | S/CB/48 | 10 | SO on sewer network | SE2280021380 | 422720 | 421345 | GB104027062710 | Spen Beck from Source to River Calder | River | 3268 | Lower Calder | 3001 | Aire and Calder | VARIES WITH OUTLET | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0 | 2020 | 90.72 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01060
YWS01061 | Yorkshire Water | Live | YWS UNKNOWN SITES DEFAULT | BECKETT NOOK/NO 2 CSO | S/CB/48 | S/CB/48 | 10b | SO on sewer network | SE2280021380 | 422720 | 421345 | GB104027062710 | Spen Beck from Source to River Calder | River | 3268 | Lower Calder | 3001 | Aire and Calder | VARIES WITH OUTLET | Not Applicable | Not Applicable | Not Applicable | 1:15 | 3 | 4.2 | 2020 | 99.68 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01061
YWS01063 | Yorkshire Water | Live | YWS UNKNOWN SITES DEFAULT | LOW COMMON/CSO | S/CB/51 | S/CB/51 | 1 | SO on sewer network | SE1429017830 | 416780 | 414249 | GB104027063340 | Fenay beck from Source to River Colne | River | 3097 | Colne and Holme | 3001 | Aire and Calder | VARIES WITH OUTLET | Not Applicable | Not Applicable | Not Applicable | 3:00 | 2 | 3.6 | 2020 | 68.6 | Comms failure / issue | Resolved - Apr | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01063
YWS01064 | Yorkshire Water | Live | YWS UNKNOWN SITES DEFAULT | ALL SAINTS SQUARE/CSO | S/CB/67 | S/CB/67 | 27 | SO on sewer network | SK4274593086 | 442745 | 393086 | GB104027057452 | Don from River Rother to River Dearne | River | 3312 | Middle Don | 3029 | Don and Rother | VARIES WITH OUTLET | Not Applicable | Not Applicable | Not Applicable | 141:15 | 75 | 98.4 | 2020 | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01064
YWS01065 | Yorkshire Water | Live | YWS UNKNOWN SITES DEFAULT | PSALTERS LANE HOLMES/CSO | S/CB/67 | S/CB/67 | 31 | SO on sewer network | SK4139892399 | 441398 | 392399 | GB70410276 | Sheffield and South Yorkshire Navigation (Holmes Cut) | Canal | 2018 | Don and Rother Canals | 2001 | Humber AWB | VARIES WITH OUTLET | Not Applicable | Not Applicable | Not Applicable | 34:15 | 5 | 1 | 2020 | 91.71 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01065
YWS01066 | Yorkshire Water | Live | YWS UNKNOWN SITES DEFAULT | YEW TREE ESTATE/NO 1 CSO | S/RD/132 | S/RD/132 | 3 | SO on sewer network | SK3454469679 | 434544 | 369679 | GB104027057660 | Hipper from Source to River Rother | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | RIVER HIPPER | Not Applicable | Not Applicable | Not Applicable | 56:45 | 29 | 16.6 | 2020 | 99.91 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01066
YWS01067 | Yorkshire Water | Live | VILLAGE GREEN CSO | VILLAGE GREEN/CSO | S/RD/275 | S/RD/275 | A1 | SO on sewer network | SE2602359087 | 426023 | 459087 | GB104027068296 | Nidd from Burstwith to Oak Beck | River | 3308 | Middle and Lower Nidd | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER NIDD | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0.4 | 2020 | 99.93 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01067
YWS01069 | Yorkshire Water | Live | YWS UNKNOWN SITES DEFAULT | NEWLAITHES ROAD/NO 1 CSO | S/UD/104 | S/UD/104 | A1 | SO on sewer network | SE2386636947 | 423866 | 436949 | GB104027063032 | Aire from Gill Beck (Baildon) to River Calder | River | 3265 | Lower Aire | 3001 | Aire and Calder | UNKNOWN | Not Applicable | Not Applicable | Not Applicable | 24:45 | 27 | 14 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01069
YWS01070 | Yorkshire Water | Live | SPRINGFIELD LANE CSO | SPRINGFIELD LANE/CSO | S/UD/112 | S/UD/112 | A1 | SO on sewer network | SE1918813012 | 419205 | 413032 | GB104027063340 | Fenay beck from Source to River Colne | River | 3097 | Colne and Holme | 3001 | Aire and Calder | TRIBUTARY OF DEAN BOTTOM DIKE | Not Applicable | Not Applicable | Not Applicable | 386:45 | 80 | 64.8 | 2020 | 93.16 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS01070
YWS01071 | Yorkshire Water | Live | ADWICK ROAD CSO | ADWICK ROAD/CSO | EPRYB3292RF | EPR/YB3292RF | A1 | SO on sewer network | SE4908401345 | 449084 | 401345 | GB104027063173 | Dearne Darfield STW to River Don | River | 3125 | Dearne | 3029 | Don and Rother | RIVER DEARNE | Not Applicable | Not Applicable | Not Applicable | 2:00 | 6 | 8 | 2020 | 99.94 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01071
YWS01072 | Yorkshire Water | Live | Not matched in EA Consents Database | RUSKIN AVENUE/CSO | S/UD/121 | S/UD/121 | 1b | SO on sewer network | SE4908401345 | 449084 | 401345 | GB104027063173 | Dearne Darfield STW to River Don | River | 3125 | Dearne | 3029 | Don and Rother | Not matched in EA Consents Database | Not Applicable | Not Applicable | Not Applicable | 1:45 | 6 | 10.2 | 2020 | 99.9 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01072
YWS01073 | Yorkshire Water | Live | YWS UNKNOWN SITES DEFAULT | VICTORIA TERRACE/CSO | S/UD/171/3 | EPR/BP3225PZ | A1 | SO on sewer network | SE1040403810 | 414051 | 438209 | GB104027063034 | Aire (R Worth to Gill Beck) | River | 3307 | Middle Aire | 3001 | Aire and Calder | NO DETAILS | Not Applicable | Not Applicable | Not Applicable | 1:15 | 3 | 2.8 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01073
YWS01074 | Yorkshire Water | Live | YWS UNKNOWN SITES DEFAULT | VICTORIA ROAD SHIPLEY/CSO | S/UD/171/3 | EPR/BP3229PY | A1 | SO on sewer network | SE1040403810 | 414051 | 438209 | GB104027063034 | Aire (R Worth to Gill Beck) | River | 3307 | Middle Aire | 3001 | Aire and Calder | NO DETAILS | Not Applicable | Not Applicable | Not Applicable | 186:45 | 71 | 53 | 2020 | 96.47 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement ongoing | SOAF investigation ongoing | YWS01074
YWS01075 | Yorkshire Water | Live | YWS UNKNOWN SITES DEFAULT | TICKHILL STREET/CSO | S/UD/5 | S/UD/5 | 1 | SO on sewer network | SK504998 | 450400 | 399800 | GB104027064242 | Don from River Dearne to Mill Dyke | River | 3312 | Middle Don | 3029 | Don and Rother | UNKNOWN | Not Applicable | Not Applicable | Not Applicable | 0:30 | 2 | 3 | 2020 | 99.9 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01075
YWS01076 | Yorkshire Water | Live | YWS UNKNOWN SITES DEFAULT | SCHOOL WALK/CSO | S/UD/5 | S/UD/5 | 2 | SO on sewer network | SK504998 | 450400 | 399800 | GB104027064242 | Don from River Dearne to Mill Dyke | River | 3312 | Middle Don | 3029 | Don and Rother | UNKNOWN | Not Applicable | Not Applicable | Not Applicable | 33:45 | 8 | 8 | 2020 | 82.84 | Sensor failure / issue | Resolved - Apr | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01076
YWS01077 | Yorkshire Water | Live | YWS UNKNOWN SITES DEFAULT | THE TAVERN PUB HOUSE/CSO | S/UD/5 | S/UD/5 | 3 | SO on sewer network | SK5039499886 | 450394 | 399886 | GB104027064242 | Don from River Dearne to Mill Dyke | River | 3312 | Middle Don | 3029 | Don and Rother | UNKNOWN | Not Applicable | Not Applicable | Not Applicable | 41:00 | 12 | 5.2 | 2020 | 79.16 | Comms failure / issue | Resolved - Nov | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01077
YWS01078 | Yorkshire Water | Live | YWS UNKNOWN SITES DEFAULT | AIRTON/SPS | S/RD/100 | S/RD/100 | 1 | Storm discharge at pumping station | SD9022059360 | 390226 | 459367 | GB40402G700400 | Aire & Calder Carb Limestone / Millstone Grit / Coal Measures. Water Body | Groundwater Body | 1001 | Aire and Calder Carb Limestone - Millstone Grit Coal - Measures | 1006 | Humber GW | RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 3:30 | 3 | 0.75 | 2020 | 99.92 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01078
YWS01079 | Yorkshire Water | Live | REMPLE LANE CSO | REMPLE LANE/CSO | T/83/00963/O | T/83/00963/O | A1 | SO on sewer network | SE6814908995 | 468149 | 408995 | GB104028064330 | Hatfield Waste Drain Catchment (trib of Torne/Three Rivers) | River | 3234 | Isle of Axholme | 3041 | Idle and Torne | STONEHILL DRAIN | Not Applicable | Not Applicable | Not Applicable | 26:30 | 19 | 17.4 | 2020 | 99.82 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01079
YWS01080 | Yorkshire Water | Live | MOOR LANE MOORENDS SPS | MOOR LANE MOORENDS/CSO | T/83/10162/O | T/83/10162/O | A1 | Storm discharge at pumping station | SE6963014830 | 469650 | 414700 | GB104028064350 | North Soak Drain Catchment (trib of Torne/Three Rivers) | River | 3234 | Isle of Axholme | 3041 | Idle and Torne | TRIB NORTH SOAK DRAIN | Not Applicable | Not Applicable | Not Applicable | 93:00 | 36 | 44.2 | 2020 | 99.99 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01080
YWS01081 | Yorkshire Water | Live | BALBY STW (YWS) | BALBY/STW/STORM TREATMENT | T/83/45405/R | T/83/45405/R | 2 | Storm tank at WwTW | SE5719001070 | 457190 | 401070 | GB104028058440 | Mother Drain from Source to Torne | River | 3234 | Isle of Axholme | 3041 | Idle and Torne | TRIB OF MOTHER DRAIN | Not Applicable | Not Applicable | Not Applicable | 175:30 | 20 | 35.6 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01081
YWS01082 | Yorkshire Water | Live | BALBY STW (YWS) | BALBY/STW/6XDWF OVERFLOW | T/83/45405/R | T/83/45405/R | 3 | Inlet SO at WwTW | SE5688001130 | 456880 | 401130 | GB104028058440 | Mother Drain from Source to Torne | River | 3234 | Isle of Axholme | 3041 | Idle and Torne | TRIB OF MOTHER DRAIN | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 3 | 2020 | 99.97 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01082
YWS01083 | Yorkshire Water | Live | BELLEVUE SPS | BELLE VUE/CSO | T/83/45412/O | T/83/45412/O | A1 | Storm discharge at pumping station | SE5894002200 | 458940 | 402200 | GB104028058440 | Mother Drain from Source to Torne | River | 3234 | Isle of Axholme | 3041 | Idle and Torne | THE LADY BANK DRAIN | Not Applicable | Not Applicable | Not Applicable | 50:45 | 11 | 3.8 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01083
YWS01084 | Yorkshire Water | Live | HATFIELD WOODHOUSE STW | HATFIELD WOODHOUSE/STW | T/83/45453/R | T/83/45453/R | A2 | Storm tank at WwTW | SE6857008180 | 468570 | 408180 | GB104028064330 | Hatfield Waste Drain Catchment (trib of Torne/Three Rivers) | River | 3234 | Isle of Axholme | 3041 | Idle and Torne | THE HATFIELD WASTE DRAIN | Not Applicable | Not Applicable | Not Applicable | 178:39 | 37 | 41.4 | 2020 | 99.98 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS01084
YWS01085 | Yorkshire Water | Live | SHANNON STREET CSO | SHANNON STREET/CSO | WA5854 | WA5854 | 1 | SO on sewer network | SE3077033320 | 430771 | 433324 | GB104027062900 | Meanwood Beck from Source to River Aire | River | 3265 | Lower Aire | 3001 | Aire and Calder | LADY BECK (CULVERTED) | Not Applicable | Not Applicable | Not Applicable | 106:30 | 58 | 32.33 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01085
YWS01086 | Yorkshire Water | Live | EBOR WAY CSO | EBOR WAY/CSO | WA 5855 | WA5855 | A1 | SO on sewer network | SE4407345293 | 444073 | 445293 | GB104027064255 | Wharfe from Collingham Beck to Tadcaster Weir | River | 3287 | Lower Wharfe | 3115 | Wharfe and Lower Ouse | RIVER WHARFE | Not Applicable | Not Applicable | Not Applicable | 150:30 | 43 | 48.6 | 2020 | 100 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01086
YWS01087 | Yorkshire Water | Live | VALLEY ROAD SOUTH CSO | VALLEY ROAD SOUTH/CSO | WA6002 | WA6002 | A1 | SO on sewer network | SK4517192822 | 445171 | 392822 | GB104027057452 | Don from River Rother to River Dearne | River | 3312 | Middle Don | 3029 | Don and Rother | HERRINGTHORPE BECK | Not Applicable | Not Applicable | Not Applicable | 37:30 | 18 | 10 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01087
YWS01088 | Yorkshire Water | Live | VALLEY ROAD NORTH CSO | VALLEY ROAD NORTH/CSO | WA6003 | WA6003 | A1 | SO on sewer network | SK4496494269 | 444964 | 394269 | GB104027057452 | Don from River Rother to River Dearne | River | 3312 | Middle Don | 3029 | Don and Rother | HERRINGTHORPE BECK | Not Applicable | Not Applicable | Not Applicable | 87:00 | 36 | 37.6 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | SOAF investigation completed - No work required | YWS01088
YWS01089 | Yorkshire Water | Live | FITZWILLIAM CENTRE CSO | FITZWILLIAM CENTRE/CSO | WA6004 | WA6004 | A1 | SO on sewer network | SK4480294156 | 444802 | 394156 | GB104027057452 | Don from River Rother to River Dearne | River | 3312 | Middle Don | 3029 | Don and Rother | RIVER DON | Not Applicable | Not Applicable | Not Applicable | 204:15 | 59 | 62.4 | 2020 | 100 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | No investigation activity in reporting period | No improvement action in reporting period | SOAF investigation completed - No work required | YWS01089
YWS01090 | Yorkshire Water | Live | BINGLEY ROAD CSO | BINGLEY ROAD/CSO | WA6005 | WA6005 | A1 | SO on sewer network | SE0719237243 | 407192 | 437243 | GB104027062870 | Harden Beck from Source to River Aire | River | 3307 | Middle Aire | 3001 | Aire and Calder | COW HOUSE BECK | Not Applicable | Not Applicable | Not Applicable | 52:45 | 14 | 16.6 | 2020 | 95.56 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01090
YWS01091 | Yorkshire Water | Live | GROVE LANE STORM TANKS | GROVE LANE/CSO | WA6066 | WA6066 | 1 | SO on sewer network | SE4405012570 | 444050 | 412570 | GB104027063240 | Ea Beck from Source to Frickley Beck | River | 3272 | Lower Don | 3029 | Don and Rother | HEMSWORTH DYKE | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 7 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01091
YWS01092 | Yorkshire Water | Live | THE NARROWS CSO | THE NARROWS/CSO | WA6075 | WA6075 | A1 | SO on sewer network | SE0920438058 | 409204 | 438058 | GB104027062870 | Harden Beck from Source to River Aire | River | 3307 | Middle Aire | 3001 | Aire and Calder | HARDEN BECK | Not Applicable | Not Applicable | Not Applicable | 44:00 | 22 | 22.4 | 2020 | 91.98 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01092
YWS01093 | Yorkshire Water | Live | LOTHERSDALE CSO | LOTHERSDALE/CSO | WA6084 | WA6084 | A1 | SO on sewer network | SD9640045650 | 396270 | 445680 | GB104027062970 | Lothersdale Beck from Source to Eastburn Beck | River | 3484 | Upper Aire | 3001 | Aire and Calder | LOTHERSDALE BECK | Not Applicable | Not Applicable | Not Applicable | 40:15 | 18 | 6.2 | 2020 | 77.32 | Sensor failure / issue | Resolved - Aug | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01093
YWS01094 | Yorkshire Water | Live | CASTLE MILLS CSO | CASTLE MILLS/CSO | WA6109 | WA6109 | A1 | Storm discharge at pumping station | SE6043951226 | 460439 | 451226 | GB104027069593 | Ouse from River Nidd to Stillingfleet Beck | River | 3499 | Upper Ouse Yorkshire | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER OUSE | Not Applicable | Not Applicable | Not Applicable | 0:18 | 6 | 17.6 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01094
YWS01095 | Yorkshire Water | Live | KLONDYKE SPS | KLONDYKE/CSO | WA6126 | WA6126 | 1 | SO on sewer network | SE3790008460 | 437900 | 408468 | GB104027063230 | Cudworth Dyke from Source to River Dearne | River | 3125 | Dearne | 3029 | Don and Rother | TRIB OF SMALL BRIDGE DIKE | Not Applicable | Not Applicable | Not Applicable | 6:45 | 5 | 1.2 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01095
YWS01096 | Yorkshire Water | Live | FENAY BRIDGE TANK CSO | FENAY BRIDGE TANK/CSO | WA6132 | WA6132 | A1 | SO on sewer network | SE1816015520 | 418158 | 415525 | GB104027063340 | Fenay beck from Source to River Colne | River | 3097 | Colne and Holme | 3001 | Aire and Calder | FENAY BECK | Not Applicable | Not Applicable | Not Applicable | 168:00 | 37 | 37.4 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01096
YWS01097 | Yorkshire Water | Live | LUNDHILL CSO | LUNDHILL/CSO | WA6189 | WA6189 | A1 | SO on sewer network | SE4052901656 | 440529 | 401656 | GB104027057470 | Knoll Beck from Source to River Dearne | River | 3125 | Dearne | 3029 | Don and Rother | KNOLL BECK | Not Applicable | Not Applicable | Not Applicable | 161:45 | 48 | 39.6 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01097
YWS01099 | Yorkshire Water | Live | STATION ROAD BRIMINGTON CSO | WINDMILL WAY/CSO | WA6195 | WA6195 | 1 | SO on sewer network | SK3922073960 | 439230 | 373962 | GB104027057771 | Rother, Spittal Brook to Doe Lea | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | RIVER ROTHER | Not Applicable | Not Applicable | Not Applicable | 16:45 | 8 | 6.6 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01099
YWS01100 | Yorkshire Water | Live | WOMBWELL WWTW | WOMBWELL/STW/3XDWF OVERFLOW | WA 6273 | WA6273 | A2 | Storm tank at WwTW | SE4099303788 | 440993 | 403788 | GB104027057510 | Dove from Source to River Dearne | River | 3125 | Dearne | 3029 | Don and Rother | RIVER DOVE AND BULLING DYKE | Not Applicable | Not Applicable | Not Applicable | 691:45 | 73 | 76.4 | 2020 | 99.38 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS01100
YWS01101 | Yorkshire Water | Live | WOMBWELL WWTW | WOMBWELL/STW/6XDWF OVERFLOW | WA 6273 | WA6273 | A3 | Inlet SO at WwTW | SE4088103364 | 440881 | 403364 | GB104027063173 | Dearne Darfield STW to River Don | River | 3125 | Dearne | 3029 | Don and Rother | RIVER DOVE AND BULLING DYKE | Not Applicable | Not Applicable | Not Applicable | 115:45 | 28 | 22 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | Operational investigation completed | No improvement action in reporting period | No SOAF investigation required | YWS01101
YWS01102 | Yorkshire Water | Live | WOMBWELL WWTW | WOMBWELL/STW | WA 6273 | WA6273 | A4 | Inlet SO at WwTW | SE4088103364 | 440881 | 403364 | GB104027063173 | Dearne Darfield STW to River Don | River | 3125 | Dearne | 3029 | Don and Rother | RIVER DOVE AND BULLING DYKE | Not Applicable | Not Applicable | Not Applicable | 157:15 | 25 | 22.8 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | Operational investigation completed | No improvement action in reporting period | No SOAF investigation required | YWS01102
YWS01103 | Yorkshire Water | Live | SEWAGE PUMPING STATION LOW HALL | HUNTON LOWHALL/CSO | WA6340 | WA6340 | 1 | Storm discharge at pumping station | SE1913092050 | 419130 | 492050 | GB104027068960 | Brompton Bk from Source to Newton Bk | River | 3317 | Middle Swale | 3088 | Swale, Ure, Nidd and Upper Ouse | HUNTON BECK | Not Applicable | Not Applicable | Not Applicable | 147:45 | 16 | 12.8 | 2020 | 99.92 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01103
YWS01105 | Yorkshire Water | Live | OSSETT SPA SPS | OSSETT SPA/CSO | WA6348 | WA6348 | A1 | Storm discharge at pumping station | SE3127017940 | 431270 | 417940 | GB104027062631 | Calder from River Colne to River Chald | River | 3268 | Lower Calder | 3001 | Aire and Calder | RIVER CALDER | Not Applicable | Not Applicable | Not Applicable | 189:45 | 25 | 34.4 | 2020 | 99.94 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01105
YWS01106 | Yorkshire Water | Live | BYRON STREET CSO | BYRON STREET/CSO | WA6349 | WA6349 | A1 | SO on sewer network | SE3091933975 | 430919 | 433975 | GB104027062900 | Meanwood Beck from Source to River Aire | River | 3265 | Lower Aire | 3001 | Aire and Calder | LADY BECK | Not Applicable | Not Applicable | Not Applicable | 0:15 | 1 | 1.8 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01106
YWS01107 | Yorkshire Water | Live | ACCOMMODATION ROAD CSO | ACCOMMODATION ROAD/CSO | WA6350 | WA6350 | A1 | SO on sewer network | SE3105234218 | 431052 | 434218 | GB104027062900 | Meanwood Beck from Source to River Aire | River | 3265 | Lower Aire | 3001 | Aire and Calder | STONEY ROCK BECK | Not Applicable | Not Applicable | Not Applicable | 109:30 | 58 | 53.2 | 2020 | 100 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01107
YWS01108 | Yorkshire Water | Live | WHITEHALL ROAD CSO | WHITEHALL ROAD/CSO | WA6376 | WA6376 | A1 | SO on sewer network | SE1869526331 | 418695 | 426331 | GB104027062710 | Spen Beck from Source to River Calder | River | 3268 | Lower Calder | 3001 | Aire and Calder | RIVER SPEN | Not Applicable | Not Applicable | Not Applicable | 0:30 | 1 | 1.2 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01108
YWS01109 | Yorkshire Water | Live | BIRSTALL CSO | BIRSTALL/CSO | WA6377 | WA6377 | A1 | SO on sewer network | SE2237225830 | 422372 | 425830 | GB104027062670 | Batley Beck from Source to River Calder | River | 3268 | Lower Calder | 3001 | Aire and Calder | SMITHIES BECK | Not Applicable | Not Applicable | Not Applicable | 9:15 | 8 | 12.6 | 2020 | 99.97 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01109
YWS01110 | Yorkshire Water | Live | CHERRY BURTON STW | CHERRY BURTON/STW | WA6378 | WA6378 | A2 | Storm tank at WwTW | SE9929541151 | 499295 | 441151 | GB104026066841 | High Hunsley to Arram Area | River | 3274 | Lower Hull | 3039 | Hull and East Riding | TRIBUTARY OF CATCHWATER DRAIN | Not Applicable | Not Applicable | Not Applicable | 959:00 | 78 | 52 | 2020 | 100 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement completed | SOAF investigation ongoing | YWS01110
YWS01111 | Yorkshire Water | Live | HOLME ON SPALDING MOOR WWTW | HOLME ON SPALDING MR/STW | WA6385 | WA6385 | A2 | Storm tank at WwTW | SE7989037440 | 479890 | 437440 | GB104026066690 | Foulness from Black Beck to Market Weighton Canal | River | 3191 | Foulness | 3039 | Hull and East Riding | MAIN DRAIN | Not Applicable | Not Applicable | Not Applicable | 67:45 | 6 | 10 | 2020 | 99.98 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01111
YWS01112 | Yorkshire Water | Live | PATRINGTON WWTW | PATRINGTON/STW/3XDWF OVERFLOW | WA6388 | WA6388 | A2 | Storm tank at WwTW | TA3078423361 | 530761 | 423312 | GB104026066570 | Winestead Drain from Source to Humber | River | 3057 | Burstwick and Eastern Drains | 3039 | Hull and East Riding | A TRIBUTARY OF WINESTEAD DRAIN | Not Applicable | Not Applicable | Not Applicable | 365:45 | 29 | 14.8 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01112
YWS01113 | Yorkshire Water | Live | SWINTON PUMPING STATION | SWINTON LOWFIELD/CSO | WA6392 | WA6392 | 1 | Storm discharge at pumping station | SE7621073740 | 476230 | 473740 | GB104027068320 | Rye from River Seven to River Derwent | River | 3387 | Rye | 3027 | Derwent Humber | TRIB RIVER RYE | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 9.8 | 2020 | 97.35 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01113
YWS01114 | Yorkshire Water | Live | SWINTON PUMPING STATION | SWINTON LOWFIELD/CSO | WA6392 | WA6392 | 2 | Storm discharge at pumping station | SE7621073740 | 476230 | 473740 | GB104027068320 | Rye from River Seven to River Derwent | River | 3387 | Rye | 3027 | Derwent Humber | TRIB RIVER RYE | Not Applicable | Not Applicable | Not Applicable | 29:15 | 7 | 12.8 | 2020 | 97.35 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01114
YWS01115 | Yorkshire Water | Live | THEARNE FERRY LANE NO. 2 SPS | THEARNE FERRY LN/NO 2 SPS | WA6394 | WA6394 | A1 | Storm discharge at pumping station | TA0776037100 | 507760 | 437100 | GB104026067212 | Hull from Arram Beck to Humber | River | 3274 | Lower Hull | 3039 | Hull and East Riding | R.HULL (OA)/NRTH CARR DRN (OB) | Not Applicable | Not Applicable | Not Applicable | 130:45 | 44 | 49.8 | 2020 | 99.99 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS01115
YWS01116 | Yorkshire Water | Live | THEARNE FERRY LANE NO. 2 SPS | THEARNE FERRY LN/NO 2 SPS | WA6394 | WA6394 | A2 | Storm discharge at pumping station | TA0741036880 | 507410 | 436880 | GB104026067212 | Hull from Arram Beck to Humber | River | 3274 | Lower Hull | 3039 | Hull and East Riding | R.HULL (OA)/NRTH CARR DRN (OB) | Not Applicable | Not Applicable | Not Applicable | 7:30 | 4 | 0.8 | 2020 | 99.57 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01116
YWS01117 | Yorkshire Water | Live | REETH/FREMINGTON/GRINTON STW | REETH/STW | WA6395 | WA6395 | 2 | Inlet SO at WwTW | SE0416098990 | 404310 | 498820 | GB104027069170 | Arkle Beck from Source to River Swale | River | 3503 | Upper Swale | 3088 | Swale, Ure, Nidd and Upper Ouse | ARKLE BECK | Not Applicable | Not Applicable | Not Applicable | 500:15 | 135 | 74 | 2020 | 97.68 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement completed | SOAF investigation ongoing | YWS01117
YWS01118 | Yorkshire Water | Live | BURTON PIDSEA WWTW | BURTON PIDSEA/STW | WA6400 | WA6400 | A2 | Storm tank at WwTW | TA2451031760 | 524510 | 431760 | GB104026066590 | Burton Pidsea Drain Lower Catchment | River | 3057 | Burstwick and Eastern Drains | 3039 | Hull and East Riding | BURTON PIDSEA DRAIN | Not Applicable | Not Applicable | Not Applicable | 379:15 | 35 | 28.8 | 2020 | 99.98 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01118
YWS01119 | Yorkshire Water | Live | SKIDBY STW | SKIDBY/STW | WA6412 | WA6412 | A2 | Storm tank at WwTW | TA0179033970 | 501790 | 433970 | GB104026067211 | Beverley and Barmston Drain | River | 3274 | Lower Hull | 3039 | Hull and East Riding | TRIBUTARY OF MILL BECK | Not Applicable | Not Applicable | Not Applicable | 119:15 | 18 | 35.4 | 2020 | 99.72 |  |  | High spill threshold not met | High spill threshold not met | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01119
YWS01120 | Yorkshire Water | Live | TICKTON SEWAGE PUMPING STATION | TICKTON/CSO | WA6435 | WA6435 | 1 | SO on sewer network | TA0690041960 | 506881 | 441953 | GB104026066950 | Holderness Drain Source to Fordyke Stream | River | 3274 | Lower Hull | 3039 | Hull and East Riding | TRIBUTARY OF HOLDERNESS DRAIN | Not Applicable | Not Applicable | Not Applicable | 0:15 | 1 | 0.2 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01120
YWS01121 | Yorkshire Water | Live | NETHERFIELD ROAD CSO | NETHERFIELD ROAD/CSO | WA6455 | WA6455 | A1 | Storm discharge at pumping station | SE1821643180 | 418216 | 443180 | GB104027064258 | Wharfe from Hundwith Beck to River Washburn | River | 3318 | Middle Wharfe and Washburn | 3115 | Wharfe and Lower Ouse | MIRE BECK VIA SWS | Not Applicable | Not Applicable | Not Applicable | 30:30 | 17 | 5.4 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01121
YWS01122 | Yorkshire Water | Live | NORTH AVENUE CSO | NORTH AVENUE/CSO | WA6456 | WA6456 | 1 | SO on sewer network | SE1595034900 | 415950 | 434900 | GB104027062862 | Bradford Beck (Clayton Bk to R Aire) | River | 3307 | Middle Aire | 3001 | Aire and Calder | BRADFORD BECK | Not Applicable | Not Applicable | Not Applicable | 176:45 | 30 | 34.4 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01122
YWS01123 | Yorkshire Water | Live | VALLEY ROAD CSO | VALLEY RD BRADFORD/2 CSO | WA6458 | WA6458 | 1 | SO on sewer network | SE1623034700 | 416215 | 434462 | GB104027062862 | Bradford Beck (Clayton Bk to R Aire) | River | 3307 | Middle Aire | 3001 | Aire and Calder | BRADFORD BECK | Not Applicable | Not Applicable | Not Applicable | 7:45 | 6 | 4.6 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01123
YWS01124 | Yorkshire Water | Live | MILL LANE WWTW | NORMANTON/STW | WA6472 | WA6472 | A2 | Storm tank at WwTW | SE3967024910 | 439670 | 424910 | GB104027062632 | Calder from River Chald to River Aire | River | 3268 | Lower Calder | 3001 | Aire and Calder | RIVER CALDER | Not Applicable | Not Applicable | Not Applicable | 1150:00 | 117 | 80.2 | 2020 | 99.93 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS01124
YWS01125 | Yorkshire Water | Live | FLAMBOROUGH WWTW | FLAMBOROUGH VILLAGE/STW | WA6514 | WA6514 | 3 | Inlet SO at WwTW | TA2232068130 | 522320 | 468130 | GB640402491000 | Yorkshire South | Coastal Water | 3179 | Esk TraC | 3040 | Humber TraC | NORTH SEA/HARTENDALE GUTTER | Not Applicable | Flamborough South Landing, Danes Dyke, Flamborough | Not Applicable | 61:20 | 11 | 11.2 | 2020 | 99.93 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01125
YWS01126 | Yorkshire Water | Live | BEMPTON SPS | BEMPTON/CSO | WA6517 | WA6517 | A1 | Storm discharge at pumping station | TA1935071600 | 519350 | 471600 | GB104026072780 | Danes Dyke | River | 3214 | Gypsey Race | 3039 | Hull and East Riding | TRIBUTARY OF DANES DYKE | Not Applicable | Not Applicable | Not Applicable | 125:58 | 53 | 65 | 2020 | 99.98 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation completed, Operational investigation completed | Operational improvement ongoing | SOAF investigation completed - No work required | YWS01126
YWS01127 | Yorkshire Water | Live | HAXBY RD CSO | HAXBY ROAD/CSO | WADC1003 | WADC1003 | A1 | SO on sewer network | SE6088453166 | 460884 | 453166 | GB104027063520 | Foss from the Syke to the River Ouse | River | 3190 | Foss | 3088 | Swale, Ure, Nidd and Upper Ouse | CULVERTED TRIB OF RIVER FOSS | Not Applicable | Not Applicable | Not Applicable | 3:00 | 6 | 3.6 | 2020 | 99.78 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01127
YWS01128 | Yorkshire Water | Live | OLD WHIT HIGH STREET CSO | OLD WHIT HIGH STREET/CSO | WADC1010 | WADC1010 | A1 | SO on sewer network | SK3883375169 | 438833 | 375169 | GB104027057771 | Rother, Spittal Brook to Doe Lea | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | TRIBUTARY OF RIVER ROTHER | Not Applicable | Not Applicable | Not Applicable | 2:30 | 7 | 30 | 2020 | 99.84 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01128
YWS01129 | Yorkshire Water | Live | GARGRAVE HIGH STREET CSO | GARGRAVE HIGH STREET/CSO | WADC1011 | WADC1011 | A1 | SO on sewer network | SD9319254088 | 393192 | 454088 | GB104027063050 | Aire from Otterburn Beck to Eshton Beck | River | 3484 | Upper Aire | 3001 | Aire and Calder | RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 7:30 | 4 | 4 | 2020 | 94.08 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01129
YWS01130 | Yorkshire Water | Live | HOLBECK HILL CSO | HOLBECK HILL/CSO | WADC1018 | WADC1018 | A1 | SO on sewer network | TA0472586858 | 504712 | 486858 | GB650401500004 | Yorkshire North | Coastal Water | 3179 | Esk TraC | 3040 | Humber TraC | HOLBECK RAVINE (CULVERTED) | Not Applicable | Scarborough South Bay | Not Applicable | 2:00 | 6 | 5.6 | 2020 | 99.94 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01130
YWS01131 | Yorkshire Water | Live | HOLLINS LANE CSO | HOLLINS MILL LANE/CSO | WADC1021 | WADC1021 | A1 | SO on sewer network | SE0525324004 | 405253 | 424004 | GB70410243 | Rochdale Canal, eastern section | Canal | 2007 | Calder Canals | 2001 | Humber AWB | ROCHDALE CANAL | Not Applicable | Not Applicable | Not Applicable | 11:00 | 15 | 6.6 | 2020 | 93.86 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01131
YWS01132 | Yorkshire Water | Live | OTLEY ROAD ADEL CSO | OTLEY ROAD ADEL/CSO | WADC1025 | WADC1025 | A1 | SO on sewer network | SE2711640120 | 427116 | 440120 | GB104027062900 | Meanwood Beck from Source to River Aire | River | 3265 | Lower Aire | 3001 | Aire and Calder | CULVERTED TRIB OF ADEL BECK | Not Applicable | Not Applicable | Not Applicable | 8:45 | 6 | 7 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01132
YWS01133 | Yorkshire Water | Live | HOLYWELL BROOK CSO | HOLYWELL BROOK/CSO | WADC1026 | WADC1026 | A1 | SO on sewer network | SE0885619470 | 408856 | 419470 | GB104027062570 | Black Brook from Source to River Calder | River | 3310 | Middle Calder | 3001 | Aire and Calder | CULVERTED HOLYWELL BROOK | Not Applicable | Not Applicable | Not Applicable | 48:15 | 5 | 3.4 | 2020 | 93.18 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01133
YWS01134 | Yorkshire Water | Live | CLAYTON HILL CSO | CLAYTON HILL/CSO | WADC1029 | WADC1029 | A1 | SO on sewer network | SE3267220321 | 432672 | 420321 | GB104027062620 | Chald from Source to River Calder | River | 3268 | Lower Calder | 3001 | Aire and Calder | CULVERTED TRIB OF CHALD BECK | Not Applicable | Not Applicable | Not Applicable | 0:15 | 1 | 0.2 | 2020 | 94.07 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01134
YWS01136 | Yorkshire Water | Live | HOWDEN ROAD | HOWDEN ROAD/CSO | WADC1034 | WADC1034 | 1 | Storm discharge at pumping station | SE7885029780 | 478850 | 429780 | GB104026066690 | Foulness from Black Beck to Market Weighton Canal | River | 3191 | Foulness | 3039 | Hull and East Riding | TRIB OF RIVER OUSE | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0.6 | 2020 | 99.07 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01136
YWS01137 | Yorkshire Water | Live | HUDDERSFIELD ROAD | PENISTONE RD NEW MILL/CSO | WADC1037 | WADC1037 | A1 | SO on sewer network | SE1625008918 | 416250 | 408918 | GB104027057610 | New Mill Dike from Source to River Holme | River | 3097 | Colne and Holme | 3001 | Aire and Calder | NEW MILL DIKE | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 5.8 | 2020 | 59.13 | Sensor failure / issue | Resolved - Jun | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01137
YWS01138 | Yorkshire Water | Live | IBBOT ROYD CSO | IBBOTROYD/CSO | WADC1040 | WADC1040 | A1 | SO on sewer network | SD9997827919 | 399978 | 427919 | GB104027062731 | Hebden Water from Widdop Beck to R Calder | River | 3487 | Upper Calder | 3001 | Aire and Calder | TRIB OF IBBOT ROYD CLOUGH | Not Applicable | Not Applicable | Not Applicable | 14:15 | 7 | 7.8 | 2020 | 99.93 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01138
YWS01139 | Yorkshire Water | Live | CONONLEY SPS | CONONLEY WORKS/NO 2 CSO | WADC105 | WADC105 | 1 | Storm discharge at pumping station | SD9946047040 | 399510 | 446740 | GB104027063033 | Aire (Eshton Beck to R Worth) | River | 3484 | Upper Aire | 3001 | Aire and Calder | RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 318:15 | 72 | 75.4 | 2020 | 99.98 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01139
YWS01140 | Yorkshire Water | Live | WOODSIDE CSO | WOODSIDE/CSO | WADC1050 | WADC1050 | A1 | SO on sewer network | SE3142222869 | 431422 | 422869 | GB104027062620 | Chald from Source to River Calder | River | 3268 | Lower Calder | 3001 | Aire and Calder | CUT BECK | Not Applicable | Not Applicable | Not Applicable | 0:15 | 1 | 1.6 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01140
YWS01141 | Yorkshire Water | Live | KNAVESMIRE CSO | KNAVESMIRE/CSO | WADC1065 | WADC1065 | A1 | SO on sewer network | SE5923450631 | 459234 | 450631 | GB104027064001 | Holgate Beck to Ouse | River | 3499 | Upper Ouse Yorkshire | 3088 | Swale, Ure, Nidd and Upper Ouse | CULVERTED KNAVESMIRE BECK | Not Applicable | Not Applicable | Not Applicable | 302:02 | 30 | 33.8 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01141
YWS01142 | Yorkshire Water | Live | LEEMING BAR CSO | LEEMING BAR/CSO | WADC1071 | WADC1071 | A1 | SO on sewer network | SE2933689687 | 429336 | 489687 | GB104027068910 | Bedale/Newton/Burton Bk from Rand Bk to R Swale | River | 3317 | Middle Swale | 3088 | Swale, Ure, Nidd and Upper Ouse | BEDALE BECK | Not Applicable | Not Applicable | Not Applicable | 16:45 | 7 | 8.75 | 2020 | 70.1 | Comms failure / issue | Resolved - Nov | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01142
YWS01143 | Yorkshire Water | Live | LILLANDS LANE CSO | LILLANDS LANE/CSO | WADC1074 | WADC1074 | A1 | SO on sewer network | SE1405722645 | 414057 | 422645 | GB104027062642 | Calder from Ryburn Confluence to River Colne | River | 3310 | Middle Calder | 3001 | Aire and Calder | RIVER CALDER | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0 | 2020 | 99.98 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01143
YWS01144 | Yorkshire Water | Live | LIMEKILN LANE CSO | LIMEKILN LANE/NO 2 CSO | WADC1075 | WADC1075 | A1 | SO on sewer network | TA1940967722 | 519367 | 467871 | GB640402491000 | Yorkshire South | Coastal Water | 3179 | Esk TraC | 3040 | Humber TraC | NORTH SEA | Not Applicable | Bridlington North Beach | Not Applicable | 1:15 | 3 | 2.5 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01144
YWS01145 | Yorkshire Water | Live | EASTMOOR CSO | EASTMOOR/CSO | WADC1082 | WADC1082 | A1 | SO on sewer network | SE3574121362 | 435741 | 421362 | GB104027062632 | Calder from River Chald to River Aire | River | 3268 | Lower Calder | 3001 | Aire and Calder | RIVER CALDER | Not Applicable | Not Applicable | Not Applicable | 211:00 | 74 | 66.5 | 2020 | 94.72 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01145
YWS01146 | Yorkshire Water | Live | LODGE FARM NO1 CSO | LODGE FARM/NO 2 CSO | WADC1086 | WADC1086 | A1 | SO on sewer network | SE2117537240 | 421175 | 437240 | GB70410231 | Leeds and Liverpool Canal, summit to Leeds | Canal | 2031 | Leeds and Liverpool Canal | 2001 | Humber AWB | TRIB OF LEEDS/LIVERPOOL CANAL | Not Applicable | Not Applicable | Not Applicable | 104:45 | 58 | 49.4 | 2020 | 99.87 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01146
YWS01148 | Yorkshire Water | Live | PALTERTON MAIN STREET CSO | PALTERTON MAIN STREET/CSO | WADC1112 | WADC1112 | A1 | SO on sewer network | SK4709368596 | 447093 | 368596 | GB104027057290 | Doe Lea from Source to Hawke Brook | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | TRIBUTARY OF RIVER DOE LEA | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 20.2 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01148
YWS01149 | Yorkshire Water | Live | HELPERBY MARKET CSO | HELPERBY MARKET/CSO | WADC1121 | WADC1121 | A1 | SO on sewer network | SE4371569841 | 443715 | 469841 | GB104027069591 | Swale from Wiske to River Ure | River | 3283 | Lower Swale | 3088 | Swale, Ure, Nidd and Upper Ouse | CULV TRIB OF RIVER SWALE | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0 | 2020 | 88.87 | Installation set-up/design issue | Resolved - Feb | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01149
YWS01150 | Yorkshire Water | Live | MIDGELEY ROAD CSO | MIDGELEY ROAD/CSO | WADC1136 | WADC1136 | A1 | SO on sewer network | SE0140926075 | 401409 | 426075 | GB104027062641 | Calder from Colden Water to Ryburn Confluence | River | 3310 | Middle Calder | 3001 | Aire and Calder | CULVERTED WHITE LEE CLOUGH | Not Applicable | Not Applicable | Not Applicable | 1:15 | 3 | 3.4 | 2020 | 99.94 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01150
YWS01151 | Yorkshire Water | Live | MILL HILL LANE SSO | MILL HILL LANE/CSO | WADC1137 | WADC1137 | A2 | Storm discharge at pumping station | SE3731093080 | 437278 | 492621 | GB104027069450 | Otterington Beck catchment (trib of Wiske) | River | 3541 | Wiske | 3088 | Swale, Ure, Nidd and Upper Ouse | TRIB OF RIVER WISKE | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 1.2 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01151
YWS01152 | Yorkshire Water | Live | AMPLEFORTH CSO | AMPLEFORTH/CSO | WADC1140 | WADC1140 | A1 | SO on sewer network | SE5821478092 | 458214 | 478092 | GB104027068420 | Holbeck from Source to Wath Beck | River | 3387 | Rye | 3027 | Derwent Humber | TRIBUTARY OF HOLBECK | Not Applicable | Not Applicable | Not Applicable | 15:30 | 11 | 10.8 | 2020 | 76.17 | Sensor failure / issue | Resolved - Jul | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01152
YWS01154 | Yorkshire Water | Live | HARLINGTON MILL LANE CSO | HARLINGTON MILL LN/CSO | WADC1142 | WADC1142 | A1 | SO on sewer network | SE4834201988 | 448342 | 401988 | GB104027063173 | Dearne Darfield STW to River Don | River | 3125 | Dearne | 3029 | Don and Rother | CULV TRIB OF OLD RIVER DEARNE | Not Applicable | Not Applicable | Not Applicable | 153:30 | 27 | 40.5 | 2020 | 100 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement ongoing | SOAF investigation ongoing | YWS01154
YWS01155 | Yorkshire Water | Live | DACRE SEWAGE PUMPING STATION | DACRE BANKS/CSO | WADC115 | WADC115 | A2 | SO on sewer network | SE1990061700 | 419953 | 461626 | GB104027068295 | Nidd from Ashfoldside Beck to Birstwith | River | 3497 | Upper Nidd | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER NIDD | Not Applicable | Not Applicable | Not Applicable | 1470:00 | 118 | 87.2 | 2020 | 97.15 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement ongoing | SOAF investigation ongoing | YWS01155
YWS01156 | Yorkshire Water | Live | NEW ROAD CSO | NEW ROAD/CSO | WADC1161 | WADC1161 | A1 | SO on sewer network | SE0415625805 | 404156 | 425805 | GB104027062770 | Luddenden Brook from Source to River Calder | River | 3310 | Middle Calder | 3001 | Aire and Calder | LUDDENDEN BROOK | Not Applicable | Not Applicable | Not Applicable | 426:15 | 59 | 51.5 | 2020 | 80.42 | Sensor failure / issue | Resolved - Mar | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01156
YWS01157 | Yorkshire Water | Live | NORTHALLERTON ROAD CSO | NORTHALLERTON ROAD/CSO | WADC1179 | WADC1179 | A1 | SO on sewer network | SE2925990224 | 429259 | 490224 | GB104027068910 | Bedale/Newton/Burton Bk from Rand Bk to R Swale | River | 3317 | Middle Swale | 3088 | Swale, Ure, Nidd and Upper Ouse | TERRY GUTTER | Not Applicable | Not Applicable | Not Applicable | 136:45 | 34 | 38.8 | 2020 | 98.32 |  |  | High spill threshold not met | High spill threshold not met | UWWTR investigation ongoing, Operational investigation completed | Operational improvement ongoing | SOAF investigation ongoing | YWS01157
YWS01159 | Yorkshire Water | Live | OAKDALE AVENUE CSO | OAKDALE AVENUE/CSO | WADC1184 | WADC1184 | A1 | SO on sewer network | SE2938056231 | 429380 | 456231 | GB104027063760 | Oak Beck Catchment (Trib of Nidd) | River | 3308 | Middle and Lower Nidd | 3088 | Swale, Ure, Nidd and Upper Ouse | OAK BECK | Not Applicable | Not Applicable | Not Applicable | 64:45 | 24 | 25.4 | 2020 | 92.63 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01159
YWS01160 | Yorkshire Water | Live | COLLINGHAM LEEDS ROAD CSO | COLLINGHAM LEEDS ROAD/CSO | WADC1192 | WADC1192 | A1 | SO on sewer network | SE3768745219 | 437687 | 445219 | GB104027063970 | Collingham Bk Catchment (trib of Wharfe) | River | 3318 | Middle Wharfe and Washburn | 3115 | Wharfe and Lower Ouse | COLLINGHAM BECK | Not Applicable | Wharfe at Wilderness Carpark | Not Applicable | 435:15 | 65 | 25.6 | 2020 | 97.4 |  |  | Not asset maintenance - Hydraulic capacity | High spill threshold not met | UWWTR investigation ongoing, Operational investigation ongoing | Operational improvement ongoing | SOAF investigation ongoing | YWS01160
YWS01161 | Yorkshire Water | Live | APPLEHAIGH VIEW SPS | APPLEHAIGH VIEW/CSO | WADC12 | WADC12 | A2 | Storm discharge at pumping station | SE3510011510 | 435055 | 411437 | GB104027062530 | Owler Beck from Source to River Calder | River | 3268 | Lower Calder | 3001 | Aire and Calder | BLEAKLEY DYKE | Not Applicable | Not Applicable | Not Applicable | 23:00 | 5 | 4 | 2020 | 99.61 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01161
YWS01162 | Yorkshire Water | Live | OLD GATE CSO | OLD GATE/CSO | WADC1201 | WADC1201 | A1 | SO on sewer network | SD9920427292 | 399204 | 427292 | GB104027062731 | Hebden Water from Widdop Beck to R Calder | River | 3487 | Upper Calder | 3001 | Aire and Calder | HEBDEN WATER | Not Applicable | Not Applicable | Not Applicable | 65:45 | 25 | 26.4 | 2020 | 99.95 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01162
YWS01163 | Yorkshire Water | Live | CUTTHORPE ROAD CSO | CUTTHORPE ROAD/CSO | WADC1210 | WADC1210 | A1 | SO on sewer network | SK3490673370 | 434906 | 373370 | GB104027057670 | Holme Brook/Linacre Beck | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | TRIBUTARY OF HOLME BROOK | Not Applicable | Not Applicable | Not Applicable | 13:30 | 14 | 15.8 | 2020 | 93.9 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01163
YWS01164 | Yorkshire Water | Live | PARK HILL FARM CSO | PARK HILL FARM/CSO | WADC1219 | WADC1219 | A1 | SO on sewer network | SE3574121362 | 435741 | 421362 | GB104027062632 | Calder from River Chald to River Aire | River | 3268 | Lower Calder | 3001 | Aire and Calder | RIVER CALDER | Not Applicable | Not Applicable | Not Applicable | 244:15 | 68 | 76 | 2020 | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement ongoing | SOAF investigation ongoing | YWS01164
YWS01165 | Yorkshire Water | Live | PORT ROYAL SSO | PORT ROYAL/CSO | WADC1240 | WADC1240 | A2 | SO on sewer network | SE8151037590 | 481507 | 437589 | GB104026066690 | Foulness from Black Beck to Market Weighton Canal | River | 3191 | Foulness | 3039 | Hull and East Riding | TRIBUTARY OF RIVER FOULNESS | Not Applicable | Not Applicable | Not Applicable | 0:30 | 1 | 0.4 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01165
YWS01167 | Yorkshire Water | Live | DUNSLOW ROAD SPS | DUNSLOW ROAD/CSO | WADC126 | WADC126 | 1 | Storm discharge at pumping station | TA0348083370 | 503480 | 483360 | GB104027073281 | Eastfield Drain Lower to River Hertford | River | 3489 | Upper Derwent Yorkshire | 3027 | Derwent Humber | RIVER HERTFORD VIA DITCH | Not Applicable | Not Applicable | Not Applicable | 314:15 | 35 | 8.8 | 2020 | 99.77 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01167
YWS01168 | Yorkshire Water | Live | MOORBRIDGE ROAD CSO | MOORBRIDGE ROAD/CSO | WADC1261 | WADC1261 | A1 | SO on sewer network | SE4172502174 | 441725 | 402174 | GB104027057470 | Knoll Beck from Source to River Dearne | River | 3125 | Dearne | 3029 | Don and Rother | KNOLL BECK | Not Applicable | Not Applicable | Not Applicable | 18:45 | 10 | 9.2 | 2020 | 99.85 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01168
YWS01169 | Yorkshire Water | Live | TOLLERTON BRIDGE CSO | TOLLERTON BRIDGE/CSO | WADC1262 | WADC1262 | A1 | SO on sewer network | SE5156764549 | 451567 | 464549 | GB104027063860 | Kyle from Derrings Beck to New Parks Beck | River | 3499 | Upper Ouse Yorkshire | 3088 | Swale, Ure, Nidd and Upper Ouse | SIDINGS DRAIN | Not Applicable | Not Applicable | Not Applicable | 51:30 | 17 | 11.2 | 2020 | 98.77 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01169
YWS01170 | Yorkshire Water | Live | RAKEHILL ROAD CSO | RAKEHILL ROAD/CSO | WADC1264 | WADC1264 | A1 | SO on sewer network | SE3814237528 | 438142 | 437528 | GB104027063940 | Cock Beck Catchment (trib of Wharfe) | River | 3287 | Lower Wharfe | 3115 | Wharfe and Lower Ouse | RAKE BECK | Not Applicable | Not Applicable | Not Applicable | 77:15 | 26 | 24.2 | 2020 | 96.04 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01170
YWS01171 | Yorkshire Water | Live | OLD BRIDGE INN CSO | OLD BRIDGE INN/CSO | WADC1284 | WADC1284 | A1 | SO on sewer network | SE0406819791 | 404068 | 419791 | GB104027062580 | Ryburn from Booth Dean Clough to R Calder | River | 3310 | Middle Calder | 3001 | Aire and Calder | RIVER RYBURN | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0.8 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01171
YWS01172 | Yorkshire Water | Live | RIVELIN VALLEY 3 CSO | RIVELIN VALLEY 3/CSO | WADC1286 | WADC1286 | A1 | SO on sewer network | SK3143087987 | 431430 | 387987 | GB104027057340 | Rivelin from Source to River Loxley | River | 3490 | Upper Don | 3029 | Don and Rother | RIVER RIVELIN | Not Applicable | Not Applicable | Not Applicable | 243:52 | 60 | 71.2 | 2020 | 98.06 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | No investigation activity in reporting period | No improvement action in reporting period | SOAF investigation completed - Work required | YWS01172
YWS01173 | Yorkshire Water | Live | RIVER STREET CSO | RIVER STREET/CSO | WADC1289 | WADC1289 | A1 | SO on sewer network | SE1566022060 | 415683 | 422178 | GB104027062642 | Calder from Ryburn Confluence to River Colne | River | 3310 | Middle Calder | 3001 | Aire and Calder | RIVER CALDER | Not Applicable | Not Applicable | Not Applicable | 31:34 | 16 | 38.2 | 2020 | 51.41 | Sensor failure / issue | Scheduled | High spill threshold not met | High spill threshold not met | UWWTR investigation ongoing, Operational investigation completed | Operational improvement ongoing | SOAF investigation ongoing | YWS01173
YWS01174 | Yorkshire Water | Live | SCALBY LANE CSO | SCALBY LANE/CSO | WADC1307 | WADC1307 | 1 | SO on sewer network | SE8373029280 | 483738 | 429274 | Not part of a WFD catchment | Not part of a WFD catchment | River | N/A | N/A | N/A | N/A | BISHOPSOIL DRAIN | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0 | 2020 | 96.55 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01174
YWS01175 | Yorkshire Water | Live | SCOTT LANE CSO | SCOTT LANE/CSO | WADC1313 | WADC1313 | 1 | SO on sewer network | SE4030448013 | 440304 | 448013 | GB104027064255 | Wharfe from Collingham Beck to Tadcaster Weir | River | 3287 | Lower Wharfe | 3115 | Wharfe and Lower Ouse | RIVER WHARFE | Not Applicable | Wharfe at Wilderness Carpark | Not Applicable | 9:15 | 14 | 10.2 | 2020 | 99.75 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01175
YWS01176 | Yorkshire Water | Live | SCOUTHILL CSO | SCOUTHILL/CSO | WADC1314 | WADC1314 | A1 | SO on sewer network | SE2294620725 | 422946 | 420725 | GB104027062710 | Spen Beck from Source to River Calder | River | 3268 | Lower Calder | 3001 | Aire and Calder | SPEN RIVER | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 12.4 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01176
YWS01177 | Yorkshire Water | Live | SCOUT ROAD CSO | SCOUT ROAD/CSO | WADC1315 | WADC1315 | A1 | SO on sewer network | SE0143525695 | 401435 | 425695 | GB104027062641 | Calder from Colden Water to Ryburn Confluence | River | 3310 | Middle Calder | 3001 | Aire and Calder | TRIBUTARY OF RIVER CALDER | Not Applicable | Not Applicable | Not Applicable | 0:15 | 1 | 0.2 | 2020 | 99.97 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01177
YWS01178 | Yorkshire Water | Live | SEASIDE ROAD EASINGTON CSO | SEASIDE RD EASINGTON/CSO | WADC1317 | WADC1317 | 1 | SO on sewer network | TA4013619032 | 540136 | 419032 | Not part of a WFD catchment | Not part of a WFD catchment | River | N/A | N/A | N/A | N/A | EASINGTON DRAIN | Not Applicable | Not Applicable | Not Applicable | 182:15 | 30 | 46.5 | 2020 | 99.84 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | Operational investigation completed | Operational improvement completed | SOAF investigation completed - No work required | YWS01178
YWS01179 | Yorkshire Water | Live | TOLLERTON GARAGE CSO | TOLLERTON GARAGE/CSO | WADC1320 | WADC1320 | A1 | SO on sewer network | SE5072264218 | 450722 | 464218 | GB104027063860 | Kyle from Derrings Beck to New Parks Beck | River | 3499 | Upper Ouse Yorkshire | 3088 | Swale, Ure, Nidd and Upper Ouse | CULVERTED TRIB OF RIVER KYLE | Not Applicable | Not Applicable | Not Applicable | 2:00 | 3 | 14.4 | 2020 | 99.52 |  |  | High spill threshold not met | High spill threshold not met | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS01179
YWS01180 | Yorkshire Water | Live | SEVERUS STREET SSO | SEVERUS STREET/CSO | WADC1321 | WADC1321 | A1 | SO on sewer network | SE5784351170 | 457843 | 451170 | GB104027064001 | Holgate Beck to Ouse | River | 3499 | Upper Ouse Yorkshire | 3088 | Swale, Ure, Nidd and Upper Ouse | HOLGATE BECK | Not Applicable | Not Applicable | Not Applicable | 4:15 | 6 | 8.8 | 2020 | 96.78 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01180
YWS01181 | Yorkshire Water | Live | CHURCH WOOD CSO | CHURCH WOOD/CSO | WADC1337 | WADC1337 | A1 | SO on sewer network | SE3600868039 | 436008 | 468039 | GB104027064161 | Ure from River Skell to River Tutt | River | 3309 | Middle and Lower Ure | 3088 | Swale, Ure, Nidd and Upper Ouse | CULVERTED SCOUR GUTTER | Not Applicable | Not Applicable | Not Applicable | 164:15 | 37 | 23 | 2020 | 99.93 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01181
YWS01182 | Yorkshire Water | Live | SKEW BRIDGE CSO | SKEW BRIDGE/CSO | WADC1338 | WADC1338 | A1 | SO on sewer network | SD9341921728 | 393419 | 421728 | GB104027062600 | Walsden Water from Source to River Calder | River | 3487 | Upper Calder | 3001 | Aire and Calder | WALSDEN WATER | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0 | 2020 | 91.94 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01182
YWS01183 | Yorkshire Water | Live | SOUTH CRESCENT CSO | SOUTH CRESCENT/CSO | WADC1343 | WADC1343 | A1 | SO on sewer network | SE3110970986 | 431109 | 470986 | GB104027064140 | Skell from River Laver to River Ure | River | 3309 | Middle and Lower Ure | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER SKELL | Not Applicable | Not Applicable | Not Applicable | 1:30 | 5 | 4.8 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01183
YWS01184 | Yorkshire Water | Live | SOUTH STREET CSO | SAVILLE TOWN/CSO | WADC1348 | WADC1348 | A1 | SO on sewer network | SE2405521043 | 424055 | 421043 | GB104027062631 | Calder from River Colne to River Chald | River | 3268 | Lower Calder | 3001 | Aire and Calder | RIVER CALDER | Not Applicable | Not Applicable | Not Applicable | 2:00 | 6 | 2.6 | 2020 | 90.48 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01184
YWS01185 | Yorkshire Water | Live | INGS LANE SPS | DUNSWELL INGS LANE/CSO | WADC136 | WADC136 | A2 | Storm discharge at pumping station | TA0739035320 | 507620 | 435320 | GB104026067211 | Beverley and Barmston Drain | River | 3274 | Lower Hull | 3039 | Hull and East Riding | DITCH TO RIVER HULL | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0.2 | 2020 | 77.1 | Comms failure / issue | Resolved - Sep | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01185
YWS01186 | Yorkshire Water | Live | STADDLETHORPE BROAD LANE CSO | GILBERDYKE/CSO | WADC1368 | WADC1368 | A1 | Storm discharge at pumping station | SE8358028570 | 483580 | 428570 | Not part of a WFD catchment | Not part of a WFD catchment | River | N/A | N/A | N/A | N/A | TRIB OF THE OUSE (TIDAL) | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | Operational investigation completed | Operational improvement ongoing | No SOAF investigation required | YWS01186
YWS01187 | Yorkshire Water | Live | STATION ROAD SSO | STATION ROAD WISTOW/CSO | WADC1383 | WADC1383 | A2 | Storm discharge at pumping station | SE5970135400 | 458772 | 435373 | GB104027063650 | Holmes Dike catchment (trib of Ouse) | River | 3280 | Lower Ouse Yorkshire | 3115 | Wharfe and Lower Ouse | TRIB OF RIVER OUSE | Not Applicable | Not Applicable | Not Applicable | 119:00 | 16 | 15.2 | 2020 | 95.94 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01187
YWS01188 | Yorkshire Water | Live | STILLINGTON ROAD SSO | GREY CLOSE/CSO | WADC1390 | WADC1390 | 1 | SO on sewer network | SE5805064670 | 457933 | 464702 | GB104027063900 | Huby Burn from Source to New Parks Beck | River | 3499 | Upper Ouse Yorkshire | 3088 | Swale, Ure, Nidd and Upper Ouse | TRIB OF THE RIVER KYLE | Not Applicable | Not Applicable | Not Applicable | 311:15 | 37 | 26.2 | 2020 | 99.54 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01188
YWS01189 | Yorkshire Water | Live | STORFORTH LANE CSO | STORFORTH LANE/CSO | WADC1396 | WADC1396 | A1 | SO on sewer network | SK3876169284 | 438761 | 369284 | GB104027057630 | Rother from Redleadmill Brook to Spital Brook | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | RIVER ROTHER | Not Applicable | Not Applicable | Not Applicable | 78:15 | 32 | 56 | 2020 | 99.99 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement ongoing | SOAF investigation ongoing | YWS01189
YWS01191 | Yorkshire Water | Live | THE BATTS CSO | THE BATTS/CSO | WADC1411 | WADC1411 | A1 | SO on sewer network | NZ1745000871 | 417450 | 500871 | GB104027069122 | Swale from Clapgate Beck to Bedale Beck | River | 3317 | Middle Swale | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER SWALE | Not Applicable | Not Applicable | Not Applicable | 586:30 | 93 | 99.2 | 2020 | 99.88 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS01191
YWS01192 | Yorkshire Water | Live | THE GREEN SSO | PICKHILL/CSO | WADC1415 | WADC1415 | 1 | Storm discharge at pumping station | SE3464083670 | 434640 | 483670 | GB104027069591 | Swale from Wiske to River Ure | River | 3283 | Lower Swale | 3088 | Swale, Ure, Nidd and Upper Ouse | PICKHILL BECK | Not Applicable | Not Applicable | Not Applicable | 64:45 | 23 | 18.8 | 2020 | 95.45 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01192
YWS01193 | Yorkshire Water | Live | RYEDALE NEW ROAD CSO | RYEDALE NEW ROAD/CSO | WADC1419 | WADC1419 | A1 | SO on sewer network | SE6759670731 | 467596 | 470731 | GB104027068330 | Wath Beck from Souce to Holbeck | River | 3387 | Rye | 3027 | Derwent Humber | TRIBUTARY OF WATH BECK | Not Applicable | Not Applicable | Not Applicable | 8:30 | 11 | 49.8 | 2020 | 99.95 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01193
YWS01194 | Yorkshire Water | Live | RYEDALE CARR LANE CSO | RYEDALE CARR LANE/CSO | WADC1420 | WADC1420 | A1 | SO on sewer network | SE5793278696 | 457932 | 478696 | GB104027068420 | Holbeck from Source to Wath Beck | River | 3387 | Rye | 3027 | Derwent Humber | TRIBUTARY OF HOLBECK | Not Applicable | Not Applicable | Not Applicable | 2:00 | 5 | 1.2 | 2020 | 95.02 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01194
YWS01195 | Yorkshire Water | Live | THORNE ROAD CSO | CROSSWAYS/CSO | WADC1424 | WADC1424 | 1 | SO on sewer network | SE5976005100 | 459810 | 406170 | GB70410281 | Sheffield and South Yorkshire Navigation (New Junction and Stainforth and Keadby | Canal | 2018 | Don and Rother Canals | 2001 | Humber AWB | RIVER DON | Not Applicable | Not Applicable | Not Applicable | 30:30 | 10 | 5.6 | 2020 | 89.37 | Sensor failure / issue | Resolved - Jul | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01195
YWS01196 | Yorkshire Water | Live | OTTERINGTON ROAD SSO | THORNTON LE MOOR/CSO | WADC1427 | WADC1427 | 1 | SO on sewer network | SE3893088050 | 438914 | 488047 | GB104027069530 | Wiske from Trenholme Stell to River Swale | River | 3541 | Wiske | 3088 | Swale, Ure, Nidd and Upper Ouse | TRIB OF RIVER WISKE | Not Applicable | Not Applicable | Not Applicable | 0:15 | 1 | 5.8 | 2020 | 84.89 | Sensor failure / issue | Resolved - Feb | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01196
YWS01197 | Yorkshire Water | Live | TIVYDALE ROAD CSO | TIVYDALE ROAD/CSO | WADC1432 | WADC1432 | A1 | SO on sewer network | SE2790007392 | 427900 | 407392 | GB104027063150 | Cawthorne Dyke from Source to River Dearne | River | 3125 | Dearne | 3029 | Don and Rother | TANYARD BECK | Not Applicable | Not Applicable | Not Applicable | 63:30 | 21 | 6.75 | 2020 | 98.53 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01197
YWS01198 | Yorkshire Water | Live | THURSTONLAND CSO | THURSTONLAND/CSO | WADC1433 | WADC1433 | A1 | SO on sewer network | SE1604810531 | 416048 | 410531 | GB104027063301 | Holme from New Mill Dike to R Colne | River | 3097 | Colne and Holme | 3001 | Aire and Calder | TRIBUTARY OF THE RIVER HOLME | Not Applicable | Not Applicable | Not Applicable | 0:15 | 1 | 0.2 | 2020 | 99.9 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01198
YWS01199 | Yorkshire Water | Live | TOWN GATE CALVER CSO | TOWN GATE CALVER/CSO | WADC1435 | WADC1435 | A1 | SO on sewer network | SE2096436920 | 420964 | 436920 | GB70410231 | Leeds and Liverpool Canal, summit to Leeds | Canal | 2031 | Leeds and Liverpool Canal | 2001 | Humber AWB | CULV TRIB LEEDS/LPOOL CANAL | Not Applicable | Not Applicable | Not Applicable | 13:45 | 19 | 26.4 | 2020 | 99.91 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01199
YWS01200 | Yorkshire Water | Live | WEST BARS ROUNDABOUT CSO | WEST BARS ROUNDABOUT/CSO | WADC1470 | WADC1470 | A1 | SO on sewer network | SK3767671016 | 437676 | 371016 | GB104027057670 | Holme Brook/Linacre Beck | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | HOLME BROOK / RIVER HIPPER | Not Applicable | Not Applicable | Not Applicable | 58:45 | 30 | 21.8 | 2020 | 99.98 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01200
YWS01201 | Yorkshire Water | Live | WETHERBY BYPASS CSO | WETHERBY BYPASS/CSO | WADC1477 | WADC1477 | A1 | SO on sewer network | SE4062847685 | 440628 | 447685 | GB104027064255 | Wharfe from Collingham Beck to Tadcaster Weir | River | 3287 | Lower Wharfe | 3115 | Wharfe and Lower Ouse | RIVER WHARFE | Not Applicable | Wharfe at Wilderness Carpark | Not Applicable | 0:45 | 3 | 1.2 | 2020 | 99.78 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01201
YWS01202 | Yorkshire Water | Live | MILLGATE SPS | ELLAND MILLGATE/CSO | WADC148 | WADC148 | 1 | Storm discharge at pumping station | SE1070021200 | 410690 | 421280 | GB104027062642 | Calder from Ryburn Confluence to River Colne | River | 3310 | Middle Calder | 3001 | Aire and Calder | RIVER CALDER | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0.4 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01202
YWS01203 | Yorkshire Water | Live | WIGGINTON ROAD SSO | WIGGINGTON ROAD/CSO | WADC1489 | WADC1489 | A1 | SO on sewer network | SE6034052920 | 460884 | 453164 | GB104027063520 | Foss from the Syke to the River Ouse | River | 3190 | Foss | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER FOSS | Not Applicable | Not Applicable | Not Applicable | 20:15 | 13 | 5.4 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01203
YWS01204 | Yorkshire Water | Live | WILKINSON AVENUE CSO | WILKINSON AVENUE/CSO | WADC1490 | WADC1490 | A1 | SO on sewer network | SE6960214687 | 469602 | 414687 | GB104028064350 | North Soak Drain Catchment (trib of Torne/Three Rivers) | River | 3234 | Isle of Axholme | 3041 | Idle and Torne | LEONARDS DRAIN | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 4.6 | 2020 | 99.09 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01204
YWS01205 | Yorkshire Water | Live | WOODLANDS DRIVE CSO | WOODLANDS DRIVE/CSO | WADC1505 | WADC1505 | A1 | SO on sewer network | SE2050338449 | 420503 | 438449 | GB104027063032 | Aire from Gill Beck (Baildon) to River Calder | River | 3265 | Lower Aire | 3001 | Aire and Calder | RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 305:15 | 100 | 71.8 | 2020 | 99.96 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS01205
YWS01206 | Yorkshire Water | Live | UNDERWOOD DRIVE CSO | UNDERWOOD DRIVE/CSO | WADC1506 | WADC1506 | A1 | SO on sewer network | SE2153138320 | 421531 | 438320 | GB104027063032 | Aire from Gill Beck (Baildon) to River Calder | River | 3265 | Lower Aire | 3001 | Aire and Calder | TRIBUTARY OF RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 4 | 2020 | 99.9 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01206
YWS01207 | Yorkshire Water | Live | WYKE BECK CSO | WYKE BECK/CSO | WADC1512 | WADC1512 | A1 | SO on sewer network | SE1453525545 | 414535 | 425545 | GB104027062700 | Clifton Beck from Source to River Calder | River | 3310 | Middle Calder | 3001 | Aire and Calder | BOTTOM HALL BECK | Not Applicable | Not Applicable | Not Applicable | 387:15 | 89 | 83.4 | 2020 | 98.15 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | No investigation activity in reporting period | No improvement action in reporting period | SOAF investigation completed - Work required | YWS01207
YWS01208 | Yorkshire Water | Live | HESSAY MAIN STREET CSO | HESSAY MAIN STREET/CSO | WADC1519 | WADC1519 | A1 | SO on sewer network | SE5296153423 | 452961 | 453423 | GB104027063720 | Foss Dike | River | 3499 | Upper Ouse Yorkshire | 3088 | Swale, Ure, Nidd and Upper Ouse | NEW DIKE | Not Applicable | Not Applicable | Not Applicable | 238:30 | 65 | 24 | 2020 | 99.97 |  |  | Performance - Partial / no capacity due to blockage or restriction (e.g. roots / grid) - maintenance issue | High spill threshold not met | UWWTR investigation ongoing, Operational investigation completed | Operational improvement completed | SOAF investigation ongoing | YWS01208
YWS01209 | Yorkshire Water | Live | FOSS BANK CSO | FOSS BANK/CSO | WADC1520 | WADC1520 | A1 | SO on sewer network | SE6088852490 | 460888 | 452490 | GB104027063520 | Foss from the Syke to the River Ouse | River | 3190 | Foss | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER FOSS | Not Applicable | Not Applicable | Not Applicable | 35:30 | 15 | 12.2 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01209
YWS01210 | Yorkshire Water | Live | ASHLEY PARK SSO | ASHLEY PARK CRESCENT/CSO | WADC16 | WADC16 | 1 | Storm discharge at pumping station | SE6355041950 | 462852 | 453004 | GB104027063500 | Tang Hall Bk/Old Foss Bk catch, trib of River Foss | River | 3190 | Foss | 3088 | Swale, Ure, Nidd and Upper Ouse | TANG HALL BECK | Not Applicable | Not Applicable | Not Applicable | 17:30 | 8 | 2.6 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01210
YWS01211 | Yorkshire Water | Live | ETTON SPS | ETTON/CSO | WADC160 | WADC160 | 1 | Storm discharge at pumping station | SE9809043500 | 498100 | 443480 | GB104026066901 | Scorborough Beck | River | 3274 | Lower Hull | 3039 | Hull and East Riding | FIELD DITCH | Not Applicable | Not Applicable | Not Applicable | 1:15 | 1 | 0.4 | 2020 | 99.93 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01211
YWS01212 | Yorkshire Water | Live | FAIRFIELD SEWAGE PUMPING STATION | SKELTON FAIRFIELD/CSO | WADC161 | WADC161 | 1 | Storm discharge at pumping station | SE5710055800 | 457130 | 455500 | GB104027069593 | Ouse from River Nidd to Stillingfleet Beck | River | 3499 | Upper Ouse Yorkshire | 3088 | Swale, Ure, Nidd and Upper Ouse | UNKNOWN BECK | Not Applicable | Not Applicable | Not Applicable | 95:36 | 22 | 11.6 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01212
YWS01213 | Yorkshire Water | Live | FANGFOSS SEWAGE PUMPING STATION | FANGFOSS MAIN ST/CSO | WADC162 | WADC162 | 1 | Storm discharge at pumping station | SE7430054800 | 476550 | 453400 | GB104027063490 | Gowthorpe Beck Catch (trib of Blackfoss Beck) | River | 3271 | Lower Derwent Yorkshire | 3027 | Derwent Humber | DITCH | Not Applicable | Not Applicable | Not Applicable | 1:15 | 1 | 0.4 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01213
YWS01214 | Yorkshire Water | Live | FOLKTON SEWAGE PUMPING STATION | FOLKTON CARR LN/CSO | WADC173 | WADC173 | 1 | Storm discharge at pumping station | TA0570079900 | 505760 | 479940 | GB104027067811 | Hertford from Source to River Derwent | River | 3489 | Upper Derwent Yorkshire | 3027 | Derwent Humber | DITCH | Not Applicable | Not Applicable | Not Applicable | 102:15 | 28 | 20.2 | 2020 | 99.97 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01214
YWS01215 | Yorkshire Water | Live | FOSTON SEWAGE PUMPING STATION | FOSTON/CSO | WADC176 | WADC176 | 1 | Storm discharge at pumping station | SE6980063900 | 470000 | 465270 | GB104027063580 | Spittle/Bulmer/Ings Becks catch (trib of Derwent) | River | 3311 | Middle Derwent Yorkshire | 3027 | Derwent Humber | SPITTAL BECK | Not Applicable | Not Applicable | Not Applicable | 8:45 | 6 | 4.4 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01215
YWS01216 | Yorkshire Water | Live | GALPHAY SEWAGE PUMPING STATION | GALPHAY/CSO | WADC179 | WADC179 | A2 | Storm discharge at pumping station | SE2540072500 | 425438 | 472516 | GB104027069260 | Kex Beck and the Laver | River | 3309 | Middle and Lower Ure | 3088 | Swale, Ure, Nidd and Upper Ouse | TRIB OF LAVER | Not Applicable | Not Applicable | Not Applicable | 144:00 | 34 | 32.4 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01216
YWS01217 | Yorkshire Water | Live | SELBY ROAD SPS | ASKERN SELBY RD/CSO | WADC18 | WADC18 | 1 | Storm discharge at pumping station | SE5610014600 | 456180 | 414610 | GB104027063360 | Went from Hoyle Mill Stream to Blowell Drain | River | 3272 | Lower Don | 3029 | Don and Rother | SWAN SIKE DRAIN | Not Applicable | Not Applicable | Not Applicable | 3:30 | 2 | 8.8 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01217
YWS01219 | Yorkshire Water | Live | GOODMANHAM SPS | GOODMANHAM/CSO | WADC192 | WADC192 | 1 | Storm discharge at pumping station | SE8836042470 | 488370 | 442470 | GB104026066690 | Foulness from Black Beck to Market Weighton Canal | River | 3191 | Foulness | 3039 | Hull and East Riding | MILL BECK | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 1.4 | 2020 | 98.26 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01219
YWS01220 | Yorkshire Water | Live | GREAT LANGTON SPS | SWALE COTTAGES/CSO | WADC195 | WADC195 | 1 | Storm discharge at pumping station | SE2940096400 | 429500 | 496400 | GB104027069122 | Swale from Clapgate Beck to Bedale Beck | River | 3317 | Middle Swale | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER SWALE | Not Applicable | Not Applicable | Not Applicable | 21:15 | 3 | 2.8 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01220
YWS01221 | Yorkshire Water | Live | HARDSTOFT SPS | HARDSTOFT/CSO | WADC204 | WADC204 | A2 | SO on sewer network | SK4416062790 | 444161 | 362780 | GB104027057290 | Doe Lea from Source to Hawke Brook | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | RIVER DOE LEA | Not Applicable | Not Applicable | Not Applicable | 36:30 | 14 | 11.2 | 2020 | 99.98 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01221
YWS01222 | Yorkshire Water | Live | CHESTNUT AVENUE SPS | HEDON CHESTNUT AVE/CSO | WADC212 | WADC212 | 1 | Storm discharge at pumping station | TA1800126301 | 518650 | 429050 | GB104026067200 | Burstwick Drain from Source to Humber | River | 3057 | Burstwick and Eastern Drains | 3039 | Hull and East Riding | BURSTWICK DRAIN | Not Applicable | Not Applicable | Not Applicable | 0:15 | 1 | 0.4 | 2020 | 97.73 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01222
YWS01223 | Yorkshire Water | Live | HUNMANBY GAP SPS | HUNMANBY GAP/CSO | WADC228 | WADC228 | 1 | Storm discharge at pumping station | TA1310077210 | 513110 | 477210 | Not part of a WFD catchment | Not part of a WFD catchment | River | N/A | N/A | N/A | N/A | NORTH SEA VIA REIGHTON GILL | Not Applicable | Reighton | Not Applicable | 105:16 | 30 | 12.4 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01223
YWS01224 | Yorkshire Water | Live | TIDBY LANE SPS | TIBBY LANE/SPS | WADC244 | WADC244 | A2 | Storm discharge at pumping station | TA0027049520 | 500276 | 449508 | GB104026066980 | Middleton on the Wolds and Watton Beck | River | 3274 | Lower Hull | 3039 | Hull and East Riding | FIELD DRAIN | Not Applicable | Not Applicable | Not Applicable | 12:00 | 6 | 6 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01224
YWS01225 | Yorkshire Water | Live | LANGTHORPE SPS | LANGTHORPE/CSO | WADC250 | WADC250 | 1 | Storm discharge at pumping station | SE3940067200 | 439500 | 467130 | GB104027064161 | Ure from River Skell to River Tutt | River | 3309 | Middle and Lower Ure | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER URE | Not Applicable | Not Applicable | Not Applicable | 673:45 | 75 | 75.2 | 2020 | 99.99 |  |  | Performance - Infiltration | Performance - Infiltration | UWWTR investigation ongoing, Operational investigation completed | Operational improvement completed | SOAF investigation ongoing | YWS01225
YWS01226 | Yorkshire Water | Live | LEEDS ROAD SPS (ICI) | HUDDERSFIELD LEEDS RD/CSO | WADC258 | WADC258 | 1 | Storm discharge at pumping station | SE1650018700 | 416760 | 418930 | GB104027062550 | Colne from River Holme to River Calder | River | 3097 | Colne and Holme | 3001 | Aire and Calder | SEWER TO RIVER COLNE | Not Applicable | Not Applicable | Not Applicable | 0:45 | 1 | 0.2 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01226
YWS01227 | Yorkshire Water | Live | WALKINGTON ROAD SPS | LITTLE WEIGHTON/CSO | WADC269 | WADC269 | A2 | Storm discharge at pumping station | SE9883033930 | 498822 | 433898 | GB104026066820 | High Hunsley to Woodmansey Area | River | 3274 | Lower Hull | 3039 | Hull and East Riding | FIELD DITCH | Not Applicable | Not Applicable | Not Applicable | 1:45 | 4 | 12.6 | 2020 | 12.94 | Comms failure / issue | Resolved - Dec | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01227
YWS01229 | Yorkshire Water | Live | LOCKINGTON NO.1 SPS | CHAPEL STREET/CSO | WADC275 | WADC275 | A2 | Storm discharge at pumping station | SE9860047500 | 499521 | 447348 | GB104026066960 | Bryan Mills Beck Source to Bryan Mills Farm | River | 3274 | Lower Hull | 3039 | Hull and East Riding | NEARBY DYKE | Not Applicable | Not Applicable | Not Applicable | 42:30 | 5 | 3.4 | 2020 | 99.97 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01229
YWS01230 | Yorkshire Water | Live | MAIN ROAD SPS | HIGHFIELD RD BUBWITH/CSO | WADC283 | WADC283 | 1 | Storm discharge at pumping station | SE7215036360 | 472150 | 436370 | GB104027063430 | Birk Lane Drain Catch (trib of Derwent) | River | 3271 | Lower Derwent Yorkshire | 3027 | Derwent Humber | WEST LINELANDS SOUTH DRAIN | Not Applicable | Not Applicable | Not Applicable | 1:15 | 1 | 0.2 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01230
YWS01231 | Yorkshire Water | Live | BEEFORD SPS | BEEFORD/SPS | WADC284 | WADC284 | 1 | Storm discharge at pumping station | TA1268054040 | 512850 | 454110 | GB104026067021 | Old Howe/Frodingham Beck to R Hull | River | 3492 | Upper Hull | 3039 | Hull and East Riding | DITCH | Not Applicable | Not Applicable | Not Applicable | 62:00 | 11 | 11.2 | 2020 | 99.97 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01231
YWS01232 | Yorkshire Water | Live | METAL BOX SPS | METAL BOX/CSO | WADC296 | WADC296 | 1 | Storm discharge at pumping station | SE1580038500 | 415830 | 438500 | GB104027063034 | Aire (R Worth to Gill Beck) | River | 3307 | Middle Aire | 3001 | Aire and Calder | RIVER AIRE | Not Applicable | Not Applicable | Not Applicable |  |  | 4.25 | 2020 | 0 | Sensor failure / issue | Scheduled | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01232
YWS01233 | Yorkshire Water | Live | MILBY ISLAND SPS | MILBY ISLAND/SPS | WADC302 | WADC302 | 1 | Storm discharge at pumping station | SE3950067100 | 439660 | 467020 | GB104027064161 | Ure from River Skell to River Tutt | River | 3309 | Middle and Lower Ure | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER URE | Not Applicable | Not Applicable | Not Applicable | 50:15 | 5 | 1.25 | 2020 | 99.93 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01233
YWS01235 | Yorkshire Water | Live | MOLESCROFT SPS | PIGHILL LANE/CSO | WADC307 | WADC307 | 1 | SO on sewer network | TA0280041500 | 502756 | 441305 | GB104026066841 | High Hunsley to Arram Area | River | 3274 | Lower Hull | 3039 | Hull and East Riding | NEARBY DITCH | Not Applicable | Not Applicable | Not Applicable | 73:30 | 14 | 6.4 | 2020 | 99.8 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01235
YWS01236 | Yorkshire Water | Live | NORWOOD SPS | NORWOOD/CSO | WADC320 | WADC320 | 1 | Storm discharge at pumping station | SK4640081910 | 446390 | 382040 | GB104027057772 | Rother, Doe Lea to Don | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | COUNTY DYKE TO RIVER ROTHER | Not Applicable | Not Applicable | Not Applicable | 52:00 | 18 | 27.2 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01236
YWS01237 | Yorkshire Water | Live | OLD EARSWICK SPS | EARSWICK WILLOW GROVE/CSO | WADC325 | WADC325 | A2 | SO on sewer network | SE6220057200 | 461668 | 457248 | GB104027063520 | Foss from the Syke to the River Ouse | River | 3190 | Foss | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER FOSS | Not Applicable | Not Applicable | Not Applicable | 222:00 | 31 | 17.2 | 2020 | 99.93 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01237
YWS01238 | Yorkshire Water | Live | PATRINGTON SPS | PATRINGTON HAVEN/SPS | WADC334 | WADC334 | 1 | Storm discharge at pumping station | TA3020021100 | 530260 | 421130 | GB104026066570 | Winestead Drain from Source to Humber | River | 3057 | Burstwick and Eastern Drains | 3039 | Hull and East Riding | NEARBY DITCH | Not Applicable | Not Applicable | Not Applicable | 76:00 | 6 | 3.2 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01238
YWS01240 | Yorkshire Water | Live | PRESTON SPS | ABBEY LANE HULL/CSO | WADC342 | WADC342 | 1 | Storm discharge at pumping station | TA1850030700 | 518570 | 430770 | GB104026067200 | Burstwick Drain from Source to Humber | River | 3057 | Burstwick and Eastern Drains | 3039 | Hull and East Riding | NEARBY DITCH | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0.8 | 2020 | 99.98 |  |  | High spill threshold not met | High spill threshold not met | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01240
YWS01242 | Yorkshire Water | Live | SANDSEND SPS | SANDSEND ROAD/CSO | WADC364 | WADC364 | 1 | Storm discharge at pumping station | NZ8809011520 | 488080 | 511490 | Not part of a WFD catchment | Not part of a WFD catchment | River | N/A | N/A | N/A | N/A | UPGANG BECK | Not Applicable | Sandsend | Not Applicable | 8:38 | 8 | 3.4 | 2020 | 99.93 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01242
YWS01244 | Yorkshire Water | Live | SINNINGTON SPS | SINNINGTON MAIN ST/CSO | WADC383 | WADC383 | 1 | Storm discharge at pumping station | SE7440085400 | 474430 | 485380 | GB104027068490 | Seven from Little Beck to Catter Beck | River | 3387 | Rye | 3027 | Derwent Humber | RIVER SEVERN | Not Applicable | Not Applicable | Not Applicable | 122:00 | 15 | 15 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01244
YWS01245 | Yorkshire Water | Live | SLEIGHTS SPS | SLEIGHTS/CSO | WADC385 | WADC385 | 1 | SO on sewer network | NZ5750008300 | 487528 | 508282 | GB104027068150 | Esk from Sleddale Beck to Ruswarp | River | 3177 | Esk | 3037 | Esk and Coast | RIVER ESK | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 7 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01245
YWS01246 | Yorkshire Water | Live | BIRCHES LANE SPS | BIRCHES LANE/CSO | WADC39 | WADC39 | 1 | Storm discharge at pumping station | SK3664079810 | 436680 | 379820 | GB104027057710 | Drone/Whitting from Source to River Rother | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | TRIBUTARY OF THE RIVER MOSS | Not Applicable | Not Applicable | Not Applicable | 83:00 | 37 | 36.4 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01246
YWS01248 | Yorkshire Water | Live | ST. ANDREWS TERRACE SPS | ST ANDREWS TERRACE/SPS | WADC396 | WADC396 | 1 | Storm discharge at pumping station | SE0100045400 | 401000 | 445400 | GB40402G700400 | Aire & Calder Carb Limestone / Millstone Grit / Coal Measures. Water Body | Groundwater Body | 1001 | Aire and Calder Carb Limestone - Millstone Grit Coal - Measures | 1006 | Humber GW | SOAKAWAY | Not Applicable | Not Applicable | Not Applicable | 5:00 | 10 | 36.6 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01248
YWS01249 | Yorkshire Water | Live | STAXTON VILLAGE SPS | STAXTON VILLAGE/CSO | WADC406 | WADC406 | A2 | Storm discharge at pumping station | TA0270079400 | 501670 | 479440 | GB104027067811 | Hertford from Source to River Derwent | River | 3489 | Upper Derwent Yorkshire | 3027 | Derwent Humber | DITCH | Not Applicable | Not Applicable | Not Applicable | 73:30 | 25 | 25.4 | 2020 | 99.85 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01249
YWS01250 | Yorkshire Water | Live | STRENSALL SPS | STRENSALL/CSO | WADC408 | WADC408 | 1 | Storm discharge at pumping station | SE6260060600 | 462700 | 460640 | GB104027063520 | Foss from the Syke to the River Ouse | River | 3190 | Foss | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER FOSS | Not Applicable | Not Applicable | Not Applicable | 512:45 | 55 | 52.6 | 2020 | 99.94 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01250
YWS01251 | Yorkshire Water | Live | BISHOP BURTON SPS | BISHOP BURTON/CSO | WADC41 | WADC41 | 1 | Storm discharge at pumping station | SE9890040000 | 498930 | 440230 | GB104026066841 | High Hunsley to Arram Area | River | 3274 | Lower Hull | 3039 | Hull and East Riding | NEARBY DITCH | Not Applicable | Not Applicable | Not Applicable | 219:30 | 37 | 40.6 | 2020 | 99.98 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01251
YWS01252 | Yorkshire Water | Live | SUTTON FIELDS SPS | SUTTON FIELDS/SPS | WADC412 | WADC412 | 1 | Storm discharge at pumping station | SE0030044500 | 400280 | 444480 | GB104027062960 | Eastburn Beck from Lothersdale Beck to River Aire | River | 3484 | Upper Aire | 3001 | Aire and Calder | HOLME BECK | Not Applicable | Not Applicable | Not Applicable | 0:30 | 1 | 0.2 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01252
YWS01253 | Yorkshire Water | Live | STAIRFOOT SPS | STAIRFOOT/SPS | WADC417 | WADC417 | A2 | Storm discharge at pumping station | SE3783004800 | 437830 | 404800 | GB104027057510 | Dove from Source to River Dearne | River | 3125 | Dearne | 3029 | Don and Rother | RIVER DOVE | Not Applicable | Not Applicable | Not Applicable | 2:30 | 2 | 9.6 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01253
YWS01255 | Yorkshire Water | Live | TUNSTALL SEWAGE PUMPING STATION | TUNSTALL VILLAGE/CSO | WADC438 | WADC438 | 1 | Storm discharge at pumping station | SE2700096100 | 422080 | 496190 | GB104027068990 | Brough Bk/Scotton Bk from Source to River Swale | River | 3317 | Middle Swale | 3088 | Swale, Ure, Nidd and Upper Ouse | TUNSTALL BECK | Not Applicable | Not Applicable | Not Applicable | 111:45 | 13 | 13.6 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01255
YWS01256 | Yorkshire Water | Live | WATH ROAD SPS | WATH ROAD/CSO | WADC447 | WADC447 | 1 | Storm discharge at pumping station | SE4101002450 | 441030 | 402460 | GB104027057470 | Knoll Beck from Source to River Dearne | River | 3125 | Dearne | 3029 | Don and Rother | DOVE CANAL - RIVER DEARNE | Not Applicable | Not Applicable | Not Applicable | 0:15 | 1 | 0.2 | 2020 | 99.9 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01256
YWS01258 | Yorkshire Water | Live | BOLTON ON SWALE SPS | BOLTON ON SWALE/NO 2 CSO | WADC45 | WADC45 | 1 | Storm discharge at pumping station | SE2530099200 | 425350 | 499190 | GB104027069160 | Scorton Beck from Source to River Swale | River | 3317 | Middle Swale | 3088 | Swale, Ure, Nidd and Upper Ouse | SCORTON BECK | Not Applicable | Not Applicable | Not Applicable | 0:30 | 1 | 3.6 | 2020 | 65.2 | Sensor failure / issue | Resolved - May | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01258
YWS01259 | Yorkshire Water | Live | WEST END SPS | WEST END SEATON ROSS/CSO | WADC453 | WADC453 | 1 | Storm discharge at pumping station | SE7773041220 | 477745 | 441197 | GB104026066690 | Foulness from Black Beck to Market Weighton Canal | River | 3191 | Foulness | 3039 | Hull and East Riding | POND | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0.4 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01259
YWS01260 | Yorkshire Water | Live | WHELDRAKE SPS | COURTNEYS/CSO | WADC461 | WADC461 | A2 | SO on sewer network | SE6840045200 | 468487 | 445179 | GB104027068311 | Derwent from Elvington Beck to River Ouse | River | 3271 | Lower Derwent Yorkshire | 3027 | Derwent Humber | DITCH | Not Applicable | Not Applicable | Not Applicable | 161:30 | 31 | 66.4 | 2020 | 99.94 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement completed | SOAF investigation ongoing | YWS01260
YWS01261 | Yorkshire Water | Live | SHORPETH WAY SPS | SHOPETH WAY/CSO | WADC472 | WADC472 | 1 | Storm discharge at pumping station | TA0581037980 | 505820 | 438020 | GB104026067211 | Beverley and Barmston Drain | River | 3274 | Lower Hull | 3039 | Hull and East Riding | SURFACE WATER SEWER | Not Applicable | Not Applicable | Not Applicable | 203:15 | 20 | 16.2 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01261
YWS01262 | Yorkshire Water | Live | MAIN ROAD SPS | WYTON/SPS | WADC477 | WADC477 | 1 | Storm discharge at pumping station | TA1740033000 | 517430 | 433050 | GB104026066610 | Humbleton Beck Catchment | River | 3057 | Burstwick and Eastern Drains | 3039 | Hull and East Riding | NEARBY DITCH | Not Applicable | Not Applicable | Not Applicable | 152:45 | 21 | 13 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01262
YWS01263 | Yorkshire Water | Live | YAFFORTH SEWAGE PUMPING STATION | YAFFORTH/CSO | WADC478 | WADC478 | 1 | Storm discharge at pumping station | SE3460094400 | 434610 | 494420 | GB104027069530 | Wiske from Trenholme Stell to River Swale | River | 3541 | Wiske | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER WISKE | Not Applicable | Not Applicable | Not Applicable | 61:15 | 26 | 11.4 | 2020 | 99.98 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01263
YWS01264 | Yorkshire Water | Live | BRAMLEY HALL FARM SPS | BRAMLEY HALL FM/CSO | WADC53 | WADC53 | 1 | Storm discharge at pumping station | SK4067079380 | 440680 | 379380 | GB104027057720 | The Moss from Source to River Rother | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | TRIBUTARY OF THE RIVER MOSS | Not Applicable | Not Applicable | Not Applicable | 15:45 | 6 | 9.6 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01264
YWS01265 | Yorkshire Water | Live | STANFREE CSO | STANFREE/CSO | WADC57 | WADC57 | A1 | SO on sewer network | SK4745874465 | 447458 | 374465 | GB104027057320 | Hawke Brook from Source to Doe Lea | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | TRIB OF BARLBOROUGH BROOK | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 17.6 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01265
YWS01266 | Yorkshire Water | Live | AISLABY SEWAGE PUMPING STATION | RYEDALE AISLABY/SPS | WADC6 | WADC6 | 1 | Storm discharge at pumping station | SE7737085500 | 477420 | 485660 | GB104027068480 | Costa Beck from Source to Pickering Beck | River | 3387 | Rye | 3027 | Derwent Humber | TRIB OF COSTA BECK | Not Applicable | Not Applicable | Not Applicable | 0:15 | 1 | 3.8 | 2020 | 99.98 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01266
YWS01267 | Yorkshire Water | Live | 109 STATION ROAD | RYHILL STATION ROAD/CSO | WADC626 | WADC626 | A1 | SO on sewer network | SE3823514670 | 438235 | 414670 | Not part of a WFD catchment | Not part of a WFD catchment | River | N/A | N/A | N/A | N/A | TRIB OF WINTERSETT RESERVOIR | Not Applicable | Not Applicable | Not Applicable | 6:15 | 5 | 10 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01267
YWS01268 | Yorkshire Water | Live | CHESTERFIELD ROAD CSO | CHESTERFIELD ROAD/CSO | WADC627 | WADC627 | A1 | SO on sewer network | SK4278074668 | 442780 | 374668 | GB104027057771 | Rother, Spittal Brook to Doe Lea | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | RIVER ROTHER | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 3.4 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01268
YWS01269 | Yorkshire Water | Live | SPRING BANK ROAD CSO | SPRING BANK ROAD/CSO | WADC635 | WADC635 | A1 | SO on sewer network | SK3758971356 | 437318 | 371399 | GB104027057670 | Holme Brook/Linacre Beck | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | HOLME BROOK | Not Applicable | Not Applicable | Not Applicable | 0:15 | 1 | 4.6 | 2020 | 64.6 | Comms failure / issue | Resolved - May | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01269
YWS01270 | Yorkshire Water | Live | ILKLEY ROAD | ILKLEY ROAD/CSO | WADC640 | WADC640 | A1 | SO on sewer network | SE1962545353 | 419625 | 445353 | GB104027064258 | Wharfe from Hundwith Beck to River Washburn | River | 3318 | Middle Wharfe and Washburn | 3115 | Wharfe and Lower Ouse | RIVER WHARFE | Not Applicable | Not Applicable | Not Applicable | 98:30 | 46 | 46.2 | 2020 | 99.9 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01270
YWS01271 | Yorkshire Water | Live | ABERFORD ROAD SSO | ABERFORD ROAD 87/CSO | WADC658 | WADC658 | A1 | SO on sewer network | SE4025837362 | 440258 | 437362 | GB104027063940 | Cock Beck Catchment (trib of Wharfe) | River | 3287 | Lower Wharfe | 3115 | Wharfe and Lower Ouse | TRIB OF COCK BECK | Not Applicable | Not Applicable | Not Applicable | 2:00 | 6 | 2 | 2020 | 83.19 | Comms failure / issue | Resolved - Jan | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01271
YWS01272 | Yorkshire Water | Live | BYWATER FARM CSO | BYWATER FARM/CSO | WADC659 | WADC659 | A1 | SO on sewer network | SE2845038735 | 428450 | 438735 | GB104027062900 | Meanwood Beck from Source to River Aire | River | 3265 | Lower Aire | 3001 | Aire and Calder | ADEL BECK | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01272
YWS01273 | Yorkshire Water | Live | WATH BROOK DIKE CSO | WATH BROOK DIKE/CSO | WADC660 | WADC660 | A1 | SO on sewer network | SE4329401036 | 443294 | 401036 | GB104027057470 | Knoll Beck from Source to River Dearne | River | 3125 | Dearne | 3029 | Don and Rother | BROOK DYKE | Not Applicable | Not Applicable | Not Applicable | 37:15 | 26 | 15.8 | 2020 | 99.97 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01273
YWS01274 | Yorkshire Water | Live | ASH GROVE CSO | ASH GROVE CASTLETON/CSO | WADC681 | WADC681 | A1 | SO on sewer network | NZ6896707838 | 468967 | 507838 | GB104027068110 | Danby Beck catchement (trib of Esk) | River | 3177 | Esk | 3037 | Esk and Coast | DANBY BECK | Not Applicable | Not Applicable | Not Applicable | 13:45 | 10 | 16.8 | 2020 | 90.15 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01274
YWS01275 | Yorkshire Water | Live | ASHENHURST ROAD | ASHENHURST ROAD/CSO | WADC682 | WADC682 | A1 | SO on sewer network | SD9312224854 | 393122 | 424854 | GB104027062660 | Calder from Source to Walsden Water | River | 3487 | Upper Calder | 3001 | Aire and Calder | RIVER CALDER | Not Applicable | Not Applicable | Not Applicable | 189:15 | 75 | 44.2 | 2020 | 99.9 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01275
YWS01276 | Yorkshire Water | Live | AYTON FOOTBRIDGE SSO | FOOTBRIDGE WST AYTON/CSO | WADC688 | WADC688 | 1 | SO on sewer network | SE9871084470 | 498715 | 484467 | GB104027067930 | Derwent from Black Beck to River Rye | River | 3489 | Upper Derwent Yorkshire | 3027 | Derwent Humber | RIVER DERWENT | Not Applicable | Not Applicable | Not Applicable | 40:45 | 22 | 21 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01276
YWS01277 | Yorkshire Water | Live | PAULL BACK ROAD CSO | PAULL BACK ROAD/CSO | WADC691 | WADC691 | A1 | SO on sewer network | TA1675726350 | 516757 | 426350 | Not part of a WFD catchment | Not part of a WFD catchment | River | N/A | N/A | N/A | N/A | CULV TRIBUTARY OF HEDON HAVEN | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01277
YWS01278 | Yorkshire Water | Live | AISLABY SEWAGE PUMPING STATION | AISLABY/CSO | WADC7 | WADC7 | 1 | Storm discharge at pumping station | NZ8550008500 | 485480 | 508450 | GB104027068150 | Esk from Sleddale Beck to Ruswarp | River | 3177 | Esk | 3037 | Esk and Coast | DITCH | Not Applicable | Not Applicable | Not Applicable | 0:15 | 1 | 0.4 | 2020 | 99.83 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01278
YWS01279 | Yorkshire Water | Live | BEIGHTON STW | BEIGHTON/CSO | WADC709 | WADC709 | A1 | SO on sewer network | SK4351684383 | 443516 | 384383 | GB104027057773 | Shire Brook | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | SHIRE BROOK | Not Applicable | Not Applicable | Not Applicable | 3:00 | 3 | 3.4 | 2020 | 99.95 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01279
YWS01280 | Yorkshire Water | Live | BILLAMS HILL SSO | BILLAMS HILL/CSO | WADC717 | WADC717 | A1 | SO on sewer network | SE2009945880 | 420099 | 445880 | GB104027064258 | Wharfe from Hundwith Beck to River Washburn | River | 3318 | Middle Wharfe and Washburn | 3115 | Wharfe and Lower Ouse | RIVER WHARFE | Not Applicable | Not Applicable | Not Applicable | 135:45 | 64 | 68 | 2020 | 99.94 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01280
YWS01281 | Yorkshire Water | Live | CAPSTAN ROAD SPS | CAPSTAN ROAD/CSO | WADC72 | WADC72 | A2 | Storm discharge at pumping station | TA0810033800 | 508430 | 433840 | GB104026067212 | Hull from Arram Beck to Humber | River | 3274 | Lower Hull | 3039 | Hull and East Riding | RIVER HULL | Not Applicable | Not Applicable | Not Applicable | 24:15 | 30 | 6.2 | 2020 | 99.95 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01281
YWS01282 | Yorkshire Water | Live | BLACK SWAN CSO | BLACK SWAN/CSO | WADC722 | WADC722 | A1 | SO on sewer network | SE2995051338 | 429950 | 451338 | GB104027063741 | Crimple Beck from Source to Park Beck | River | 3308 | Middle and Lower Nidd | 3088 | Swale, Ure, Nidd and Upper Ouse | CRIMPLE BECK OR RIVER CRIMPLE | Not Applicable | Not Applicable | Not Applicable | 74:30 | 25 | 6.4 | 2020 | 76.89 | Sensor failure / issue | Resolved - Dec | High spill threshold not met | High spill threshold not met | Operational investigation completed | No improvement action in reporting period | No SOAF investigation required | YWS01282
YWS01283 | Yorkshire Water | Live | HARROGATE ROAD CSO | HARROGATE ROAD/CSO | WADC733 | WADC733 | A1 | SO on sewer network | SE3094070854 | 430940 | 470854 | GB104027064140 | Skell from River Laver to River Ure | River | 3309 | Middle and Lower Ure | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER SKELL | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0 | 2020 | 94.68 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01283
YWS01284 | Yorkshire Water | Live | BOTTOM BOAT ROAD SSO | BOTTOM BOAT ROAD/CSO | WADC734 | WADC734 | A1 | SO on sewer network | SE3557924464 | 435579 | 424464 | GB104027062632 | Calder from River Chald to River Aire | River | 3268 | Lower Calder | 3001 | Aire and Calder | RIVER CALDER | Not Applicable | Not Applicable | Not Applicable | 1:30 | 2 | 2.8 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01284
YWS01285 | Yorkshire Water | Live | BRANDSBY ROAD SSO | BRANDSBY ROAD/NO 1 CSO | WADC744 | WADC744 | A1 | SO on sewer network | SE5631070000 | 456616 | 471160 | GB104027067760 | Foss from Source to Farlington Beck | River | 3190 | Foss | 3088 | Swale, Ure, Nidd and Upper Ouse | TRIB OF RIVER KYLE | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0 | 2020 | 19.56 | Sensor failure / issue | Scheduled | High spill threshold not met | High spill threshold not met | Operational investigation ongoing | No improvement action in reporting period | No SOAF investigation required | YWS01285
YWS01286 | Yorkshire Water | Live | BREWERY LANE CSO | BREWERY LANE/CSO | WADC745 | WADC745 | A1 | SO on sewer network | SE2403820061 | 424038 | 420061 | GB104027062631 | Calder from River Colne to River Chald | River | 3268 | Lower Calder | 3001 | Aire and Calder | CULVERTED TRIB OF RIVER CALDER | Not Applicable | Not Applicable | Not Applicable | 20:30 | 11 | 23.6 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01286
YWS01287 | Yorkshire Water | Live | BRIDGE LANE/MARKET STREET | MARKET STREET/CSO | WADC748 | WADC748 | A1 | SO on sewer network | SD9886527184 | 398865 | 427184 | GB104027062641 | Calder from Colden Water to Ryburn Confluence | River | 3310 | Middle Calder | 3001 | Aire and Calder | RIVER CALDER | Not Applicable | Not Applicable | Not Applicable | 61:45 | 11 | 8.8 | 2020 | 92.83 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01287
YWS01289 | Yorkshire Water | Live | BRIDGE STREET SSO | OTLEY BRIDGE STREET/CSO | WADC757 | WADC757 | A1 | SO on sewer network | SE2015245833 | 420152 | 445833 | GB104027064258 | Wharfe from Hundwith Beck to River Washburn | River | 3318 | Middle Wharfe and Washburn | 3115 | Wharfe and Lower Ouse | RIVER WHARFE | Not Applicable | Not Applicable | Not Applicable | 33:30 | 15 | 26.2 | 2020 | 52.31 | Sensor failure / issue | Scheduled | High spill threshold not met | High spill threshold not met | Operational investigation ongoing | Operational improvement ongoing | No SOAF investigation required | YWS01289
YWS01290 | Yorkshire Water | Live | CARR LANE SPS | GLASS HOUGHTON/CSO | WADC76 | WADC76 | A2 | SO on sewer network | SE4340024020 | 443340 | 423916 | GB104027062632 | Calder from River Chald to River Aire | River | 3268 | Lower Calder | 3001 | Aire and Calder | CARR BECK | Not Applicable | Not Applicable | Not Applicable | 33:45 | 34 | 43 | 2020 | 100 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01290
YWS01291 | Yorkshire Water | Live | BROOK STREET CSO | BROOK STREET/CSO | WADC761 | WADC761 | A1 | SO on sewer network | SD9860851732 | 398608 | 451732 | GB104027063020 | Eller Beck from Haw Beck to River Aire | River | 3484 | Upper Aire | 3001 | Aire and Calder | ELLER BECK | Not Applicable | Not Applicable | Not Applicable | 0:30 | 2 | 1.8 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01291
YWS01292 | Yorkshire Water | Live | BROCKHOLES LANE CSO | BROCKHOLES LANE/CSO | WADC770 | WADC770 | A1 | SO on sewer network | SE1509210976 | 415092 | 410976 | GB104027063301 | Holme from New Mill Dike to R Colne | River | 3097 | Colne and Holme | 3001 | Aire and Calder | CULV TRIB OF RIVER HOLME | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 21.4 | 2020 | 67.54 | Comms failure / issue | Resolved - May | High spill threshold not met | High spill threshold not met | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01292
YWS01293 | Yorkshire Water | Live | CARRS SEWAGE PUMPING STATION | RUSWARP CARRS/SPS | WADC78 | WADC78 | 1 | Storm discharge at pumping station | NZ8790008600 | 487970 | 508610 | GB104027068150 | Esk from Sleddale Beck to Ruswarp | River | 3177 | Esk | 3037 | Esk and Coast | DITCH | Not Applicable | Not Applicable | Not Applicable | 309:00 | 27 | 18.2 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01293
YWS01294 | Yorkshire Water | Live | BRADFORD ROAD | BRICK KILN LANE/CSO | WADC783 | WADC783 | A1 | SO on sewer network | SE0962041230 | 459382 | 428427 | GB104027064270 | Ouse from R Wharfe to Upper Humber | River | 3280 | Lower Ouse Yorkshire | 3115 | Wharfe and Lower Ouse | RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 225:45 | 66 | 39.4 | 2020 | 86.94 | Sensor failure / issue | Resolved - May | Not asset maintenance - Hydraulic capacity | High spill threshold not met | UWWTR investigation ongoing, Operational investigation completed | Operational improvement completed | SOAF investigation ongoing | YWS01294
YWS01295 | Yorkshire Water | Live | CARR LANE EAST AYTON CSO | CARR LANE EAST AYTON/CSO | WADC798 | WADC798 | A1 | SO on sewer network | SE9919484354 | 499194 | 484354 | GB104027067930 | Derwent from Black Beck to River Rye | River | 3489 | Upper Derwent Yorkshire | 3027 | Derwent Humber | RIVER DERWENT | Not Applicable | Not Applicable | Not Applicable | 13:45 | 13 | 8 | 2020 | 99.89 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01295
YWS01296 | Yorkshire Water | Live | CASTLEGATE BRADFORD CSO | CASTLEGATE BRADFORD/CSO | WADC805 | WADC805 | A1 | SO on sewer network | SE1467817569 | 414678 | 417569 | GB104027062550 | Colne from River Holme to River Calder | River | 3097 | Colne and Holme | 3001 | Aire and Calder | CULV TRIB OF HEBBLE BECK | Not Applicable | Not Applicable | Not Applicable | 2:30 | 7 | 5.8 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01296
YWS01297 | Yorkshire Water | Live | CEMETERY LANE CSO | CEMETERY LANE/CSO | WADC809 | WADC809 | A1 | SO on sewer network | SE0612643100 | 406126 | 443100 | GB104027063033 | Aire (Eshton Beck to R Worth) | River | 3484 | Upper Aire | 3001 | Aire and Calder | RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 322:30 | 95 | 106.8 | 2020 | 99.97 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01297
YWS01298 | Yorkshire Water | Live | CHANTRY ROAD SSO | CHANTRY ROAD/CSO | WADC810 | WADC810 | 1 | Storm discharge at pumping station | SE3584093250 | 435840 | 493250 | GB104027069540 | Willow Beck Catchment (trib of Wiske) | River | 3541 | Wiske | 3088 | Swale, Ure, Nidd and Upper Ouse | TRIB OF RIVER WISKE | Not Applicable | Not Applicable | Not Applicable | 1:00 | 1 | 0.2 | 2020 | 97.65 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01298
YWS01299 | Yorkshire Water | Live | SKIRLAUGH CSO | SKIRLAUGH CHURCH LANE/CSO | WADC826 | WADC826 | A1 | SO on sewer network | TA1421939766 | 514219 | 439766 | GB104026066860 | Lambwath Stream from Source to Foredyke Stream | River | 3274 | Lower Hull | 3039 | Hull and East Riding | LAMBWATH STREAM | Not Applicable | Not Applicable | Not Applicable | 52:30 | 20 | 18.2 | 2020 | 99.94 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01299
YWS01300 | Yorkshire Water | Live | CATWICK LANE SPS | CATWICK LANE/CSO | WADC83 | WADC83 | 1 | Storm discharge at pumping station | TA1330046000 | 513370 | 446040 | GB104026066970 | Catchwater Drain | River | 3274 | Lower Hull | 3039 | Hull and East Riding | NEARBY DYKE | Not Applicable | Not Applicable | Not Applicable | 12:45 | 10 | 18.4 | 2020 | 99.98 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01300
YWS01301 | Yorkshire Water | Live | CLAYWHEELS LANE CSO | CLAYWHEELS LANE/CSO | WADC833 | WADC833 | A1 | SO on sewer network | SK3279591656 | 432795 | 391656 | GB104027057411 | Don from Little Don to River Loxley confluence | River | 3490 | Upper Don | 3029 | Don and Rother | CULV TRIB OF RIVER DON | Not Applicable | Not Applicable | Not Applicable | 2:30 | 3 | 3.4 | 2020 | 94.84 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01301
YWS01302 | Yorkshire Water | Live | CLEVELAND AVENUE SSO | CLEVELAND AVENUE/CSO | WADC835 | WADC835 | A1 | SO on sewer network | TA0295089850 | 502981 | 489805 | GB104027067980 | Burniston Beck/Sea Cut/Scalby Beck Catch to N Sea | River | 3489 | Upper Derwent Yorkshire | 3027 | Derwent Humber | TRIB TO FOUL SEWER | Not Applicable | Scarborough North Bay | Not Applicable | 1:00 | 3 | 5 | 2020 | 99.58 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01302
YWS01303 | Yorkshire Water | Live | CAYTON BAY SEWAGE PUMPING STATION | CAYTON BAY/CSO | WADC84 | WADC84 | 1 | Storm discharge at pumping station | TA0685084100 | 506850 | 484100 | GB650401500004 | Yorkshire North | Coastal Water | 3179 | Esk TraC | 3040 | Humber TraC | NORTH SEA | Not Applicable | Cayton Bay | Not Applicable | 19:36 | 4 | 2.2 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01303
YWS01304 | Yorkshire Water | Live | CROOK FARM CSO | CROOK FARM/CSO | WADC861 | WADC861 | A1 | SO on sewer network | SE2524245354 | 425242 | 445354 | GB104027064254 | Wharfe from R Washburn to Collingham Beck | River | 3318 | Middle Wharfe and Washburn | 3115 | Wharfe and Lower Ouse | CULVERTED TRIB OF RIVER WHARFE | Not Applicable | Not Applicable | Not Applicable | 196:30 | 56 | 54.8 | 2020 | 97.42 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement ongoing | SOAF investigation ongoing | YWS01304
YWS01305 | Yorkshire Water | Live | CROW NEST BRIDGE CSO | CROW NEST BRIDGE/CSO | WADC864 | WADC864 | A1 | SO on sewer network | SD9958726845 | 399587 | 426845 | GB104027062641 | Calder from Colden Water to Ryburn Confluence | River | 3310 | Middle Calder | 3001 | Aire and Calder | RIVER CALDER | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 17.6 | 2020 | 99.95 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | SOAF investigation completed - No work required | YWS01305
YWS01306 | Yorkshire Water | Live | DIMLINGTON ROAD CSO | DIMLINGTON ROAD/CSO | WADC886 | WADC886 | A1 | SO on sewer network | TA3987518815 | 539875 | 418815 | Not part of a WFD catchment | Not part of a WFD catchment | River | N/A | N/A | N/A | N/A | CULV TRIB OF EASINGTON DRAIN | Not Applicable | Not Applicable | Not Applicable | 87:45 | 20 | 50.2 | 2020 | 99.99 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement completed | SOAF investigation ongoing | YWS01306
YWS01307 | Yorkshire Water | Live | HONLEY EASTGATE CSO | HONLEY EASTGATE/CSO | WADC895 | WADC895 | A1 | SO on sewer network | SE1399912140 | 413999 | 412140 | GB104027063301 | Holme from New Mill Dike to R Colne | River | 3097 | Colne and Holme | 3001 | Aire and Calder | CULV TRIB OF RIVER HOLME | Not Applicable | Not Applicable | Not Applicable | 0:15 | 1 | 4.2 | 2020 | 92.74 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01307
YWS01308 | Yorkshire Water | Live | ELLEN HOUSE ROAD | ELLEN HOLME ROAD/CSO | WADC906 | WADC906 | 1 | SO on sewer network | SE0397024400 | 403873 | 424408 | GB104027062641 | Calder from Colden Water to Ryburn Confluence | River | 3310 | Middle Calder | 3001 | Aire and Calder | RIVER CALDER | Not Applicable | Not Applicable | Not Applicable | 200:00 | 28 | 50.2 | 2020 | 99.98 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS01308
YWS01309 | Yorkshire Water | Live | ELLERBECK CSO | OLD CATTLE MARKET/CSO | WADC908 | WADC908 | A1 | SO on sewer network | SD9860051380 | 398603 | 451380 | GB104027063020 | Eller Beck from Haw Beck to River Aire | River | 3484 | Upper Aire | 3001 | Aire and Calder | WALLER HILL BECK | Not Applicable | Not Applicable | Not Applicable | 198:00 | 74 | 95 | 2020 | 99.81 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | No investigation activity in reporting period | No improvement action in reporting period | SOAF investigation completed - No work required | YWS01309
YWS01310 | Yorkshire Water | Live | CHURCH LANE SPS | CHURCH LANE DRIFFIELD/CSO | WADC91 | WADC91 | A2 | Storm discharge at pumping station | TA0098057970 | 500970 | 457920 | GB104026067080 | West Beck Upper | River | 3492 | Upper Hull | 3039 | Hull and East Riding | POND | Not Applicable | Not Applicable | Not Applicable | 1836:15 | 87 | 44 | 2020 | 99.5 |  |  | Performance - GW inundation | Performance - GW inundation | UWWTR investigation ongoing, Operational investigation completed | Operational improvement completed | SOAF investigation ongoing | YWS01310
YWS01311 | Yorkshire Water | Live | CHURCH LANE SEWAGE PUMPING STATION | LINTON/CSO | WADC92 | WADC92 | 1 | SO on sewer network | SE0030063200 | 400361 | 463227 | GB104027064253 | Wharfe from Park Gill Bk to Barben Beck/River Dibb | River | 3507 | Upper Wharfe | 3115 | Wharfe and Lower Ouse | RIVER WHARFE | Not Applicable | Wharfe at Cromwheel, Ilkley | Not Applicable | 210:00 | 41 | 33 | 2020 | 99.77 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01311
YWS01312 | Yorkshire Water | Live | FIELD 7500 CSO | FIELD 7500/CSO | WADC921 | WADC921 | A1 | SO on sewer network | SE4481257977 | 444812 | 457977 | GB104027068292 | Nidd from Crimple Beck to River Ouse | River | 3308 | Middle and Lower Nidd | 3088 | Swale, Ure, Nidd and Upper Ouse | WHIXLEY CUT | Not Applicable | Not Applicable | Not Applicable | 221:15 | 73 | 38.4 | 2020 | 97.22 |  |  | Not asset maintenance - Hydraulic capacity | High spill threshold not met | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS01312
YWS01313 | Yorkshire Water | Live | FIELDING STREET CSO | FIELDING STREET/CSO | WADC927 | WADC927 | A1 | SO on sewer network | SD9901127154 | 399011 | 427154 | GB104027062641 | Calder from Colden Water to Ryburn Confluence | River | 3310 | Middle Calder | 3001 | Aire and Calder | RIVER CALDER | Not Applicable | Not Applicable | Not Applicable | 195:30 | 38 | 35.6 | 2020 | 99.98 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | SOAF investigation completed - No work required | YWS01313
YWS01314 | Yorkshire Water | Live | FIR COTTAGE CSO | FIR COTTAGE/CSO | WADC929 | WADC929 | 1 | SO on sewer network | SE2227319777 | 422273 | 419777 | GB104027062631 | Calder from River Colne to River Chald | River | 3268 | Lower Calder | 3001 | Aire and Calder | RIVER CALDER | Not Applicable | Not Applicable | Not Applicable | 45:15 | 11 | 8.2 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01314
YWS01315 | Yorkshire Water | Live | FISHER END SSO | FISHER END/CSO | WADC932 | WADC932 | 1 | Storm discharge at pumping station | SE5095060110 | 450950 | 460100 | GB104027069592 | Ouse from River Ure to River Nidd | River | 3309 | Middle and Lower Ure | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER OUSE | Not Applicable | Not Applicable | Not Applicable | 74:45 | 32 | 21.2 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01315
YWS01316 | Yorkshire Water | Live | GARMANCARR SSO | WISTOW GARMAN CARR/CSO | WADC946 | WADC946 | 1 | SO on sewer network | SE5960034900 | 459720 | 435425 | GB104027063650 | Holmes Dike catchment (trib of Ouse) | River | 3280 | Lower Ouse Yorkshire | 3115 | Wharfe and Lower Ouse | GARMANCARR DIKE | Not Applicable | Not Applicable | Not Applicable | 82:30 | 30 | 27.8 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01316
YWS01317 | Yorkshire Water | Live | CLOVERLEY CLOSE SPS | CLOVERLEY CLOSE/CSO | WADC95 | WADC95 | 1 | Storm discharge at pumping station | SE7095045820 | 470909 | 455291 | GB104027068312 | Derwent from Kirkham to Elvington Beck | River | 3311 | Middle Derwent Yorkshire | 3027 | Derwent Humber | SURFACE WATER SEWER TO DITCH | Not Applicable | Not Applicable | Not Applicable | 0:30 | 1 | 0.4 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01317
YWS01318 | Yorkshire Water | Live | COACH ROAD SPS | BAILDON COACH RD/CSO | WADC96 | WADC96 | 1 | Storm discharge at pumping station | SE1410038200 | 414064 | 438230 | GB104027063034 | Aire (R Worth to Gill Beck) | River | 3307 | Middle Aire | 3001 | Aire and Calder | RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 172:30 | 21 | 9.4 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01318
YWS01319 | Yorkshire Water | Live | HALFWAY HOUSE SSO | HALFWAY HOUSE/CSO | WADC981 | WADC981 | A1 | Storm discharge at pumping station | SE3686095360 | 436804 | 495350 | GB104027069540 | Willow Beck Catchment (trib of Wiske) | River | 3541 | Wiske | 3088 | Swale, Ure, Nidd and Upper Ouse | TRIB OF RIVER WISKE | Not Applicable | Not Applicable | Not Applicable | 101:00 | 20 | 11 | 2020 | 99.94 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01319
YWS01320 | Yorkshire Water | Live | HAZELWOOD STREET CSO | HAZELWOOD STREET/CSO | WADC984 | WADC984 | A1 | SO on sewer network | SD9474024327 | 394740 | 424327 | GB104027062650 | Calder from Walsden Water to Colden Water | River | 3487 | Upper Calder | 3001 | Aire and Calder | RIVER CALDER | Not Applicable | Not Applicable | Not Applicable | 95:30 | 36 | 50.2 | 2020 | 99 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS01320
YWS01321 | Yorkshire Water | Live | HEALEY LANE CSO | HEALEY LANE/CSO | NPSWQD002297 | WQD002297 | A1 | SO on sewer network | SE1230538141 | 412305 | 438141 | GB104027063034 | Aire (R Worth to Gill Beck) | River | 3307 | Middle Aire | 3001 | Aire and Calder | THE RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 5:20 | 6 | 3.6 | 2020 | 99.98 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01321
YWS01322 | Yorkshire Water | Live | YORKSHIRE WATER SERVICES LIMITED, T | TODWICK/NO 3 CSO | WRA6606 | WRA6606 | 1 | SO on sewer network | SK4871084020 | 448722 | 384016 | GB104027057730 | Pigeon Bridge Brook from Source to River Rother | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | TODWICK BECK | Not Applicable | Not Applicable | Not Applicable | 50:15 | 13 | 10.8 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01322
YWS01323 | Yorkshire Water | Live | STAVELEY WWTW | STAVELEY/STW | WRA 6647 | WRA6647 | A2 | Storm tank at WwTW | SK4437576612 | 444372 | 376543 | GB104027057301 | Doe Lea from Hawke Brooke to River Rother | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | RIVER DOE LEA | Not Applicable | Not Applicable | Not Applicable | 1283:00 | 120 | 113.8 | 2020 | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS01323
YWS01324 | Yorkshire Water | Live | AIREDALE STW | AIREDALE/STW | WRA6658 | WRA6658 | A2 | Storm tank at WwTW | SE4690027000 | 446900 | 427000 | GB104027062760 | Aire from River Calder to River Ouse | River | 3265 | Lower Aire | 3001 | Aire and Calder | RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 8:15 | 2 | 15.8 | 2020 | 6.53 | Sensor failure / issue | Scheduled | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01324
YWS01325 | Yorkshire Water | Live | AIREDALE STW | AIREDALE/STW | WRA6658 | WRA6658 | A3 | Inlet SO at WwTW | SE4690027000 | 446900 | 427000 | GB104027062760 | Aire from River Calder to River Ouse | River | 3265 | Lower Aire | 3001 | Aire and Calder | RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 11:00 | 4 | 64.6 | 2020 | 6.53 | Sensor failure / issue | Scheduled | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01325
YWS01326 | Yorkshire Water | Live | CASTLEFORD STW | CASTLEFORD/STW | WRA6659 | WRA6659 | A2 | Storm tank at WwTW | SE4464026680 | 444640 | 426680 | GB104027062760 | Aire from River Calder to River Ouse | River | 3265 | Lower Aire | 3001 | Aire and Calder | RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 41:30 | 19 | 65.2 | 2020 | 99.95 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01326
YWS01327 | Yorkshire Water | Live | INGS LANE STORM TANKS | CASTLEFORD INGS LANE/CSO | WRA6660 | WRA6660 | A1 | Storm discharge at pumping station | SE4350026800 | 443500 | 426800 | GB104027062760 | Aire from River Calder to River Ouse | River | 3265 | Lower Aire | 3001 | Aire and Calder | RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 856:15 | 118 | 46 | 2020 | 99.91 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS01327
YWS01328 | Yorkshire Water | Live | INGS LANE STORM TANKS | CASTLEFORD INGS LANE/CSO | WRA6660 | WRA6660 | A2 | Storm discharge at pumping station | SE4350026800 | 443500 | 426800 | GB104027062760 | Aire from River Calder to River Ouse | River | 3265 | Lower Aire | 3001 | Aire and Calder | RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 14:15 | 6 | 6 | 2023 | 99.04 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01328
YWS01329 | Yorkshire Water | Live | WHELDALE FARM CSO | WHELDALE FARM/CSO | WRA6661 | WRA6661 | A1 | SO on sewer network | SE4486826721 | 444868 | 426721 | GB104027062760 | Aire from River Calder to River Ouse | River | 3265 | Lower Aire | 3001 | Aire and Calder | RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 1:45 | 6 | 9 | 2020 | 99.84 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01329
YWS01330 | Yorkshire Water | Live | MELTHAM STW | MELTHAM/STW | WRA6680 | WRA6680 | A2 | Storm tank at WwTW | SE1131711660 | 411200 | 411600 | GB104027063590 | Mag Brook from Source to River Holme | River | 3097 | Colne and Holme | 3001 | Aire and Calder | MAG BROOK | Not Applicable | Not Applicable | Not Applicable | 991:45 | 105 | 104.4 | 2020 | 99.12 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS01330
YWS01331 | Yorkshire Water | Live | HANGINGWATER ROAD CSO | HANGINGWATER ROAD/CSO | WRA6682 | WRA6682 | A1 | SO on sewer network | SK3163085310 | 431630 | 385310 | GB104027057760 | Porter from Source to River Sheaf | River | 3312 | Middle Don | 3029 | Don and Rother | PORTER BROOK | Not Applicable | Not Applicable | Not Applicable | 227:45 | 65 | 78.8 | 2020 | 100 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | No investigation activity in reporting period | No improvement action in reporting period | SOAF investigation completed - No work required | YWS01331
YWS01332 | Yorkshire Water | Live | GLYNNDALE DRIVE TANK SEWER | GLYNNDALE DRIVE/CSO | WRA6696 | WRA6696 | 1 | SO on sewer network | TA0105090000 | 501050 | 490000 | GB104027067980 | Burniston Beck/Sea Cut/Scalby Beck Catch to N Sea | River | 3489 | Upper Derwent Yorkshire | 3027 | Derwent Humber | SEA CUT (SCALBY BECK) | Not Applicable | Scarborough North Bay | Not Applicable | 39:18 | 12 | 8.4 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01332
YWS01333 | Yorkshire Water | Live | MARTON HALL FARM PUMPING STATION | MARTON HALL FARM/SPS | WRA6712 | WRA6712 | A2 | Storm discharge at pumping station | SD8951250184 | 389512 | 450184 | GB104027063032 | Aire from Gill Beck (Baildon) to River Calder | River | 3265 | Lower Aire | 3001 | Aire and Calder | CULVERTED TRIB OF BEDLAM DYKE | Not Applicable | Not Applicable | Not Applicable | 188:30 | 31 | 35.6 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01333
YWS01334 | Yorkshire Water | Live | OLD WHITTINGTON (CHESTERFIELD) STW | OLD WHITTINGTON/STW | WRA6756 | WRA6756 | 2 | Storm tank at WwTW | SK3925074370 | 439250 | 374370 | GB104027057771 | Rother, Spittal Brook to Doe Lea | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | RIVER ROTHER | Not Applicable | Not Applicable | Not Applicable | 879:00 | 79 | 76 | 2020 | 99.04 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01334
YWS01335 | Yorkshire Water | Live | OLD WHITTINGTON (CHESTERFIELD) STW | OLD WHITTINGTON/STW | WRA6756 | WRA6756 | 3 | Inlet SO at WwTW | SK3929074400 | 439200 | 374300 | GB104027057771 | Rother, Spittal Brook to Doe Lea | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | RIVER ROTHER | Not Applicable | Not Applicable | Not Applicable | 603:30 | 34 | 32 | 2020 | 99.28 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01335
YWS01336 | Yorkshire Water | Live | MARTON LE MOOR STW | MARTON LE MOOR/STW | WRA6820 | WRA6820 | 2 | Inlet SO at WwTW | SE3694070990 | 436940 | 470990 | GB104027064161 | Ure from River Skell to River Tutt | River | 3309 | Middle and Lower Ure | 3088 | Swale, Ure, Nidd and Upper Ouse | TRIB OF CUNDALL BECK | Not Applicable | Not Applicable | Not Applicable | 531:45 | 153 | 193.6 | 2020 | 87.02 | Sensor failure / issue | Resolved - Aug | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement ongoing | SOAF investigation ongoing | YWS01336
YWS01337 | Yorkshire Water | Live | LEEMING BAR SEWAGE TREATMENT WORKS | LEEMING BAR/STW | WRA6832 | WRA6832 | A2 | Storm tank at WwTW | SE2995789983 | 429957 | 489983 | GB104027068910 | Bedale/Newton/Burton Bk from Rand Bk to R Swale | River | 3317 | Middle Swale | 3088 | Swale, Ure, Nidd and Upper Ouse | BEDALE BECK | Not Applicable | Not Applicable | Not Applicable | 390:15 | 56 | 89.4 | 2020 | 99.89 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement completed | SOAF investigation ongoing | YWS01337
YWS01338 | Yorkshire Water | Live | BURLEY LODGE CSO | BURLEY LODGE/CSO | WRA6863 | WRA6863 | A1 | SO on sewer network | SE1739046268 | 417390 | 446268 | GB104027064258 | Wharfe from Hundwith Beck to River Washburn | River | 3318 | Middle Wharfe and Washburn | 3115 | Wharfe and Lower Ouse | RIVER WHARFE | Not Applicable | Not Applicable | Not Applicable | 2:15 | 6 | 7 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01338
YWS01339 | Yorkshire Water | Live | YORKSHIRE WATER SERVICES LTD, DETEN | BROOKHOUSE HILL/CSO | WRA6878 | WRA6878 | A1 | SO on sewer network | SK3046085030 | 430460 | 384997 | GB104027057760 | Porter from Source to River Sheaf | River | 3312 | Middle Don | 3029 | Don and Rother | PORTER BROOK | Not Applicable | Not Applicable | Not Applicable | 20:15 | 8 | 24 | 2020 | 98.61 |  |  | High spill threshold not met | High spill threshold not met | UWWTR investigation ongoing, Operational investigation ongoing | Operational improvement ongoing | SOAF investigation ongoing | YWS01339
YWS01340 | Yorkshire Water | Live | BEAMSLEY WASTEWATER TREATMENT WORKS | BEAMSLEY/STW | WRA6885 | WRA6885 | 2 | Inlet SO at WwTW | SE0766052350 | 407660 | 452350 | GB104027064050 | Kex Beck Catchment (trib of Wharfe) | River | 3318 | Middle Wharfe and Washburn | 3115 | Wharfe and Lower Ouse | RIVER WHARFE | Not Applicable | Wharfe at Cromwheel, Ilkley | Not Applicable | 238:15 | 104 | 94.75 | 2020 | 100 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS01340
YWS01341 | Yorkshire Water | Live | FLAMBOROUGH SPS | FLAMBOROUGH/CSO | WA6516 | WA6516 | A1 | Storm discharge at pumping station | TA2246269918 | 522462 | 469918 | Not part of a WFD catchment | Not part of a WFD catchment | River | N/A | N/A | N/A | N/A | HARTENDALE GUTTER | Not Applicable | Flamborough South Landing | Not Applicable | 128:10 | 32 | 26.25 | 2021 | 99.97 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01341
YWS01342 | Yorkshire Water | Live | FLAMBOROUGH NORTH SPS | FLAMBOROUGH NTH/CSO | WRA6887 | WRA6887 | A2 | Storm discharge at pumping station | TA2362071800 | 523600 | 471800 | Not part of a WFD catchment | Not part of a WFD catchment | River | N/A | N/A | N/A | N/A | MOOR FARM DRAIN | Not Applicable | Not Applicable | Not Applicable | 16:00 | 4 | 5.4 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01342
YWS01343 | Yorkshire Water | Live | KILHAM STW | KILHAM/STW | WRA6889 | WRA6889 | A2 | Storm tank at WwTW | TA0679064140 | 506790 | 464140 | GB104026067101 | Lowthorpe/Kelk/Foston Bks from Source to Frodingham Beck | River | 3492 | Upper Hull | 3039 | Hull and East Riding | LOWTHORPE BECK | Not Applicable | Not Applicable | Not Applicable | 1500:00 | 89 | 55 | 2020 | 99.82 |  |  | Performance - GW inundation | Performance - GW inundation | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS01343
YWS01344 | Yorkshire Water | Live | KILHAM STW | KILHAM/STW | WRA6889 | WRA6889 | A3 | Inlet SO at WwTW | TA0679064140 | 506790 | 464140 | GB104026067101 | Lowthorpe/Kelk/Foston Bks from Source to Frodingham Beck | River | 3492 | Upper Hull | 3039 | Hull and East Riding | LOWTHORPE BECK | Not Applicable | Not Applicable | Not Applicable | 0:15 | 1 | 0.4 | 2020 | 99.83 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01344
YWS01345 | Yorkshire Water | Live | KNOSTROP WWTW | KNOSTROP/H LEVEL STW/3XDWF OVERFLOW | WRA6924 | WRA6924 | A2 | Storm tank at WwTW | SE3384031860 | 433840 | 431860 | GB104027062880 | Wyke Beck from Source to River Aire | River | 3265 | Lower Aire | 3001 | Aire and Calder | WYKE BECK AND THE RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 679:00 | 73 | 102 | 2020 | 99.84 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01345
YWS01346 | Yorkshire Water | Live | KNOSTROP WWTW | KNOSTROP/H LEVEL STW/6XDWF OVERFLOW | WRA6924 | WRA6924 | A3 | Inlet SO at WwTW | SE3378031930 | 433780 | 431930 | GB104027062880 | Wyke Beck from Source to River Aire | River | 3265 | Lower Aire | 3001 | Aire and Calder | WYKE BECK AND THE RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 536:15 | 101 | 88.6 | 2020 | 99.93 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01346
YWS01347 | Yorkshire Water | Live | KNOSTROP WWTW | KNOSTROP/L LEVEL STW/3XDWF OVERFLOW | WRA6924 | WRA6924 | A5 | Storm tank at WwTW | SE3286031380 | 432860 | 431380 | GB104027063032 | Aire from Gill Beck (Baildon) to River Calder | River | 3265 | Lower Aire | 3001 | Aire and Calder | WYKE BECK AND THE RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 537:45 | 56 | 58.2 | 2020 | 99.97 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01347
YWS01348 | Yorkshire Water | Live | KNOSTROP WWTW | KNOSTROP/L LEVEL STW/6XDWF OVERFLOW | WRA6924 | WRA6924 | A7 | Inlet SO at WwTW | SE3286031380 | 432860 | 431380 | GB104027063032 | Aire from Gill Beck (Baildon) to River Calder | River | 3265 | Lower Aire | 3001 | Aire and Calder | WYKE BECK AND THE RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 150:15 | 27 | 161 | 2020 | 74.28 | Sensor failure / issue | Resolved - Apr | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS01348
YWS01349 | Yorkshire Water | Live | ESHOLT STW | BRADFORD ESHOLT/NO 2 STW | WRA6925 | WRA6925 | 3 | Storm tank at WwTW | SE1847039840 | 418480 | 439830 | GB104027063032 | Aire from Gill Beck (Baildon) to River Calder | River | 3265 | Lower Aire | 3001 | Aire and Calder | RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 560:45 | 77 | 75.8 | 2020 | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01349
YWS01350 | Yorkshire Water | Live | ESHOLT STW | BRADFORD ESHOLT/NO 2 STW | WRA6925 | WRA6925 | 4 | Inlet SO at WwTW | SE1847039840 | 418480 | 439820 | GB104027063032 | Aire from Gill Beck (Baildon) to River Calder | River | 3265 | Lower Aire | 3001 | Aire and Calder | RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 197:45 | 48 | 49.8 | 2020 | 98.77 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01350
YWS01351 | Yorkshire Water | Live | PRESTON STREET CSO | PRESTON STREET/CSO | WRA6948 | WRA6948 | A1 | SO on sewer network | SE1520033370 | 415206 | 433375 | GB104027062862 | Bradford Beck (Clayton Bk to R Aire) | River | 3307 | Middle Aire | 3001 | Aire and Calder | BRADFORD BECK | Not Applicable | Not Applicable | Not Applicable | 61:30 | 33 | 44.4 | 2020 | 100 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01351
YWS01352 | Yorkshire Water | Live | LONGSIDE LANE HALL CSO | LONGSIDE LANE HALL/CSO | WRA6968 | WRA6968 | A1 | SO on sewer network | SE1543032970 | 415432 | 432972 | GB104027062862 | Bradford Beck (Clayton Bk to R Aire) | River | 3307 | Middle Aire | 3001 | Aire and Calder | WESTBROOK | Not Applicable | Not Applicable | Not Applicable | 36:30 | 15 | 42.2 | 2020 | 100 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation ongoing | Operational improvement ongoing | SOAF investigation ongoing | YWS01352
YWS01353 | Yorkshire Water | Live | IRON CLIFFE ROAD CSO | IRON CLIFFE ROAD/CSO | WRA7029 | WRA7029 | A1 | SO on sewer network | SK4644371208 | 446443 | 371208 | GB104027057290 | Doe Lea from Source to Hawke Brook | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | TRIB OF RIVER DOE LEA | Not Applicable | Not Applicable | Not Applicable | 1:15 | 2 | 8.4 | 2020 | 20.68 | Power failure / issue | Resolved - February after reporting year | High spill threshold not met | High spill threshold not met | Operational investigation completed | Operational improvement completed | No SOAF investigation required | YWS01353
YWS01354 | Yorkshire Water | Live | STATION ROAD BOLSOVER CSO | STATION RD BOLSOVER/CSO | WRA7030 | WRA7030 | A1 | SO on sewer network | SK4675470802 | 446754 | 370802 | GB104027057290 | Doe Lea from Source to Hawke Brook | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | TRIBUTARY OF THE RIVER DOE LEA | Not Applicable | Not Applicable | Not Applicable | 18:00 | 18 | 22.2 | 2020 | 99.75 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01354
YWS01355 | Yorkshire Water | Live | GILPIN STREET DVISA A22 CSO | DVISA A22 GILPIN STREET/CSO | WRA7031 | WRA7031 | A1 | SO on sewer network | SK3447688633 | 434476 | 388633 | GB104027057412 | Don from River Loxley confl to River Don Works | River | 3312 | Middle Don | 3029 | Don and Rother | RIVER DON | Not Applicable | Not Applicable | Not Applicable | 1:10 | 1 | 0.6 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01355
YWS01356 | Yorkshire Water | Live | DUNCOMBE STREET CSO | DUNCOMBE STREET/CSO | WRA7091 | WRA7091 | A1 | SO on sewer network | SE1459533261 | 414595 | 433261 | GB104027062862 | Bradford Beck (Clayton Bk to R Aire) | River | 3307 | Middle Aire | 3001 | Aire and Calder | BRADFORD BECK | Not Applicable | Not Applicable | Not Applicable | 2:15 | 3 | 3 | 2020 | 81.92 | Comms failure / issue | Resolved - Apr | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01356
YWS01357 | Yorkshire Water | Live | ARKWRIGHT SPS | ARKWRIGHT/CSO | WRA7093 | WRA7093 | A2 | SO on sewer network | SK4362771362 | 443627 | 371362 | GB104027057310 | Pools Brook from Source to Doe Lea | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | POOLS BROOK | Not Applicable | Not Applicable | Not Applicable | 13:00 | 5 | 1 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | Operational investigation completed | No improvement action in reporting period | No SOAF investigation required | YWS01357
YWS01358 | Yorkshire Water | Live | HALL STREET SSO | HALL STREET/CSO | WRA7115 | WRA7115 | 1 | SO on sewer network | SD9355024040 | 393552 | 424049 | GB104027062600 | Walsden Water from Source to River Calder | River | 3487 | Upper Calder | 3001 | Aire and Calder | WALSDEN WATER | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0.2 | 2020 | 96.6 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01358
YWS01359 | Yorkshire Water | Live | YORKSHIRE WATER SERVICES LTD,AKETON | AKETON ROAD CUTSYKE/CSO | WRA7126 | WRA7126 | A2 | SO on sewer network | SE4188024260 | 441882 | 424260 | GB104027062632 | Calder from River Chald to River Aire | River | 3268 | Lower Calder | 3001 | Aire and Calder | CARR BECK | Not Applicable | Not Applicable | Not Applicable | 14:00 | 14 | 29.2 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01359
YWS01360 | Yorkshire Water | Live | ROCHDALE CANAL CSO | ROCHDALE CANAL/CSO | WRA7128 | WRA7128 | A1 | SO on sewer network | SE0640123628 | 406401 | 423628 | GB104027062642 | Calder from Ryburn Confluence to River Colne | River | 3310 | Middle Calder | 3001 | Aire and Calder | RIVER CALDER | Not Applicable | Not Applicable | Not Applicable | 0:46 | 1 | 0.8 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01360
YWS01361 | Yorkshire Water | Live | BRADLEY MILLS ROAD SPS | BRADLEY MILLS/2 CSO | WRA7164 | WRA7164 | 1 | Storm discharge at pumping station | SE1550017750 | 415500 | 417750 | GB104027062550 | Colne from River Holme to River Calder | River | 3097 | Colne and Holme | 3001 | Aire and Calder | RIVER COLNE | Not Applicable | Not Applicable | Not Applicable | 1:45 | 2 | 1.6 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01361
YWS01362 | Yorkshire Water | Live | KEIGHLEY (MARLEY) STW | KEIGHLEY MARLEY/STW | WRA7172 | WRA7172 | A3 | Storm tank at WwTW | SE0870841406 | 408708 | 441406 | GB104027063034 | Aire (R Worth to Gill Beck) | River | 3307 | Middle Aire | 3001 | Aire and Calder | RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 1780:15 | 122 | 125.75 | 2020 | 100 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01362
YWS01363 | Yorkshire Water | Live | KEIGHLEY (MARLEY) STW | KEIGHLEY MARLEY/STW | WRA7172 | WRA7172 | A5 | Inlet SO at WwTW | SE0870841406 | 408708 | 441406 | GB104027063034 | Aire (R Worth to Gill Beck) | River | 3307 | Middle Aire | 3001 | Aire and Calder | RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 584:15 | 105 | 93.4 | 2020 | 99.5 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | Operational investigation completed | Operational improvement completed | SOAF investigation completed - No work required | YWS01363
YWS01364 | Yorkshire Water | Live | KEIGHLEY (MARLEY) STW | KEIGHLEY MARLEY/STW | WRA7172 | WRA7172 | A6 | Inlet SO at WwTW | SE0870841406 | 408708 | 441406 | GB104027063034 | Aire (R Worth to Gill Beck) | River | 3307 | Middle Aire | 3001 | Aire and Calder | RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 312:00 | 61 | 48.2 | 2020 | 100 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS01364
YWS01365 | Yorkshire Water | Live | LEMONROYD WWTW | LEMONROYD/STW | WRA7220 | WRA7220 | A2 | Storm tank at WwTW | SE3820028000 | 438200 | 428000 | GB104027063032 | Aire from Gill Beck (Baildon) to River Calder | River | 3265 | Lower Aire | 3001 | Aire and Calder | RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 1049:15 | 83 | 75.8 | 2020 | 99.85 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement completed | SOAF investigation ongoing | YWS01365
YWS01366 | Yorkshire Water | Live | LEMONROYD WWTW | LEMONROYD/STW | WRA7220 | WRA7220 | A3 | Inlet SO at WwTW | SE3820028000 | 438200 | 428000 | GB104027063032 | Aire from Gill Beck (Baildon) to River Calder | River | 3265 | Lower Aire | 3001 | Aire and Calder | RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 225:45 | 45 | 38.5 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | Operational investigation completed | No improvement action in reporting period | No SOAF investigation required | YWS01366
YWS01367 | Yorkshire Water | Live | LONG RISTON WWTW | LONG RISTON NORTH/STW | WRA7249 | WRA7249 | A2 | Storm tank at WwTW | TA1193042430 | 511930 | 442430 | GB104026066910 | Fordyke Stream Lower to Holderness Dr | River | 3274 | Lower Hull | 3039 | Hull and East Riding | STONLEY GOAT DYKE | Not Applicable | Not Applicable | Not Applicable | 243:00 | 25 | 29.2 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01367
YWS01368 | Yorkshire Water | Live | DARK LANE WORSBORO CSO | DARK LANE WORSBORO/CSO | WRA7252 | WRA7252 | A1 | SO on sewer network | SE3594003490 | 435950 | 403495 | GB104027057510 | Dove from Source to River Dearne | River | 3125 | Dearne | 3029 | Don and Rother | RIVER DOVE | Not Applicable | Not Applicable | Not Applicable | 99:00 | 43 | 21.6 | 2020 | 96.15 |  |  | High spill threshold not met | High spill threshold not met | UWWTR investigation completed | No improvement action in reporting period | SOAF investigation completed - No work required | YWS01368
YWS01369 | Yorkshire Water | Live | KERESFORTH ROAD CSO | KERESFORTH ROAD/2 CSO | WRA7254 | WRA7254 | A1 | SO on sewer network | SE3230204893 | 432302 | 404893 | GB104027057520 | Dodworth Dyke from Source to River Dove | River | 3125 | Dearne | 3029 | Don and Rother | CLVRT TRIB OF DODWORTH DYKE | Not Applicable | Not Applicable | Not Applicable | 61:00 | 26 | 24.2 | 2020 | 99.91 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01369
YWS01370 | Yorkshire Water | Live | BAGLEY BECK RODLEY CSO | BAGLEY BECK RODLEY/CSO | WRA7339 | WRA7339 | A1 | SO on sewer network | SE2249036490 | 422512 | 436489 | GB104027063032 | Aire from Gill Beck (Baildon) to River Calder | River | 3265 | Lower Aire | 3001 | Aire and Calder | BAGLEY BECK | Not Applicable | Not Applicable | Not Applicable | 328:45 | 71 | 44 | 2020 | 100 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation ongoing | Operational improvement ongoing | SOAF investigation ongoing | YWS01370
YWS01371 | Yorkshire Water | Live | MOSS BRIDGE ROAD CSO | MOSS BRIDGE ROAD/CSO | WRA7340 | WRA7340 | A1 | SO on sewer network | SE2296636235 | 422966 | 436235 | GB104027063032 | Aire from Gill Beck (Baildon) to River Calder | River | 3265 | Lower Aire | 3001 | Aire and Calder | RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 64:00 | 17 | 55.2 | 2020 | 26.95 | Sensor failure / issue | Resolved - Sep | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01371
YWS01372 | Yorkshire Water | Live | DYKE VALE ROAD CSO | DYKE VALE ROAD 2/NO 2 CSO | WRA7342 | WRA7342 | 1 | SO on sewer network | SK4142084080 | 441430 | 384080 | GB104027057773 | Shire Brook | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | SHIRE BROOK IN CULVERT | Not Applicable | Not Applicable | Not Applicable | 4:00 | 3 | 6 | 2020 | 96.24 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01372
YWS01373 | Yorkshire Water | Live | SPRINGFIELD AVENUE 2 CSO | SPRINGFIELD AVENUE/2 CSO | WRA7343 | WRA7343 | A1 | SO on sewer network | TA1819066800 | 518880 | 465320 | GB640402491000 | Yorkshire South | Coastal Water | 3179 | Esk TraC | 3040 | Humber TraC | GYPSEY RACE | Not Applicable | Bridlington South Beach | Not Applicable | 36:08 | 26 | 6.2 | 2020 | 92.38 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01373
YWS01374 | Yorkshire Water | Live | BESSINGBY ROAD CSO | BESSINGBY ROAD/CSO | WRA7345 | WRA7345 | A1 | SO on sewer network | TA1812066790 | 518880 | 465320 | GB640402491000 | Yorkshire South | Coastal Water | 3179 | Esk TraC | 3040 | Humber TraC | GYPSEY RACE | Not Applicable | Bridlington South Beach | Not Applicable | 13:02 | 12 | 13.2 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01374
YWS01375 | Yorkshire Water | Live | DRIFFIELD STW | OUTGANG DRIFFIELD/CSO | WRA7349 | WRA7349 | A2 | SO on sewer network | TA0318056810 | 503180 | 456810 | GB70410028 | Driffield Navigation | Canal | 2027 | Hull and East Riding Canals | 2001 | Humber AWB | DRIFFIELD CANAL | Not Applicable | Not Applicable | Not Applicable | 1385:45 | 86 | 48 | 2020 | 99.97 |  |  | Performance - GW inundation | Performance - GW inundation | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS01375
YWS01376 | Yorkshire Water | Live | LEVEN WWTW | LEVEN/STW | WRA7350 | WRA7350 | A2 | Storm tank at WwTW | TA1031044250 | 510310 | 444250 | GB104026066910 | Fordyke Stream Lower to Holderness Dr | River | 3274 | Lower Hull | 3039 | Hull and East Riding | LEVEN TOWN DRAIN | Not Applicable | Not Applicable | Not Applicable | 75:30 | 8 | 21.4 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01376
YWS01377 | Yorkshire Water | Live | WORTH WAY NORTH BECK CSO | WORTH WAY NORTH BECK/CSO | WRA7351 | WRA7351 | 1 | SO on sewer network | SE0625040780 | 406254 | 440787 | GB104027062891 | Worth from Bridgehouse Beck to R Aire | River | 3307 | Middle Aire | 3001 | Aire and Calder | RIVER WORTH | Not Applicable | Not Applicable | Not Applicable | 204:30 | 42 | 43.8 | 2020 | 100 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01377
YWS01378 | Yorkshire Water | Live | BECKSIDE CSO | BECKSIDE/CSO | WRA7358 | WRA7358 | A1 | SO on sewer network | TA0581939339 | 505819 | 439339 | GB104026067212 | Hull from Arram Beck to Humber | River | 3274 | Lower Hull | 3039 | Hull and East Riding | RIVER HULL | Not Applicable | Not Applicable | Not Applicable | 161:30 | 38 | 42.4 | 2020 | 99.99 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01378
YWS01379 | Yorkshire Water | Live | INGBIRCHWORTH NO. 2 STW | INGBIRCHWORTH/NO 2 STW | WRA7365 | WRA7365 | A2 | Inlet SO at WwTW | SE2422003750 | 424220 | 403750 | GB104027057500 | Don from Source to Scout Dyke | River | 3490 | Upper Don | 3029 | Don and Rother | RIVER DON & INGBIRCHWORTH DYKE | Not Applicable | Not Applicable | Not Applicable | 404:45 | 100 | 102.6 | 2020 | 99.96 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01379
YWS01380 | Yorkshire Water | Live | RODLEY STORM TANK SITE | RODLEY TRANSFER/SPS/3XDWF OVERFLOW | WRA7372 | WRA7372 | 1 | SO on sewer network | SE2370036240 | 423710 | 436322 | GB104027063032 | Aire from Gill Beck (Baildon) to River Calder | River | 3265 | Lower Aire | 3001 | Aire and Calder | RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 1189:30 | 95 | 90.4 | 2020 | 99.87 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01380
YWS01381 | Yorkshire Water | Live | RODLEY STORM TANK SITE | RODLEY TRANSFER/SPS/6XDWF OVERFLOW | WRA7372 | WRA7372 | 2 | SO on sewer network | SE2370036240 | 423700 | 436240 | GB104027063032 | Aire from Gill Beck (Baildon) to River Calder | River | 3265 | Lower Aire | 3001 | Aire and Calder | RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 107:15 | 40 | 68.2 | 2020 | 62.27 | Sensor failure / issue | Resolved - Jun | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01381
YWS01382 | Yorkshire Water | Live | KEARSLEY LNE/DAYLANDS AVE/HAMELINE | KEARSLEY LANE/CSO | WRA7381 | WRA7381 | 1 | SO on sewer network | SK5097097850 | 450970 | 397850 | GB104027064244 | Kearsley Bk | River | 3312 | Middle Don | 3029 | Don and Rother | KEARSLEY BROOK | Not Applicable | Not Applicable | Not Applicable | 6:30 | 7 | 7 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01382
YWS01383 | Yorkshire Water | Live | KEARSLEY LNE/DAYLANDS AVE/HAMELINE | DAYLANDS AVENUE/NO 2 CSO | WRA7381 | WRA7381 | 2 | SO on sewer network | SK5097097850 | 450970 | 397850 | GB104027064244 | Kearsley Bk | River | 3312 | Middle Don | 3029 | Don and Rother | KEARSLEY BROOK | Not Applicable | Not Applicable | Not Applicable | 63:00 | 23 | 57 | 2020 | 99.99 |  |  | High spill threshold not met | N/A - Ongoing investigation | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS01383
YWS01384 | Yorkshire Water | Live | KEARSLEY LNE/DAYLANDS AVE/HAMELINE | HAMELINE ROAD/NO 2 CSO | WRA7381 | WRA7381 | 3 | SO on sewer network | SK5097097850 | 450970 | 397850 | GB104027064244 | Kearsley Bk | River | 3312 | Middle Don | 3029 | Don and Rother | KEARSLEY BROOK | Not Applicable | Not Applicable | Not Applicable | 0:45 | 2 | 0.4 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01384
YWS01385 | Yorkshire Water | Live | SOWERBY BRIDGE SEWAGE PUMPING STN | SOWERBY BRIDGE/CSO | WRA7389 | WRA7389 | A1 | SO on sewer network | SE0720023670 | 407240 | 423635 | GB104027062642 | Calder from Ryburn Confluence to River Colne | River | 3310 | Middle Calder | 3001 | Aire and Calder | RIVER CALDER | Not Applicable | Not Applicable | Not Applicable | 2:15 | 2 | 25.2 | 2020 | 99.9 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01385
YWS01386 | Yorkshire Water | Live | SMITHY MILLS LANE CSO | SMITHY MILLS LANE/2 CSO | WRA7399 | WRA7399 | 1 | SO on sewer network | SE2798038390 | 427988 | 438389 | GB104027062900 | Meanwood Beck from Source to River Aire | River | 3265 | Lower Aire | 3001 | Aire and Calder | ADEL BECK | Not Applicable | Not Applicable | Not Applicable | 31:45 | 28 | 24.8 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01386
YWS01387 | Yorkshire Water | Live | ADEL RING ROAD CSO | ADEL RING ROAD/CSO | WRA7400 | WRA7400 | A1 | SO on sewer network | SE2772338518 | 427723 | 438518 | GB104027062900 | Meanwood Beck from Source to River Aire | River | 3265 | Lower Aire | 3001 | Aire and Calder | TRIB OF MEANWOOD BECK | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0.2 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01387
YWS01388 | Yorkshire Water | Live | MEANWOOD PARK SIDE CSO | MEANWOOD PARK SIDE/CSO | WRA7401 | WRA7401 | A1 | SO on sewer network | SE2820438515 | 428204 | 438515 | GB104027062900 | Meanwood Beck from Source to River Aire | River | 3265 | Lower Aire | 3001 | Aire and Calder | ADEL BECK | Not Applicable | Not Applicable | Not Applicable | 351:45 | 60 | 55.4 | 2020 | 100 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01388
YWS01389 | Yorkshire Water | Live | BUCKSTONE ROAD CSO | BUCKSTONE ROAD/NO X CSO | WRA7403 | WRA7403 | A1 | SO on sewer network | SE2838439758 | 428384 | 439758 | GB104027062900 | Meanwood Beck from Source to River Aire | River | 3265 | Lower Aire | 3001 | Aire and Calder | ADEL BECK | Not Applicable | Not Applicable | Not Applicable | 162:30 | 55 | 60.2 | 2020 | 100 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation completed | No improvement action in reporting period | SOAF investigation completed - No work required | YWS01389
YWS01390 | Yorkshire Water | Live | WORSBROUGH STW | WORSBROUGH/STW | WRA7404 | WRA7404 | A2 | Storm tank at WwTW | SE3628003430 | 436280 | 403430 | GB104027057510 | Dove from Source to River Dearne | River | 3125 | Dearne | 3029 | Don and Rother | RIVER DOVE | Not Applicable | Not Applicable | Not Applicable | 331:15 | 42 | 47.8 | 2020 | 99.83 |  |  | High spill threshold not met | Performance - Infiltration | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01390
YWS01391 | Yorkshire Water | Live | ARCHER ROAD NO 2 CSO | ARCHER ROAD/NO 2 CSO | WRA7405 | WRA7405 | A1 | SO on sewer network | SK3399883477 | 433998 | 383477 | GB104027057750 | Sheaf from Source to River Don | River | 3312 | Middle Don | 3029 | Don and Rother | GRAVES PARK BECK | Not Applicable | Not Applicable | Not Applicable | 7:45 | 5 | 1 | 2020 | 99.87 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01391
YWS01392 | Yorkshire Water | Live | RUSHDALE ROAD CSO | RUSHDALE ROAD/CSO | WRA7406 | WRA7406 | A1 | SO on sewer network | SK3573484492 | 435734 | 384492 | GB104027057750 | Sheaf from Source to River Don | River | 3312 | Middle Don | 3029 | Don and Rother | MEERS BROOK CULVERTED | Not Applicable | Not Applicable | Not Applicable | 75:45 | 43 | 43.8 | 2020 | 100 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01392
YWS01393 | Yorkshire Water | Live | WIDE LANE MORLEY CSO | WIDE LANE MORLEY/CSO | WRA7407 | WRA7407 | A1 | SO on sewer network | SE2876827575 | 428768 | 427575 | GB104027062750 | Milshaw Beck from Source to Low/Wortley/Pudsey Bks | River | 3265 | Lower Aire | 3001 | Aire and Calder | OWLER BECK | Not Applicable | Not Applicable | Not Applicable | 151:15 | 66 | 56 | 2020 | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01393
YWS01394 | Yorkshire Water | Live | HUDDERSFIELD STW | DEIGHTON/STW | WRA7409 | WRA7409 | 3 | Storm tank at WwTW | SE1725019480 | 417250 | 419480 | GB104027062550 | Colne from River Holme to River Calder | River | 3097 | Colne and Holme | 3001 | Aire and Calder | RIVER CALDER & RIVER COLNE | Not Applicable | Not Applicable | Not Applicable | 1620:45 | 132 | 109.6 | 2020 | 100 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement completed | SOAF investigation ongoing | YWS01394
YWS01395 | Yorkshire Water | Live | HUDDERSFIELD STW | BRIGHOUSE/UPPER STW/3XDWF OVERFLOW | WRA7409 | WRA7409 | 4 | Storm tank at WwTW | SE1729021120 | 417300 | 421120 | GB104027062642 | Calder from Ryburn Confluence to River Colne | River | 3310 | Middle Calder | 3001 | Aire and Calder | RIVER CALDER & RIVER COLNE | Not Applicable | Not Applicable | Not Applicable | 864:00 | 88 | 88.4 | 2020 | 98.52 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01395
YWS01396 | Yorkshire Water | Live | HUDDERSFIELD STW | DEIGHTON/STW | WRA7409 | WRA7409 | 5 | Inlet SO at WwTW | SE1697019070 | 416970 | 419080 | GB104027062550 | Colne from River Holme to River Calder | River | 3097 | Colne and Holme | 3001 | Aire and Calder | RIVER CALDER & RIVER COLNE | Not Applicable | Not Applicable | Not Applicable | 450:30 | 86 | 71.8 | 2020 | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01396
YWS01397 | Yorkshire Water | Live | HUDDERSFIELD STW | BRIGHOUSE/UPPER STW/6XDWF OVERFLOW | WRA7409 | WRA7409 | 6 | Inlet SO at WwTW | SE1729021120 | 417290 | 421120 | GB104027062642 | Calder from Ryburn Confluence to River Colne | River | 3310 | Middle Calder | 3001 | Aire and Calder | RIVER CALDER & RIVER COLNE | Not Applicable | Not Applicable | Not Applicable | 303:30 | 49 | 55.6 | 2020 | 99.76 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01397
YWS01398 | Yorkshire Water | Live | BIRLEY VALE COMBINED SEWER OVERFLOW | BIRLEY MANSFIELD RD/CSO | WRA7419 | WRA7419 | 1 | SO on sewer network | SK3943084260 | 439430 | 384260 | GB104027057773 | Shire Brook | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | SHIRE BROOK | Not Applicable | Not Applicable | Not Applicable | 120:30 | 36 | 38.6 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01398
YWS01399 | Yorkshire Water | Live | NEW AUGUSTUS STREET CSO | NEW AUGUSTUS ST/CSO | WRA7447 | WRA7447 | A1 | SO on sewer network | SE1697032830 | 416970 | 432830 | GB104027062862 | Bradford Beck (Clayton Bk to R Aire) | River | 3307 | Middle Aire | 3001 | Aire and Calder | EASTBROOK | Not Applicable | Not Applicable | Not Applicable | 1:15 | 2 | 0.6 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01399
YWS01400 | Yorkshire Water | Live | DICK LNE CSO & NEW LNE SPS | DICK LANE/NO 2 CSO | WRA7450 | WRA7450 | A2 | SO on sewer network | SE1971533266 | 419715 | 433266 | GB104027062830 | Low/Wortley/Pudsey Bks | River | 3265 | Lower Aire | 3001 | Aire and Calder | CUL TRIB OF TYERSAL BECK | Not Applicable | Not Applicable | Not Applicable | 155:00 | 34 | 6.8 | 2020 | 99.93 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01400
YWS01401 | Yorkshire Water | Live | WOOD BOTTOM CSO | WOOD BOTTOM/CSO | WRA7455 | WRA7455 | 1 | SO on sewer network | SE0536012050 | 405360 | 412048 | GB104027063330 | Colne from Wessenden Brook to R Holme | River | 3097 | Colne and Holme | 3001 | Aire and Calder | RIVER COLNE | Not Applicable | Not Applicable | Not Applicable | 234:30 | 66 | 84.2 | 2020 | 99.83 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS01401
YWS01402 | Yorkshire Water | Live | SPA MILLS BRIDGE ST CSO | SPA MILLS BRIDGE ST/CSO | WRA7456 | WRA7456 | A1 | SO on sewer network | SE0851014140 | 408513 | 414143 | GB104027063330 | Colne from Wessenden Brook to R Holme | River | 3097 | Colne and Holme | 3001 | Aire and Calder | RIVER COLNE | Not Applicable | Not Applicable | Not Applicable | 213:45 | 51 | 64.2 | 2020 | 99.99 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01402
YWS01403 | Yorkshire Water | Live | GORDON TERRACE CSO | GORDON TERRACE/CSO | WRA7457 | WRA7457 | A1 | SO on sewer network | SE0989214773 | 409892 | 414773 | GB104027063330 | Colne from Wessenden Brook to R Holme | River | 3097 | Colne and Holme | 3001 | Aire and Calder | RIVER COLNE | Not Applicable | Not Applicable | Not Applicable | 93:15 | 37 | 96.2 | 2020 | 99.99 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01403
YWS01404 | Yorkshire Water | Live | BARGATE CSO | BARGATE/NO 2 CSO | WRA7458 | WRA7458 | 1 | SO on sewer network | SE0973014550 | 409726 | 414544 | GB104027063330 | Colne from Wessenden Brook to R Holme | River | 3097 | Colne and Holme | 3001 | Aire and Calder | RIVER COLNE | Not Applicable | Not Applicable | Not Applicable | 24:00 | 17 | 20 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01404
YWS01405 | Yorkshire Water | Live | CAUSEWAY SIDE 12 CSO | CAUSEWAY SIDE 12/CSO | WRA7459 | WRA7459 | A1 | SO on sewer network | SE0974014010 | 409756 | 414018 | GB104027063330 | Colne from Wessenden Brook to R Holme | River | 3097 | Colne and Holme | 3001 | Aire and Calder | CULV'D TRIB OF HOYLE HOUSE BRK | Not Applicable | Not Applicable | Not Applicable | 262:00 | 86 | 69.2 | 2020 | 96.86 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement ongoing | SOAF investigation ongoing | YWS01405
YWS01406 | Yorkshire Water | Live | CAUSEWAY SIDE 13 C.S.O | CAUSEWAY SIDE 13/CSO | WRA7460 | WRA7460 | A1 | SO on sewer network | SE0958714130 | 409587 | 414130 | GB104027063330 | Colne from Wessenden Brook to R Holme | River | 3097 | Colne and Holme | 3001 | Aire and Calder | HOYLE HOUSE BROOK | Not Applicable | Not Applicable | Not Applicable | 22:00 | 20 | 27.6 | 2020 | 92.75 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01406
YWS01407 | Yorkshire Water | Live | COPLEY BANK CSO | COPLEY BANK/CSO | WRA7461 | WRA7461 | 1 | SO on sewer network | SE0927015540 | 409270 | 415549 | GB104027063330 | Colne from Wessenden Brook to R Holme | River | 3097 | Colne and Holme | 3001 | Aire and Calder | UNNAMED TRIB OF RIVER COLNE | Not Applicable | Not Applicable | Not Applicable | 0:45 | 3 | 2.6 | 2020 | 97.79 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01407
YWS01408 | Yorkshire Water | Live | BROOK LANE CSO | GOLCAR BROOK LANE/CSO | WRA7462 | WRA7462 | 1 | SO on sewer network | SE0950015610 | 409502 | 415613 | GB104027063330 | Colne from Wessenden Brook to R Holme | River | 3097 | Colne and Holme | 3001 | Aire and Calder | UNNAMED TRIB OF RIVER COLNE | Not Applicable | Not Applicable | Not Applicable | 0:30 | 2 | 6.5 | 2020 | 99.98 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01408
YWS01409 | Yorkshire Water | Live | RAMSDEN MILL CSO | RAMSDEN MILL/CSO | WRA7463 | WRA7463 | A1 | SO on sewer network | SE1036215442 | 410362 | 415442 | GB104027063330 | Colne from Wessenden Brook to R Holme | River | 3097 | Colne and Holme | 3001 | Aire and Calder | RIVER COLNE | Not Applicable | Not Applicable | Not Applicable | 2:45 | 8 | 44.4 | 2020 | 98.22 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | No investigation activity in reporting period | No improvement action in reporting period | SOAF investigation completed - No work required | YWS01409
YWS01410 | Yorkshire Water | Live | PONTEFRACT ROAD BARNSLEY CSO | PONTEFRACT RD BARNSLY/CSO | WRA7468 | WRA7468 | A1 | SO on sewer network | SE3564006240 | 435640 | 406240 | GB104027063171 | Dearne from Cawthorne Dyke to Lundwood STW | River | 3125 | Dearne | 3029 | Don and Rother | SOUGH DYKE | Not Applicable | Not Applicable | Not Applicable | 70:00 | 42 | 37.4 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01410
YWS01411 | Yorkshire Water | Live | PUDSEY (SMALEWELL) CSO | PUDSEY SMALEWELL/CSO | WRA7473 | WRA7473 | 1 | SO on sewer network | SE2075032880 | 420751 | 432872 | GB104027062830 | Low/Wortley/Pudsey Bks | River | 3265 | Lower Aire | 3001 | Aire and Calder | TYERSAL BECK | Not Applicable | Not Applicable | Not Applicable | 154:00 | 41 | 52.2 | 2020 | 100 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01411
YWS01412 | Yorkshire Water | Live | YORKSHIRE WATER SERVICES LTD | WATH ON DEARNE/CSO | WRA7477 | WRA7477 | 1 | SO on sewer network | SE4446001100 | 444474 | 401108 | GB104027063173 | Dearne Darfield STW to River Don | River | 3125 | Dearne | 3029 | Don and Rother | BROOK DIKE | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0 | 2020 | 99.92 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01412
YWS01413 | Yorkshire Water | Live | FRASER DRIVE SPS | FRASER DRIVE/CSO | WRA7482 | WRA7482 | A2 | SO on sewer network | SK3463083152 | 434630 | 383152 | GB104027057750 | Sheaf from Source to River Don | River | 3312 | Middle Don | 3029 | Don and Rother | GRAVES PARK BECK (CULVERTED) | Not Applicable | Not Applicable | Not Applicable | 253:15 | 57 | 69.6 | 2020 | 97.56 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | No investigation activity in reporting period | No improvement action in reporting period | SOAF investigation completed - Work required | YWS01413
YWS01414 | Yorkshire Water | Live | LAMBRA ROAD CSO | LAMBRA ROAD/CSO | WRA7491 | WRA7491 | A1 | SO on sewer network | SE3501006110 | 435010 | 406110 | GB104027063171 | Dearne from Cawthorne Dyke to Lundwood STW | River | 3125 | Dearne | 3029 | Don and Rother | SOUGH DYKE (CULVERT) | Not Applicable | Not Applicable | Not Applicable | 206:15 | 70 | 63.6 | 2020 | 100 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01414
YWS01415 | Yorkshire Water | Live | SHIBDEN HEAD SPS | SHIBDEN HEAD/CSO | WRA7500 | WRA7500 | 1 | SO on sewer network | SE0969029090 | 409690 | 429090 | GB104027062720 | Red Beck, Source to Calder and Hebble Navigation | River | 3310 | Middle Calder | 3001 | Aire and Calder | SHIBDEN BROOK | Not Applicable | Not Applicable | Not Applicable |  |  | 36.67 | 2020 | 0 | Telemetry or data archiving failure / issue | Resolved - February after reporting year | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01415
YWS01416 | Yorkshire Water | Live | SHIBDEN HEAD SPS | SHIBDEN HEAD/CSO | WRA7500 | WRA7500 | 2 | SO on sewer network | SE0966028430 | 409660 | 428430 | GB104027062720 | Red Beck, Source to Calder and Hebble Navigation | River | 3310 | Middle Calder | 3001 | Aire and Calder | SHIBDEN BROOK | Not Applicable | Not Applicable | Not Applicable | 34:15 | 10 | 45.2 | 2020 | 23.04 | Telemetry or data archiving failure / issue | Resolved - Oct | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01416
YWS01417 | Yorkshire Water | Live | SOUTH ELMSALL WWTW | SOUTH ELMSALL/STW/3XDWF OVERFLOW | WRA7507 | WRA7507 | 2 | Storm tank at WwTW | SE4830010650 | 448300 | 410640 | GB104027063200 | Ea Beck from Frickley Beck to the Skell | River | 3272 | Lower Don | 3029 | Don and Rother | HEMSWORTH DYKE | Not Applicable | Not Applicable | Not Applicable | 301:30 | 45 | 60.2 | 2020 | 99.89 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01417
YWS01418 | Yorkshire Water | Live | SOUTH ELMSALL WWTW | SOUTH ELMSALL/STW/6XDWF OVERFLOW | WRA7507 | WRA7507 | 4 | Inlet SO at WwTW | SE4821010640 | 448250 | 410650 | GB104027063200 | Ea Beck from Frickley Beck to the Skell | River | 3272 | Lower Don | 3029 | Don and Rother | HEMSWORTH DYKE | Not Applicable | Not Applicable | Not Applicable | 219:45 | 58 | 48.4 | 2020 | 99.89 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01418
YWS01419 | Yorkshire Water | Live | BARNBURGH STW | BARNBURGH/STW | WRA7509 | WRA7509 | 2 | Inlet SO at WwTW | SE4759003100 | 447590 | 403100 | GB104027063173 | Dearne Darfield STW to River Don | River | 3125 | Dearne | 3029 | Don and Rother | TRIBUTARY OF THE RIVER DEARNE | Not Applicable | Not Applicable | Not Applicable | 679:45 | 57 | 95 | 2020 | 99.94 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation ongoing | Operational improvement ongoing | SOAF investigation ongoing | YWS01419
YWS01420 | Yorkshire Water | Live | HALIFAX COPLEY STW | HALIFAX COPLEY/STW | WRA7510 | WRA7510 | A2 | Storm tank at WwTW | SE0922022290 | 409220 | 422290 | GB104027062642 | Calder from Ryburn Confluence to River Colne | River | 3310 | Middle Calder | 3001 | Aire and Calder | RIVER CALDER AND HEBBLE BROOK | Not Applicable | Not Applicable | Not Applicable | 982:54 | 109 | 85 | 2020 | 100 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS01420
YWS01421 | Yorkshire Water | Live | HALIFAX COPLEY STW | SALTERHEBBLE/STW/3XDWF OVERFLOW | WRA7510 | WRA7510 | A3 | Storm tank at WwTW | SE0959022370 | 409590 | 422370 | GB104027062780 | Hebble Brook from Source to River Calder | River | 3310 | Middle Calder | 3001 | Aire and Calder | RIVER CALDER AND HEBBLE BROOK | Not Applicable | Not Applicable | Not Applicable | 408:40 | 61 | 69.6 | 2020 | 99.22 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01421
YWS01422 | Yorkshire Water | Live | HALIFAX COPLEY STW | SALTERHEBBLE/STW/6XDWF OVERFLOW | WRA7510 | WRA7510 | A4 | Inlet SO at WwTW | SE0971022760 | 409710 | 422760 | GB104027062780 | Hebble Brook from Source to River Calder | River | 3310 | Middle Calder | 3001 | Aire and Calder | RIVER CALDER AND HEBBLE BROOK | Not Applicable | Not Applicable | Not Applicable | 383:25 | 106 | 93.6 | 2020 | 100 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01422
YWS01423 | Yorkshire Water | Live | LEE BRIDGE CSO | LEE BRIDGE/CSO | WRA7511 | WRA7511 | A1 | SO on sewer network | SE0871425937 | 408714 | 425937 | GB104027062780 | Hebble Brook from Source to River Calder | River | 3310 | Middle Calder | 3001 | Aire and Calder | OVENDEN BROOK | Not Applicable | Not Applicable | Not Applicable | 1:00 | 4 | 1 | 2020 | 99.77 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01423
YWS01424 | Yorkshire Water | Live | HOLDSWORTH ROAD CSO | HOLDSWORTH ROAD/NO 2 CSO | WRA7512 | WRA7512 | 1 | SO on sewer network | SE0841028600 | 408411 | 428608 | GB104027062780 | Hebble Brook from Source to River Calder | River | 3310 | Middle Calder | 3001 | Aire and Calder | STRINES BECK | Not Applicable | Not Applicable | Not Applicable | 27:30 | 12 | 3 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01424
YWS01425 | Yorkshire Water | Live | VICTORIA PARK CSO | VICTORIA PARK/CSO | WRA7515 | WRA7515 | A1 | SO on sewer network | SE1680227955 | 416802 | 427955 | GB104027062710 | Spen Beck from Source to River Calder | River | 3268 | Lower Calder | 3001 | Aire and Calder | LOW MOOR BECK (CULVERTED) | Not Applicable | Not Applicable | Not Applicable | 119:00 | 24 | 29.8 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01425
YWS01426 | Yorkshire Water | Live | STONES LANE/WAINGATE CSO | STONES LANE WAINGATE/CSO | WRA7518 | WRA7518 | 1 | SO on sewer network | SE0957013960 | 409573 | 413960 | GB104027063330 | Colne from Wessenden Brook to R Holme | River | 3097 | Colne and Holme | 3001 | Aire and Calder | HOYLE HOUSE BROOK (CULVERTED) | Not Applicable | Not Applicable | Not Applicable | 2:30 | 3 | 4.4 | 2020 | 11.2 | Sensor failure / issue | Resolved - Nov | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01426
YWS01427 | Yorkshire Water | Live | FERNLEA GROVE CSO | FERNLEA GROVE/CSO | WRA7519 | WRA7519 | A1 | SO on sewer network | SE1018315131 | 410183 | 415131 | GB104027063330 | Colne from Wessenden Brook to R Holme | River | 3097 | Colne and Holme | 3001 | Aire and Calder | RIVER COLNE | Not Applicable | Not Applicable | Not Applicable | 21:30 | 21 | 24 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01427
YWS01428 | Yorkshire Water | Live | BARBER ROW NO 2 CSO | BARBER ROW/NO 2 CSO | WRA7520 | WRA7520 | A1 | SO on sewer network | SE0954014495 | 409540 | 414495 | GB104027063330 | Colne from Wessenden Brook to R Holme | River | 3097 | Colne and Holme | 3001 | Aire and Calder | RIVER COLNE | Not Applicable | Not Applicable | Not Applicable | 389:00 | 74 | 100.6 | 2020 | 100 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS01428
YWS01429 | Yorkshire Water | Live | HOYLE HOUSE BRIDGE CSO | HOYLE HOUSE BRIDGE/CSO | WRA7527 | WRA7527 | A1 | SO on sewer network | SE1478324455 | 414783 | 424455 | GB104027062700 | Clifton Beck from Source to River Calder | River | 3310 | Middle Calder | 3001 | Aire and Calder | CLIFTON BECK | Not Applicable | Not Applicable | Not Applicable | 45:00 | 30 | 34.6 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01429
YWS01430 | Yorkshire Water | Live | ALLERTON BYWATER CSO | ALLERTON BYWATER/CSO | WRA7536 | WRA7536 | A1 | SO on sewer network | SE4226227568 | 442262 | 427568 | GB104027063032 | Aire from Gill Beck (Baildon) to River Calder | River | 3265 | Lower Aire | 3001 | Aire and Calder | TRIB OF RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 11:00 | 3 | 3.4 | 2020 | 99.98 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01430
YWS01431 | Yorkshire Water | Live | GARFORTH STORM TANKS NO 1 & 2 | GARFORTH TANKS/CSO | WRA7537 | WRA7537 | A1 | SO on sewer network | SE3980032060 | 439800 | 432060 | GB104027062810 | Lin Dike from Source to River Aire | River | 3265 | Lower Aire | 3001 | Aire and Calder | THE BECK | Not Applicable | Not Applicable | Not Applicable | 394:30 | 54 | 47.8 | 2020 | 99.98 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01431
YWS01432 | Yorkshire Water | Live | KIPPAX STORM TANKS | KIPPAX TANKS/CSO | WRA7538 | WRA7538 | A1 | SO on sewer network | SE4107029770 | 441070 | 429770 | GB104027062810 | Lin Dike from Source to River Aire | River | 3265 | Lower Aire | 3001 | Aire and Calder | HOLLINS BECK | Not Applicable | Not Applicable | Not Applicable | 4:00 | 2 | 1.4 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01432
YWS01433 | Yorkshire Water | Live | KIPPAX STORM TANKS | KIPPAX TANKS/CSO | WRA7538 | WRA7538 | A2 | SO on sewer network | SE4101029710 | 441010 | 429710 | GB104027062810 | Lin Dike from Source to River Aire | River | 3265 | Lower Aire | 3001 | Aire and Calder | HOLLINS BECK | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0.8 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01433
YWS01434 | Yorkshire Water | Live | ADWICK NO.2 STW | ADWICK/NO 2 STW | WRA7541 | WRA7541 | A2 | Storm tank at WwTW | SE5469008050 | 454690 | 408050 | GB104027057591 | Ea Beck from the Skell to River Don | River | 3272 | Lower Don | 3029 | Don and Rother | MILL DIKE | Not Applicable | Not Applicable | Not Applicable | 207:15 | 32 | 32.8 | 2020 | 99.89 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01434
YWS01435 | Yorkshire Water | Live | BENTLEY RISE PS & CSO | BENTLEY RISE/CSO | WRA7543 | WRA7543 | 1 | Storm discharge at pumping station | SE5665004860 | 456659 | 404861 | GB104027057541 | Bentley Mill Stream | River | 3272 | Lower Don | 3029 | Don and Rother | FOWLER BRIDGE DRAIN | Not Applicable | Not Applicable | Not Applicable | 105:45 | 16 | 19.2 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | Operational investigation completed | No improvement action in reporting period | No SOAF investigation required | YWS01435
YWS01436 | Yorkshire Water | Live | OVENDEN ROAD CSO | OVENDEN ROAD/CSO | WRA7547 | WRA7547 | A1 | SO on sewer network | SE0865526236 | 408655 | 426236 | GB104027062780 | Hebble Brook from Source to River Calder | River | 3310 | Middle Calder | 3001 | Aire and Calder | OVENDEN BROOK (CULVERTED) | Not Applicable | Not Applicable | Not Applicable | 21:15 | 16 | 20.8 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01436
YWS01437 | Yorkshire Water | Live | MARSH LANE SPS & STORM TANK SITE | KNOTTINGLEY MARSH LN/CSO | WRA7551 | WRA7551 | A1 | Storm discharge at pumping station | SE5100024090 | 451000 | 424090 | GB104027062760 | Aire from River Calder to River Ouse | River | 3265 | Lower Aire | 3001 | Aire and Calder | RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 625:15 | 55 | 49.6 | 2020 | 100 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01437
YWS01438 | Yorkshire Water | Live | MARSH LANE SPS & STORM TANK SITE | KNOTTINGLEY MARSH LN/CSO | WRA7551 | WRA7551 | A2 | Storm discharge at pumping station | SE5100024090 | 451000 | 424090 | GB104027062760 | Aire from River Calder to River Ouse | River | 3265 | Lower Aire | 3001 | Aire and Calder | RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 157:45 | 31 | 34.6 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01438
YWS01439 | Yorkshire Water | Live | FERRYBRIDGE SPS & STORM TANK SITE | FERRYBRIDGE/CSO | WRA7552 | WRA7552 | A2 | Storm discharge at pumping station | SE4800624869 | 448006 | 424869 | GB104027062760 | Aire from River Calder to River Ouse | River | 3265 | Lower Aire | 3001 | Aire and Calder | FRYSTON BECK | Not Applicable | Not Applicable | Not Applicable | 29:45 | 10 | 31 | 2020 | 57.7 | Sensor failure / issue | Resolved - Jun | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01439
YWS01440 | Yorkshire Water | Live | OLD GOOLE SPS | OLD GOOLE/CSO | WRA7555 | WRA7555 | A2 | SO on sewer network | SE7469422825 | 474694 | 422825 | GB104027062760 | Aire from River Calder to River Ouse | River | 3265 | Lower Aire | 3001 | Aire and Calder | DUTCH RIVER (RIVER DON) | Not Applicable | Not Applicable | Not Applicable | 22:30 | 23 | 43 | 2020 | 100 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01440
YWS01441 | Yorkshire Water | Live | GOOLE LOCK HILL SPS | GOOLE LOCK HILL/CSO | WRA7557 | WRA7557 | A2 | SO on sewer network | SE7495423471 | 474954 | 423471 | GB530402609203 | HUMBER UPPER | Transitional Water | 3228 | Humber Estuary TraC | 3040 | Humber TraC | RIVER OUSE | Not Applicable | Not Applicable | Not Applicable | 0:45 | 2 | 3 | 2020 | 99.27 |  |  | High spill threshold not met | High spill threshold not met | UWWTR investigation completed | No improvement action in reporting period | SOAF investigation completed - No work required | YWS01441
YWS01447 | Yorkshire Water | Live | OLIVE GROVE DEPOT CSO | OLIVE GROVE DEPOT/CSO | WRA7572 | WRA7572 | A1 | SO on sewer network | SK3547085441 | 435470 | 385441 | GB104027057750 | Sheaf from Source to River Don | River | 3312 | Middle Don | 3029 | Don and Rother | RIVER SHEAF (CULVERTED) | Not Applicable | Not Applicable | Not Applicable | 11:15 | 12 | 14.6 | 2020 | 98.72 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01447
YWS01448 | Yorkshire Water | Live | CUDWORTH SPS | CUDWORTH/NO 2 CSO | WRA7592 | WRA7592 | A2 | Storm discharge at pumping station | SE3809708678 | 438097 | 408678 | GB104027063230 | Cudworth Dyke from Source to River Dearne | River | 3125 | Dearne | 3029 | Don and Rother | TRIB OF SMALL BRIDGE DYKE | Not Applicable | Not Applicable | Not Applicable | 100:45 | 47 | 49.2 | 2020 | 100 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement ongoing | SOAF investigation ongoing | YWS01448
YWS01449 | Yorkshire Water | Live | BASIN BRIDGE SPS | BASIN BRIDGE/CSO | WRA7617 | WRA7617 | A1 | Storm discharge at pumping station | TA1712025070 | 517120 | 425070 | GB530402609201 | HUMBER LOWER | Transitional Water | 3228 | Humber Estuary TraC | 3040 | Humber TraC | R. HUMBER & BURSTWICK DRAIN | Not Applicable | Not Applicable | Not Applicable | 119:30 | 22 | 11 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | Operational investigation ongoing | Operational improvement ongoing | No SOAF investigation required | YWS01449
YWS01450 | Yorkshire Water | Live | HEDON STW | HEDON/STW | WRA7618 | WRA7618 | A2 | Storm tank at WwTW | TA1712025070 | 517120 | 425070 | GB530402609201 | HUMBER LOWER | Transitional Water | 3228 | Humber Estuary TraC | 3040 | Humber TraC | RIVER HUMBER | Not Applicable | Not Applicable | Not Applicable | 161:30 | 31 | 30.4 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01450
YWS01451 | Yorkshire Water | Live | HULL WWTW | HULL/STW | WRA7619 | WRA7619 | 3 | Inlet SO at WwTW | TA1486028060 | 514860 | 428060 | GB530402609201 | HUMBER LOWER | Transitional Water | 3228 | Humber Estuary TraC | 3040 | Humber TraC | RIVER HUMBER | Not Applicable | Not Applicable | Not Applicable | 2499:00 | 194 | 88.4 | 2020 | 100 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS01451
YWS01452 | Yorkshire Water | Live | BRIDLINGTON STW | BRIDLINGTON/STW | WRA7637 | WRA7637 | 2 | Inlet SO at WwTW | TA1929064910 | 519290 | 464910 | GB640402491000 | Yorkshire South | Coastal Water | 3179 | Esk TraC | 3040 | Humber TraC | NORTH SEA | Not Applicable | Bridlington South Beach | Not Applicable | 405:00 | 90 | 74.4 | 2020 | 99.92 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01452
YWS01453 | Yorkshire Water | Live | BRIDLINGTON STW | BRIDLINGTON/STW | WRA7637 | WRA7637 | 5 | Inlet SO at WwTW | TA1801065600 | 518010 | 465600 | GB640402491000 | Yorkshire South | Coastal Water | 3179 | Esk TraC | 3040 | Humber TraC | NORTH SEA | Not Applicable | Bridlington South Beach, Wilsthorpe | Not Applicable | 1:15 | 2 | 27 | 2020 | 99.93 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01453
YWS01454 | Yorkshire Water | Live | SHAY LANE SEWAGE PUMPING STATION | SHAY LANE/CSO | WRA7660 | WRA7660 | 1 | Storm discharge at pumping station | SE3594017630 | 435940 | 417630 | GB104027062560 | Oakenshaw Beck from Source to River Calder | River | 3268 | Lower Calder | 3001 | Aire and Calder | DRAIN BECK | Not Applicable | Not Applicable | Not Applicable | 13:30 | 8 | 13.4 | 2020 | 99.91 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01454
YWS01455 | Yorkshire Water | Live | CHESTERFIELD SPITAL LANE SW PMPG ST | SPITAL LANE/CSO | WRA7662 | WRA7662 | 1 | SO on sewer network | SK3888070670 | 438882 | 370671 | GB104027057771 | Rother, Spittal Brook to Doe Lea | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | RIVER ROTHER | Not Applicable | Not Applicable | Not Applicable | 16:30 | 20 | 16.6 | 2020 | 99.63 |  |  | High spill threshold not met | High spill threshold not met | Operational investigation completed | Operational improvement completed | No SOAF investigation required | YWS01455
YWS01456 | Yorkshire Water | Live | CARR VALE NO 2 SPS | CARR VALE/NO 2 CSO | WRA7665 | WRA7665 | A1 | Storm discharge at pumping station | SK4599069680 | 445990 | 369680 | GB104027057290 | Doe Lea from Source to Hawke Brook | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | RIVER DOE LEA | Not Applicable | Not Applicable | Not Applicable | 105:45 | 39 | 35 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01456
YWS01457 | Yorkshire Water | Live | DENHOLME WHALLEY LANE SEW PMPG STN | WHALLEY LANE/CSO | WRA7667 | WRA7667 | 1 | Storm discharge at pumping station | SE0744034860 | 406810 | 434850 | GB104027062870 | Harden Beck from Source to River Aire | River | 3307 | Middle Aire | 3001 | Aire and Calder | DENHOLME BECK | Not Applicable | Not Applicable | Not Applicable | 387:15 | 85 | 87.2 | 2020 | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS01457
YWS01458 | Yorkshire Water | Live | ROYSTON (CARLTON-SHAW LANE) | CARLTON SHAW LN/CSO | WRA7675 | WRA7675 | 2 | Storm discharge at pumping station | SE3779010180 | 437790 | 410180 | GB104027063230 | Cudworth Dyke from Source to River Dearne | River | 3125 | Dearne | 3029 | Don and Rother | SHAW DYKE | Not Applicable | Not Applicable | Not Applicable | 24:45 | 11 | 7.2 | 2020 | 99.92 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01458
YWS01459 | Yorkshire Water | Live | ROTHERHAM ERSKINE ROAD SPS | GRAFTON BRIDGE/CSO | WRA7691 | WRA7691 | A2 | Storm discharge at pumping station | SK4312593717 | 443125 | 393717 | GB104027057452 | Don from River Rother to River Dearne | River | 3312 | Middle Don | 3029 | Don and Rother | RIVER DON | Not Applicable | Not Applicable | Not Applicable | 1986:00 | 133 | 72.4 | 2020 | 83.96 | Sensor failure / issue | Resolved - Aug | Data collection - Tidal / river inundation | Data collection - Tidal / river inundation | Operational investigation ongoing | Operational improvement ongoing | SOAF investigation completed - No work required | YWS01459
YWS01460 | Yorkshire Water | Live | ROTHERHAM (EFFINGHAM SQUARE) SPS | CRINOLENE HOUSE/CSO | WRA7695 | WRA7695 | 1 | SO on sewer network | SK4290093250 | 442900 | 393257 | GB104027057452 | Don from River Rother to River Dearne | River | 3312 | Middle Don | 3029 | Don and Rother | DON VIA SURFACE WATER SEWER | Not Applicable | Not Applicable | Not Applicable | 52:15 | 7 | 13.5 | 2020 | 71.93 | Sensor failure / issue | Resolved - Sep | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01460
YWS01461 | Yorkshire Water | Live | TREETON MILL LANE SEW PUMPING STN | TREETON MILL LANE/CSO | WRA7697 | WRA7697 | A2 | SO on sewer network | SK4257487801 | 442574 | 387801 | GB104027057772 | Rother, Doe Lea to Don | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | RIVER ROTHER | Not Applicable | Not Applicable | Not Applicable | 125:30 | 31 | 21.2 | 2020 | 98.73 |  |  | High spill threshold not met | High spill threshold not met | Operational investigation completed | Operational improvement completed | No SOAF investigation required | YWS01461
YWS01462 | Yorkshire Water | Live | SANDYBRIDGE LANE NO 3 SPS | SANDYBRIDGE LANE/NO 3 CSO | WRA7703 | WRA7703 | A2 | SO on sewer network | SE3876311673 | 438763 | 411673 | GB104027063230 | Cudworth Dyke from Source to River Dearne | River | 3125 | Dearne | 3029 | Don and Rother | HEMP DIKE | Not Applicable | Not Applicable | Not Applicable | 326:00 | 67 | 44.2 | 2020 | 100 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | No investigation activity in reporting period | No improvement action in reporting period | SOAF investigation completed - operational solution completed | YWS01462
YWS01463 | Yorkshire Water | Live | DROPPING WELL ROAD SPS | DROPPINGWELL ROAD/CSO | WRA7704 | WRA7704 | A1 | Storm discharge at pumping station | SK3941993814 | 439419 | 393814 | GB104027057440 | Blackburn Brook from Source to River Don | River | 3312 | Middle Don | 3029 | Don and Rother | OAKLEY BOTTOM DIKE | Not Applicable | Not Applicable | Not Applicable | 38:45 | 31 | 36.6 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01463
YWS01464 | Yorkshire Water | Live | ELDERTREE ROAD NO2 SPS | ELDERTREE ROAD/NO 2 CSO | WRA7705 | WRA7705 | A2 | SO on sewer network | SK3751995328 | 437519 | 395328 | GB104027057440 | Blackburn Brook from Source to River Don | River | 3312 | Middle Don | 3029 | Don and Rother | TRIB OF BLACKBURN BROOK | Not Applicable | Not Applicable | Not Applicable | 103:15 | 38 | 31.8 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01464
YWS01465 | Yorkshire Water | Live | HOYLE MILL LANE SPS | HOYLE MILL LANE/CSO | WRA7707 | WRA7707 | A2 | SO on sewer network | SE4226514425 | 442265 | 414425 | GB104027063320 | Hoyle Mill Stream from Source to River Went | River | 3272 | Lower Don | 3029 | Don and Rother | TRIB OF HOYLE MILL BECK | Not Applicable | Not Applicable | Not Applicable | 108:45 | 28 | 29.2 | 2020 | 99.98 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01465
YWS01466 | Yorkshire Water | Live | BRIMINGTON COMMON WESTWOOD LANE SPS | WESTWOOD LANE/CSO | WRA7709 | WRA7709 | 1 | SO on sewer network | SK4125071910 | 441260 | 371910 | GB70410054 | Chesterfield Canal (River Rother) | Canal | 2018 | Don and Rother Canals | 2001 | Humber AWB | TRIB OF TROUGH BECK | Not Applicable | Not Applicable | Not Applicable | 61:45 | 30 | 23.6 | 2020 | 99.85 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01466
YWS01467 | Yorkshire Water | Live | WEST HADDLESEY STW | WEST HADDLESEY/STW | WRA7723 | WRA7723 | 2 | Inlet SO at WwTW | SE5664026480 | 456640 | 426480 | GB104027062760 | Aire from River Calder to River Ouse | River | 3265 | Lower Aire | 3001 | Aire and Calder | RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 320:45 | 77 | 217.4 | 2020 | 100 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement ongoing | SOAF investigation ongoing | YWS01467
YWS01468 | Yorkshire Water | Live | CROSSFLATTS NO 2 SPS | CROSSFLATTS/NO 2 CSO | WRA7739 | WRA7739 | A1 | Storm discharge at pumping station | SE0997040220 | 409960 | 440210 | GB104027063034 | Aire (R Worth to Gill Beck) | River | 3307 | Middle Aire | 3001 | Aire and Calder | RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 776:30 | 64 | 35.2 | 2020 | 100 |  |  | Performance - Asset configuration (e.g. PS/rising main/storm tanks) | High spill threshold not met | UWWTR investigation ongoing, Operational investigation completed | Operational improvement completed | SOAF investigation ongoing | YWS01468
YWS01469 | Yorkshire Water | Live | JAMES STREET SPS | JAMES STREET/CSO | WRA7753 | WRA7753 | A2 | Storm discharge at pumping station | SE4295926283 | 442959 | 426283 | GB104027062760 | Aire from River Calder to River Ouse | River | 3265 | Lower Aire | 3001 | Aire and Calder | RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 7:45 | 5 | 6.4 | 2020 | 99.82 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01469
YWS01470 | Yorkshire Water | Live | SOUTHFIELD AVENUE SPS | SOUTHFIELD AVENUE/CSO | WRA7754 | WRA7754 | A1 | SO on sewer network | SE4220419124 | 442204 | 419124 | GB104027063380 | Went from Source to Hoyle Mill Stream | River | 3272 | Lower Don | 3029 | Don and Rother | WENT BECK | Not Applicable | Not Applicable | Not Applicable | 64:30 | 24 | 25 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01470
YWS01471 | Yorkshire Water | Live | CHAPEL HADDLESEY WWTW | CHAPEL HADDLESEY/STW | WRA7780 | WRA7780 | 2 | Storm tank at WwTW | SE5955025160 | 459550 | 425160 | GB104027062760 | Aire from River Calder to River Ouse | River | 3265 | Lower Aire | 3001 | Aire and Calder | RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 1310:00 | 103 | 61.4 | 2020 | 99.92 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS01471
YWS01472 | Yorkshire Water | Live | TINKER LANE SEWAGE PUMPING STN | TINKER LANE HOYLAND/CSO | WRA7784 | WRA7784 | A1 | Storm discharge at pumping station | SE3561000570 | 435610 | 400570 | GB104027057510 | Dove from Source to River Dearne | River | 3125 | Dearne | 3029 | Don and Rother | SHORT WOOD DIKE | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 5.8 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01472
YWS01473 | Yorkshire Water | Live | RAMPER LANE NO 2 SPS | RAMPER LANE/NO 2 CSO | WRA7789 | WRA7789 | A2 | Storm discharge at pumping station | SE6145009280 | 461450 | 409280 | GB104027064243 | Don from Mill Dyke to River Ouse | River | 3272 | Lower Don | 3029 | Don and Rother | TOWN END DRAIN | Not Applicable | Not Applicable | Not Applicable | 4:00 | 5 | 3 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01473
YWS01474 | Yorkshire Water | Live | FERRYBOAT LANE SEWAGE PUMPING STN | FERRYBOAT LANE/SPS | WRA7798 | WRA7798 | A2 | Storm discharge at pumping station | SK4814099332 | 448140 | 399332 | GB104027057452 | Don from River Rother to River Dearne | River | 3312 | Middle Don | 3029 | Don and Rother | UNNAMED TRIB OF RIVER DON | Not Applicable | Not Applicable | Not Applicable | 58:15 | 9 | 2.25 | 2020 | 90.3 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01474
YWS01475 | Yorkshire Water | Live | HEMSWORTH SPS (WOODLANDS) | WOODLANDS/CSO | WRA7806 | WRA7806 | 2 | Storm discharge at pumping station | SE4316013890 | 443160 | 413890 | GB104027063320 | Hoyle Mill Stream from Source to River Went | River | 3272 | Lower Don | 3029 | Don and Rother | TRIB OF HOYLE MILL DRAIN | Not Applicable | Not Applicable | Not Applicable | 2:45 | 5 | 3.8 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01475
YWS01476 | Yorkshire Water | Live | NETHERGATE SEWAGE PUMPING STN | NETHERGATE/NO 2 SPS | WRA7809 | WRA7809 | 2 | Storm discharge at pumping station | TA0595058740 | 506025 | 458749 | GB104026067090 | Nafferton Beck from Source to to Driffield Canal | River | 3492 | Upper Hull | 3039 | Hull and East Riding | NAFFERTON BECK | Not Applicable | Not Applicable | Not Applicable | 70:45 | 13 | 7 | 2020 | 98.3 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01476
YWS01477 | Yorkshire Water | Live | CRAKE WELLS CSO | CRAKE WELLS/CSO | WRA7810 | WRA7810 | A1 | SO on sewer network | TA0034337190 | 500343 | 437190 | GB104026066820 | High Hunsley to Woodmansey Area | River | 3274 | Lower Hull | 3039 | Hull and East Riding | AUTHERD DRAIN | Not Applicable | Not Applicable | Not Applicable | 47:00 | 26 | 13.6 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01477
YWS01478 | Yorkshire Water | Live | OTTRINGHAM SEWAGE TREATMENT WORKS | OTTRINGHAM/STW | WRA7811 | WRA7811 | 2 | Inlet SO at WwTW | TA2716024170 | 527160 | 424170 | GB104026066510 | Ottringham Drain from Ottringham Grange to Humber | River | 3057 | Burstwick and Eastern Drains | 3039 | Hull and East Riding | OTTRINGHAM DRAIN | Not Applicable | Not Applicable | Not Applicable | 45:15 | 8 | 15.2 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01478
YWS01479 | Yorkshire Water | Live | STIRLING CRESENT NO1 SPS | STIRLING CRES/NO 1 CSO | WRA7812 | WRA7812 | A2 | Storm discharge at pumping station | SE1968831248 | 419688 | 431248 | GB104027062830 | Low/Wortley/Pudsey Bks | River | 3265 | Lower Aire | 3001 | Aire and Calder | HOLME BECK | Not Applicable | Not Applicable | Not Applicable | 82:30 | 21 | 34.6 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01479
YWS01480 | Yorkshire Water | Live | THE POPLARS SPS | OTTRINGHAM THE POPLAR/CSO | WRA7815 | WRA7815 | 1 | SO on sewer network | TA2671023910 | 526710 | 423908 | GB104026066510 | Ottringham Drain from Ottringham Grange to Humber | River | 3057 | Burstwick and Eastern Drains | 3039 | Hull and East Riding | OTTRINGHAM DRAIN | Not Applicable | Not Applicable | Not Applicable | 137:00 | 26 | 51.4 | 2020 | 97.5 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01480
YWS01481 | Yorkshire Water | Live | GREAT HOUGHTON SEWAGE PUMPING STN | GREAT HOUGHTON/CSO | WRA7840 | WRA7840 | A2 | Storm discharge at pumping station | SE4408506077 | 444085 | 406077 | GB104027057550 | Ings/Carr/Thurnscoe Dikes from Source to Dearne | River | 3125 | Dearne | 3029 | Don and Rother | THURNSCOE DYKE | Not Applicable | Not Applicable | Not Applicable | 14:15 | 8 | 8.6 | 2020 | 86.68 | Sensor failure / issue | Resolved - Sep | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01481
YWS01482 | Yorkshire Water | Live | HORNSEA SPS | HORNSEA/CSO | WRA7863 | WRA7863 | 1 | Storm discharge at pumping station | TA2163047450 | 521630 | 447450 | GB640402491000 | Yorkshire South | Coastal Water | 3179 | Esk TraC | 3040 | Humber TraC | NORTH SEA | Not Applicable | Hornsea | Not Applicable | 67:40 | 101 | 32.6 | 2020 | 99.98 |  |  | Not asset maintenance - Hydraulic capacity | High spill threshold not met | UWWTR investigation ongoing, Operational investigation ongoing | Operational improvement ongoing | SOAF investigation ongoing | YWS01482
YWS01483 | Yorkshire Water | Live | MAPPLETON SPS | MAPPLETON/CSO | WRA7864 | WRA7864 | 1 | Storm discharge at pumping station | TA2272044040 | 522718 | 444026 | GB640402491000 | Yorkshire South | Coastal Water | 3179 | Esk TraC | 3040 | Humber TraC | NORTH SEA | Not Applicable | Not Applicable | Not Applicable | 177:36 | 64 | 61.2 | 2020 | 99.98 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement ongoing | SOAF investigation ongoing | YWS01483
YWS01484 | Yorkshire Water | Live | MIDDLECLIFFE SEWAGE PUMPING STATION | MIDDLECLIFFE/CSO | WRA7871 | WRA7871 | 1 | Storm discharge at pumping station | SE4310004710 | 443100 | 404713 | GB104027063172 | Dearne from Lundwood to River Dove | River | 3125 | Dearne | 3029 | Don and Rother | BILLINGLEY DYKE | Not Applicable | Not Applicable | Not Applicable | 33:15 | 7 | 10.6 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01484
YWS01485 | Yorkshire Water | Live | SHARLSTON (GIN LANE) SPS | SHARLSTON/CSO | WRA7888 | WRA7888 | A2 | SO on sewer network | SE4000019880 | 440002 | 419889 | GB104027063380 | Went from Source to Hoyle Mill Stream | River | 3272 | Lower Don | 3029 | Don and Rother | WENT BECK | Not Applicable | Not Applicable | Not Applicable | 74:15 | 24 | 26.2 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01485
YWS01486 | Yorkshire Water | Live | AGBRIGG GARAGE SPS | AGBRIGG GARAGE/SPS CSO | WRA7889 | WRA7889 | 1 | Storm discharge at pumping station | SE3493019240 | 439430 | 419240 | GB104027063380 | Went from Source to Hoyle Mill Stream | River | 3272 | Lower Don | 3029 | Don and Rother | OAKENSHAW BECK | Not Applicable | Not Applicable | Not Applicable | 0:15 | 1 | 0.5 | 2023 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01486
YWS01487 | Yorkshire Water | Live | LUPSET SPS | LUPSET/CSO | WRA7896 | WRA7896 | 1 | Storm discharge at pumping station | SE3072018570 | 430720 | 418570 | GB104027062631 | Calder from River Colne to River Chald | River | 3268 | Lower Calder | 3001 | Aire and Calder | LUPSET BECK | Not Applicable | Not Applicable | Not Applicable | 47:00 | 17 | 12 | 2020 | 99.98 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01487
YWS01488 | Yorkshire Water | Live | HOLME WATER END SPS | HOLME WATER END FARM/CSO | WRA7897 | WRA7897 | 1 | Storm discharge at pumping station | SE7884038150 | 478840 | 438150 | GB104026066690 | Foulness from Black Beck to Market Weighton Canal | River | 3191 | Foulness | 3039 | Hull and East Riding | UNNAMED TRIB OF RIVER FOULNESS | Not Applicable | Not Applicable | Not Applicable | 14:45 | 3 | 1 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01488
YWS01489 | Yorkshire Water | Live | WEEL STW | WEEL/STW | WRA7898 | WRA7898 | A2 | Inlet SO at WwTW | TA0673039430 | 506730 | 439430 | GB104026066950 | Holderness Drain Source to Fordyke Stream | River | 3274 | Lower Hull | 3039 | Hull and East Riding | WEEL TOWN DRAIN | Not Applicable | Not Applicable | Not Applicable | 246:30 | 26 | 17.8 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01489
YWS01490 | Yorkshire Water | Live | STOURTON SEWAGE PUMPING STATION | STOURTON/CSO | WRA7900 | WRA7900 | A2 | Storm discharge at pumping station | SE3338530236 | 433385 | 430236 | GB104027063032 | Aire from Gill Beck (Baildon) to River Calder | River | 3265 | Lower Aire | 3001 | Aire and Calder | STOURTON BECK | Not Applicable | Not Applicable | Not Applicable | 43:30 | 14 | 13.2 | 2020 | 99.97 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01490
YWS01491 | Yorkshire Water | Live | PARK ROAD SPS | PARK ROAD ELLAND/CSO | WRA7904 | WRA7904 | 1 | Storm discharge at pumping station | SE1123021790 | 411230 | 421790 | GB104027062642 | Calder from Ryburn Confluence to River Colne | River | 3310 | Middle Calder | 3001 | Aire and Calder | RIVER CALDER | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0.4 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01491
YWS01492 | Yorkshire Water | Live | SHIPTONTHORPE SPS | SHIPTONTHORPE/CSO | WRA7905 | WRA7905 | A1 | Storm discharge at pumping station | SE8523043010 | 485230 | 443010 | GB104026066720 | Foulness from Source to Black Beck (South) | River | 3191 | Foulness | 3039 | Hull and East Riding | RIVER FOULNESS OR SHIPTON BECK | Not Applicable | Not Applicable | Not Applicable | 35:45 | 11 | 6 | 2020 | 99.94 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01492
YWS01493 | Yorkshire Water | Live | DOCKFIELDS NO 2 SPS | DOCKFIELDS/CSO | WRA7906 | WRA7906 | A1 | SO on sewer network | SE1545038090 | 415452 | 438090 | GB104027063034 | Aire (R Worth to Gill Beck) | River | 3307 | Middle Aire | 3001 | Aire and Calder | RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 2:15 | 3 | 7 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01493
YWS01494 | Yorkshire Water | Live | CHERRY BURTON SPS | CANADA DRIVE/CSO | WRA7922 | WRA7922 | 1 | SO on sewer network | SE9919042320 | 499098 | 442287 | GB104026066841 | High Hunsley to Arram Area | River | 3274 | Lower Hull | 3039 | Hull and East Riding | NORTH DRAIN (CULVERTED) | Not Applicable | Not Applicable | Not Applicable | 538:30 | 33 | 19.2 | 2020 | 99.85 |  |  | High spill threshold not met | High spill threshold not met | Operational investigation completed | No improvement action in reporting period | No SOAF investigation required | YWS01494
YWS01495 | Yorkshire Water | Live | POLE MOOR SPS | POLE MOOR/CSO | WRA7925 | WRA7925 | A1 | Storm discharge at pumping station | SE0694016350 | 406940 | 416350 | GB104027062570 | Black Brook from Source to River Calder | River | 3310 | Middle Calder | 3001 | Aire and Calder | RED LANE DIKE | Not Applicable | Not Applicable | Not Applicable | 477:30 | 54 | 70.2 | 2020 | 99.96 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | No investigation activity in reporting period | No improvement action in reporting period | SOAF investigation completed - Work required | YWS01495
YWS01496 | Yorkshire Water | Live | HEY CLOUGH SPS | HEY CLOUGH/CSO | WRA7926 | WRA7926 | A2 | Storm discharge at pumping station | SE0599716361 | 405997 | 416361 | GB104027062570 | Black Brook from Source to River Calder | River | 3310 | Middle Calder | 3001 | Aire and Calder | HEY CLOUGH | Not Applicable | Not Applicable | Not Applicable | 124:15 | 22 | 29.4 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01496
YWS01497 | Yorkshire Water | Live | KIRTON LANE SPS | KIRTON LANE/CSO | WRA7929 | WRA7929 | 1 | SO on sewer network | SE6499012620 | 464997 | 412620 | GB104027064243 | Don from Mill Dyke to River Ouse | River | 3272 | Lower Don | 3029 | Don and Rother | RIVER DON (TIDAL) | Not Applicable | Not Applicable | Not Applicable | 84:15 | 30 | 36.5 | 2020 | 99.68 |  |  | High spill threshold not met | High spill threshold not met | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01497
YWS01498 | Yorkshire Water | Live | ELLERKER TODDS LANE SPS | ELLERKER TODDS LN/CSO | WRA7934 | WRA7934 | A1 | Storm discharge at pumping station | SE9201029120 | 492010 | 429120 | GB104026066660 | Mill Beck 2 (Ellerker Area) | River | 3191 | Foulness | 3039 | Hull and East Riding | UNNAMED TRIB OF ELLERKER DRAIN | Not Applicable | Not Applicable | Not Applicable | 15:45 | 6 | 1.2 | 2020 | 99.98 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01498
YWS01499 | Yorkshire Water | Live | HORBURY BRIDGE SPS | HORBURY BRIDGE/NO 2 CSO | WRA7938 | WRA7938 | 1 | SO on sewer network | SE2819017880 | 428195 | 417888 | GB104027062631 | Calder from River Colne to River Chald | River | 3268 | Lower Calder | 3001 | Aire and Calder | RIVER CALDER | Not Applicable | Not Applicable | Not Applicable | 283:00 | 78 | 53 | 2020 | 99.98 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01499
YWS01500 | Yorkshire Water | Live | SILKSTONE COMMON (MOOR END) SPS | SILKSTONE COMMON/CSO | WRA7939 | WRA7939 | 1 | Storm discharge at pumping station | SE2969004260 | 429690 | 404260 | GB104027057520 | Dodworth Dyke from Source to River Dove | River | 3125 | Dearne | 3029 | Don and Rother | HOUSE CARR DIKE | Not Applicable | Not Applicable | Not Applicable | 191:00 | 30 | 36.8 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01500
YWS01501 | Yorkshire Water | Live | CLAY HALL SPS | CLAY HALL/CSO | WRA7941 | WRA7941 | 1 | Storm discharge at pumping station | SE2866008370 | 428660 | 408370 | GB104027063150 | Cawthorne Dyke from Source to River Dearne | River | 3125 | Dearne | 3029 | Don and Rother | UNNAMED TRIB OF CAWTHORNE DIKE | Not Applicable | Not Applicable | Not Applicable | 0:15 | 1 | 6.6 | 2020 | 91.61 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | SOAF investigation completed - operational solution completed | YWS01501
YWS01502 | Yorkshire Water | Live | DELIGHT SPS | DELIGHT/CSO | WRA7943 | WRA7943 | A2 | Storm discharge at pumping station | SD9629128218 | 396291 | 428218 | GB104027062690 | Colden Water from Source to River Calder | River | 3487 | Upper Calder | 3001 | Aire and Calder | COLDEN WATER | Not Applicable | Not Applicable | Not Applicable | 643:45 | 49 | 19.6 | 2020 | 99.06 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01502
YWS01503 | Yorkshire Water | Live | EASTRINGTON SPS | EASTRINGTON/CSO | WRA7946 | WRA7946 | A1 | Storm discharge at pumping station | SE7982029780 | 479820 | 429780 | GB104026066690 | Foulness from Black Beck to Market Weighton Canal | River | 3191 | Foulness | 3039 | Hull and East Riding | LEYS DRAIN (CULVERTED) | Not Applicable | Not Applicable | Not Applicable | 186:15 | 19 | 21.6 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01503
YWS01504 | Yorkshire Water | Live | HILL VIEW ROAD NO 2 CSO | HILL VIEW ROAD/NO 2 CSO | WRA7948 | WRA7948 | A1 | SO on sewer network | SK3942473308 | 439424 | 373308 | GB104027057771 | Rother, Spittal Brook to Doe Lea | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | TRIB OF TINKER SICK | Not Applicable | Not Applicable | Not Applicable | 108:45 | 42 | 44.2 | 2020 | 100 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement ongoing | SOAF investigation ongoing | YWS01504
YWS01505 | Yorkshire Water | Live | WORKS ROAD CSO | WORKS ROAD/CSO | WRA7949 | WRA7949 | A1 | SO on sewer network | SK4155775164 | 441557 | 375164 | GB104027057771 | Rother, Spittal Brook to Doe Lea | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | RIVER ROTHER | Not Applicable | Not Applicable | Not Applicable | 52:30 | 18 | 26.6 | 2020 | 98.53 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01505
YWS01506 | Yorkshire Water | Live | MARSH STREET CSO/SPS | MARSH STREET/CSO | WRA7950 | WRA7950 | 1 | Storm discharge at pumping station | SK4235092230 | 442350 | 392230 | GB104027057413 | Don from River Don Works to River Rother | River | 3312 | Middle Don | 3029 | Don and Rother | RIVER DON | Not Applicable | Not Applicable | Not Applicable | 0:15 | 1 | 1.2 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01506
YWS01507 | Yorkshire Water | Live | HOYLAND KING STREET CSO | HOYLAND KING STREET/CSO | WRA7951 | WRA7951 | A1 | SO on sewer network | SE3829400798 | 438294 | 400798 | GB104027057470 | Knoll Beck from Source to River Dearne | River | 3125 | Dearne | 3029 | Don and Rother | TRIB OF DEARNE AND DOVE CANAL | Not Applicable | Not Applicable | Not Applicable | 24:00 | 18 | 4.2 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01507
YWS01508 | Yorkshire Water | Live | RETFORD ROAD NO 2 CSO | RETFORD ROAD/NO 2 CSO | WRA7952 | WRA7952 | A1 | SO on sewer network | SK4136785833 | 443167 | 385833 | GB104027057772 | Rother, Doe Lea to Don | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | RIVER ROTHER | Not Applicable | Not Applicable | Not Applicable | 52:30 | 36 | 40.2 | 2020 | 100 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01508
YWS01509 | Yorkshire Water | Live | MILLHOUSES STREET CSO | MILLHOUSES STREET/CSO | WRA7953 | WRA7953 | A1 | SO on sewer network | SE3769400309 | 437694 | 400309 | GB104027057470 | Knoll Beck from Source to River Dearne | River | 3125 | Dearne | 3029 | Don and Rother | TRIBUTARY OF KNOLL BECK | Not Applicable | Not Applicable | Not Applicable | 28:00 | 14 | 15.6 | 2020 | 99.95 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01509
YWS01510 | Yorkshire Water | Live | CLOUGHFIELDS ROAD NO 2 CSO | CLOUGHFIELDS/NO 2 CSO | WRA7954 | WRA7954 | A1 | SO on sewer network | SK3693099830 | 436930 | 399830 | GB104027057470 | Knoll Beck from Source to River Dearne | River | 3125 | Dearne | 3029 | Don and Rother | TRIBUTARY OF HARLEY DIKE | Not Applicable | Not Applicable | Not Applicable | 99:15 | 51 | 54.6 | 2020 | 100 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement ongoing | SOAF investigation ongoing | YWS01510
YWS01511 | Yorkshire Water | Live | ELSECAR CSO | ELSECAR/CSO | WRA7955 | WRA7955 | A1 | SO on sewer network | SE3892700362 | 438927 | 400362 | GB104027057470 | Knoll Beck from Source to River Dearne | River | 3125 | Dearne | 3029 | Don and Rother | KNOLL BECK | Not Applicable | Not Applicable | Not Applicable | 185:15 | 52 | 51 | 2020 | 100 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement ongoing | SOAF investigation ongoing | YWS01511
YWS01512 | Yorkshire Water | Live | NEW LODGE CSO | NEW LODGE/CSO | WRA7956 | WRA7956 | 1 | SO on sewer network | SE3397008410 | 433975 | 408423 | GB104027063171 | Dearne from Cawthorne Dyke to Lundwood STW | River | 3125 | Dearne | 3029 | Don and Rother | TRIBUTARY OF THE RIVER DEARNE | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 1 | 2020 | 96.66 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01512
YWS01513 | Yorkshire Water | Live | LAITHES LANE CSO | LAITHES LANE/CSO | WRA7957 | WRA7957 | 1 | SO on sewer network | SE3642009880 | 436422 | 409888 | GB104027063230 | Cudworth Dyke from Source to River Dearne | River | 3125 | Dearne | 3029 | Don and Rother | TRIB OF CUDWORTH DYKE | Not Applicable | Not Applicable | Not Applicable | 136:00 | 12 | 32.4 | 2020 | 99.15 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01513
YWS01514 | Yorkshire Water | Live | SMITHIES LANE BARNSLEY CSO | SMITHIES LN BARNSLEY/CSO | WRA7958 | WRA7958 | A1 | SO on sewer network | SE3479007990 | 434795 | 407995 | GB104027063171 | Dearne from Cawthorne Dyke to Lundwood STW | River | 3125 | Dearne | 3029 | Don and Rother | TRIBUTARY OF THE RIVER DEARNE | Not Applicable | Not Applicable | Not Applicable | 23:00 | 27 | 21.5 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01514
YWS01515 | Yorkshire Water | Live | WENTWORTH ROAD JUMP CSO | WENTWORTH ROAD JUMP/2 CSO | WRA7959 | WRA7959 | 1 | SO on sewer network | SE3825000810 | 438250 | 400810 | GB104027057470 | Knoll Beck from Source to River Dearne | River | 3125 | Dearne | 3029 | Don and Rother | JUMP VALLEY STREAM | Not Applicable | Not Applicable | Not Applicable | 11:00 | 8 | 12.4 | 2020 | 92.59 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01515
YWS01516 | Yorkshire Water | Live | SCARBOROUGH ROAD BRID 2 CSO | SCARBOROUGH RD BRID/2 CSO | WRA7960 | WRA7960 | A1 | SO on sewer network | TA1688067470 | 516880 | 467478 | GB104026072790 | Gypsey Race from Source to North Sea | River | 3214 | Gypsey Race | 3039 | Hull and East Riding | GYPSEY RACE | Not Applicable | Bridlington South Beach | Not Applicable | 5:15 | 7 | 20 | 2020 | 93.29 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01516
YWS01517 | Yorkshire Water | Live | DAMHILL NO 2 CSO | DAMHILL/NO 2 CSO | WRA7961 | WRA7961 | A1 | SO on sewer network | SE1909811091 | 419098 | 411091 | GB104027063340 | Fenay beck from Source to River Colne | River | 3097 | Colne and Holme | 3001 | Aire and Calder | SHEPLEY DIKE | Not Applicable | Not Applicable | Not Applicable | 179:00 | 42 | 48.8 | 2020 | 84.4 | Comms failure / issue | Resolved - Jan | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01517
YWS01518 | Yorkshire Water | Live | BRADLEY ROAD NO'S 1 & 2 CSO | BRADLEY ROAD/NO 3 CSO | WRA7962 | WRA7962 | 1 | SO on sewer network | SE1610020610 | 416102 | 420607 | GB70410521 | Calder and Hebble Navigation (river and canal sections) | Canal | 2007 | Calder Canals | 2001 | Humber AWB | TRIB OF HUDDERSFIELD BRD CANAL | Not Applicable | Not Applicable | Not Applicable | 15:30 | 17 | 23.8 | 2020 | 56.38 | Comms failure / issue | Scheduled | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01518
YWS01519 | Yorkshire Water | Live | BRADLEY ROAD NO'S 1 & 2 CSO | BRADLEY ROAD/NO 4 CSO | WRA7962 | WRA7962 | 2 | SO on sewer network | SE1610020610 | 416102 | 420607 | GB70410521 | Calder and Hebble Navigation (river and canal sections) | Canal | 2007 | Calder Canals | 2001 | Humber AWB | TRIB OF HUDDERSFIELD BRD CANAL | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 6.2 | 2020 | 99.98 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01519
YWS01520 | Yorkshire Water | Live | LUMB WOOD CSO | LUMB WOOD/NO 2 CSO | WRA7964 | WRA7964 | 1 | SO on sewer network | SE2286029340 | 422864 | 429348 | GB104027062830 | Low/Wortley/Pudsey Bks | River | 3265 | Lower Aire | 3001 | Aire and Calder | TRIB OF COCK BECK | Not Applicable | Not Applicable | Not Applicable | 1:30 | 3 | 4 | 2020 | 84.37 | Comms failure / issue | Resolved - Nov | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01520
YWS01521 | Yorkshire Water | Live | GELDERD ROAD CSO | GELDERD RD SCHOOL/2 CSO | WRA7965 | WRA7965 | 1 | SO on sewer network | SE2536029150 | 425369 | 429160 | GB104027062830 | Low/Wortley/Pudsey Bks | River | 3265 | Lower Aire | 3001 | Aire and Calder | TRIB OF DEAN BECK | Not Applicable | Not Applicable | Not Applicable | 0:30 | 1 | 0.2 | 2020 | 98.86 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01521
YWS01522 | Yorkshire Water | Live | ST BERNARDS MILL NO 2 CSO | ST BERNARDS MILL/NO 2 CSO | WRA7966 | WRA7966 | A1 | SO on sewer network | SE2591030035 | 425910 | 430035 | GB104027062830 | Low/Wortley/Pudsey Bks | River | 3265 | Lower Aire | 3001 | Aire and Calder | FARNLEY WOOD BECK | Not Applicable | Not Applicable | Not Applicable | 184:30 | 69 | 58.2 | 2020 | 100 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01522
YWS01523 | Yorkshire Water | Live | NORTH WINGFIELD CSO | NORTH WINGFIELD/CSO | WRA7967 | WRA7967 | A1 | SO on sewer network | SK4132465154 | 441324 | 365154 | GB104027052280 | Rother from Source to Redleadmill Brook | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | TRIBUTARY OF THE RIVER ROTHER | Not Applicable | Not Applicable | Not Applicable | 7:00 | 7 | 12.8 | 2020 | 51.09 | Sensor failure / issue | Resolved - Nov | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01523
YWS01524 | Yorkshire Water | Live | HILLCREST ROAD NO 2 CSO | HILLCREST ROAD/NO 2 CSO | WRA7969 | WRA7969 | A1 | SO on sewer network | SE1047029635 | 410470 | 429635 | GB104027062720 | Red Beck, Source to Calder and Hebble Navigation | River | 3310 | Middle Calder | 3001 | Aire and Calder | TRIB OF SHIBDEN BROOK | Not Applicable | Not Applicable | Not Applicable | 5:00 | 7 | 26 | 2020 | 35.25 | Comms failure / issue | Scheduled | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01524
YWS01525 | Yorkshire Water | Live | SPRING GARDENS CSO | SPRING GARDENS/NO 2 CSO | WRA7970 | WRA7970 | 1 | SO on sewer network | SE2268029040 | 422685 | 429044 | GB104027062830 | Low/Wortley/Pudsey Bks | River | 3265 | Lower Aire | 3001 | Aire and Calder | TRIB OF COCK BECK | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 1 | 2020 | 9.86 | Comms failure / issue | Resolved - Nov | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01525
YWS01526 | Yorkshire Water | Live | DALE FARM NO2 CSO | DALE FARM/NO 2 CSO | WRA7971 | WRA7971 | A1 | SO on sewer network | SE2299630114 | 422996 | 430114 | GB104027062830 | Low/Wortley/Pudsey Bks | River | 3265 | Lower Aire | 3001 | Aire and Calder | RINGSHAW BECK | Not Applicable | Not Applicable | Not Applicable | 258:45 | 82 | 82.6 | 2020 | 97.11 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01526
YWS01527 | Yorkshire Water | Live | DEVERON GROVE NO 2 CSO | DEVERON GROVE/NO 2 CSO | WRA7972 | WRA7972 | A1 | SO on sewer network | SE1347417774 | 413474 | 417774 | GB104027062550 | Colne from River Holme to River Calder | River | 3097 | Colne and Holme | 3001 | Aire and Calder | CLAYTON DIKE | Not Applicable | Not Applicable | Not Applicable | 5:00 | 10 | 4.6 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01527
YWS01528 | Yorkshire Water | Live | BONDGATE CSO | BONDGATE/CSO | WRA7973 | WRA7973 | A1 | SO on sewer network | SE4674822768 | 446748 | 422768 | GB104027062760 | Aire from River Calder to River Ouse | River | 3265 | Lower Aire | 3001 | Aire and Calder | WASH DIKE | Not Applicable | Not Applicable | Not Applicable | 47:30 | 28 | 38.6 | 2020 | 99.96 |  |  | High spill threshold not met | High spill threshold not met | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01528
YWS01529 | Yorkshire Water | Live | ALLERTON PARK CSO | ALLERTON PARK/CSO | WRA7974 | WRA7974 | A1 | SO on sewer network | SE3117337299 | 431173 | 437299 | GB104027062900 | Meanwood Beck from Source to River Aire | River | 3265 | Lower Aire | 3001 | Aire and Calder | GLEDHOW BECK | Not Applicable | Not Applicable | Not Applicable | 78:30 | 47 | 41.25 | 2020 | 100 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS01529
YWS01530 | Yorkshire Water | Live | ROUNDHAY 109 NO 2 CSO | ROUNDHAY 109/NO 2 CSO | WRA7975 | WRA7975 | A1 | SO on sewer network | SE3264338035 | 432643 | 438035 | GB104027062880 | Wyke Beck from Source to River Aire | River | 3265 | Lower Aire | 3001 | Aire and Calder | CULVERTED TRIB OF WYKE BECK | Not Applicable | Not Applicable | Not Applicable | 79:18 | 51 | 51.6 | 2020 | 100 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01530
YWS01531 | Yorkshire Water | Live | HARROGATE ROAD 135 CSO | HARROGATE ROAD 135/CSO | WRA7976 | WRA7976 | A1 | SO on sewer network | SE3038237910 | 430382 | 437910 | GB104027062900 | Meanwood Beck from Source to River Aire | River | 3265 | Lower Aire | 3001 | Aire and Calder | KING LANE BECK | Not Applicable | Not Applicable | Not Applicable | 226:15 | 73 | 69.8 | 2020 | 96.96 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation completed, Operational investigation completed | No improvement action in reporting period | SOAF investigation completed - No work required | YWS01531
YWS01533 | Yorkshire Water | Live | RETFORD RD RECREATION GROUND 3 CSO | RETFORD RD REC GND/2 CSO | WRA7979 | WRA7979 | A1 | SO on sewer network | SK4317585810 | 443175 | 385810 | GB104027057772 | Rother, Doe Lea to Don | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | RIVER ROTHER | Not Applicable | Not Applicable | Not Applicable | 227:45 | 61 | 58.8 | 2020 | 96.39 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS01533
YWS01534 | Yorkshire Water | Live | GLEN BRIDGE COMBINED SEWER OVERFLOW | GLEN BRIDGE/CSO | WRA7981 | WRA7981 | A1 | SO on sewer network | SK3115087828 | 431150 | 387828 | GB104027057340 | Rivelin from Source to River Loxley | River | 3490 | Upper Don | 3029 | Don and Rother | RIVER RIVELIN | Not Applicable | Not Applicable | Not Applicable | 152:34 | 50 | 21.4 | 2020 | 97.96 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01534
YWS01535 | Yorkshire Water | Live | WESTFIELDS CSO | WESTFIELDS/CSO | WRA7982 | WRA7982 | A1 | SO on sewer network | SE3539003760 | 432394 | 403762 | GB104027057520 | Dodworth Dyke from Source to River Dove | River | 3125 | Dearne | 3029 | Don and Rother | SNAPE DIKE | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0.2 | 2020 | 95.77 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01535
YWS01536 | Yorkshire Water | Live | PINFOLD LANE RECREATION CSO | PINFOLD LN RECREATION/CSO | WRA7983 | WRA7983 | A1 | SO on sewer network | SE4202004500 | 442025 | 404506 | GB104027063172 | Dearne from Lundwood to River Dove | River | 3125 | Dearne | 3029 | Don and Rother | RIVER DEARNE | Not Applicable | Not Applicable | Not Applicable | 82:15 | 45 | 53.8 | 2020 | 99.99 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | No investigation activity in reporting period | No improvement action in reporting period | SOAF investigation completed - No work required | YWS01536
YWS01537 | Yorkshire Water | Live | SPRING AVENUE CSO | SPRING AVENUE/CSO | WRA7984 | WRA7984 | A1 | SO on sewer network | SE0686041160 | 406864 | 441159 | GB104027062891 | Worth from Bridgehouse Beck to R Aire | River | 3307 | Middle Aire | 3001 | Aire and Calder | RIVER WORTH (VIA PUBLIC SEWER) | Not Applicable | Not Applicable | Not Applicable | 104:45 | 57 | 29.2 | 2020 | 99.71 |  |  | High spill threshold not met | High spill threshold not met | Operational investigation completed | No improvement action in reporting period | No SOAF investigation required | YWS01537
YWS01538 | Yorkshire Water | Live | WOODBINE COTTAGE CSO | WOODBINE COTTAGE/CSO | WRA7987 | WRA7987 | A1 | SO on sewer network | SE3443400334 | 434434 | 400334 | GB104027057480 | Rockley Dike from Source to River Dove | River | 3125 | Dearne | 3029 | Don and Rother | BIRDWELL DIKE | Not Applicable | Not Applicable | Not Applicable | 128:15 | 31 | 33 | 2020 | 97.94 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01538
YWS01539 | Yorkshire Water | Live | SPRING AVENUE CSO | LONG LEE LANE/CSO | WRA7988 | WRA7988 | 1 | SO on sewer network | SE0686041160 | 406864 | 441159 | GB104027062891 | Worth from Bridgehouse Beck to R Aire | River | 3307 | Middle Aire | 3001 | Aire and Calder | RIVER WORTH (VIA PUBLIC SEWER) | Not Applicable | Not Applicable | Not Applicable | 0:15 | 1 | 2 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01539
YWS01540 | Yorkshire Water | Live | ASHGAP LANE CSO | ASHGAP LANE/CSO | WRA7989 | WRA7989 | 1 | SO on sewer network | SE3887023490 | 438873 | 423497 | GB104027062590 | Choke Churl Bk from Source to River Calder | River | 3268 | Lower Calder | 3001 | Aire and Calder | ASHFIELD BECK | Not Applicable | Not Applicable | Not Applicable | 3:30 | 7 | 17.6 | 2020 | 99.29 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01540
YWS01541 | Yorkshire Water | Live | KING EDWARD STREET NO 2 CSO | KING EDWARD ST/NO 2 CSO | WRA7990 | WRA7990 | A1 | SO on sewer network | SE3841423088 | 438414 | 423088 | GB104027062590 | Choke Churl Bk from Source to River Calder | River | 3268 | Lower Calder | 3001 | Aire and Calder | ASHFIELD BECK | Not Applicable | Not Applicable | Not Applicable | 29:15 | 24 | 27.6 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | SOAF investigation completed - operational solution completed | YWS01541
YWS01542 | Yorkshire Water | Live | AIZLEWOOD ROAD CSO | AIZLEWOOD ROAD/NO 2 CSO | WRA7991 | WRA7991 | A1 | SO on sewer network | SK3510985131 | 435109 | 385131 | GB104027057750 | Sheaf from Source to River Don | River | 3312 | Middle Don | 3029 | Don and Rother | RIVER SHEAF | Not Applicable | Not Applicable | Not Applicable | 8:15 | 12 | 16 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01542
YWS01543 | Yorkshire Water | Live | THUNDERBRIDGE NO 2 CSO | THUNDERBRIDGE/NO 2 CSO | WRA7992 | WRA7992 | A1 | SO on sewer network | SE1880511409 | 418805 | 411409 | GB104027063340 | Fenay beck from Source to River Colne | River | 3097 | Colne and Holme | 3001 | Aire and Calder | SHEPLEY DIKE | Not Applicable | Not Applicable | Not Applicable | 15:45 | 7 | 8 | 2020 | 98.23 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01543
YWS01544 | Yorkshire Water | Live | BRANDY CARR LANE NO 2 CSO | BRANDY CARR ROAD/NO 2 CSO | WRA7993 | WRA7993 | A1 | SO on sewer network | SE3021623146 | 430216 | 423146 | GB104027062620 | Chald from Source to River Calder | River | 3268 | Lower Calder | 3001 | Aire and Calder | FOSTER FORD BECK | Not Applicable | Not Applicable | Not Applicable | 7:15 | 8 | 8.4 | 2020 | 96.67 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01544
YWS01545 | Yorkshire Water | Live | EASTBURN CSO | EASTBURN/CSO | WRA7994 | WRA7994 | A1 | SO on sewer network | SE0214045305 | 402140 | 445305 | GB104027063033 | Aire (Eshton Beck to R Worth) | River | 3484 | Upper Aire | 3001 | Aire and Calder | RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 80:30 | 21 | 21.6 | 2020 | 99.93 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01545
YWS01546 | Yorkshire Water | Live | CARR GATE BECK CSO | CARR GATE BECK/NO 2 CSO | WRA7995 | WRA7995 | 1 | SO on sewer network | SE3110024130 | 431105 | 424130 | GB104027062620 | Chald from Source to River Calder | River | 3268 | Lower Calder | 3001 | Aire and Calder | CARR GATE BECK | Not Applicable | Not Applicable | Not Applicable | 49:00 | 27 | 30.6 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01546
YWS01547 | Yorkshire Water | Live | HARDEN ROAD CSO | HARDEN ROAD/CSO | WRA7996 | WRA7996 | A1 | SO on sewer network | SE0891637219 | 408916 | 437219 | GB104027062870 | Harden Beck from Source to River Aire | River | 3307 | Middle Aire | 3001 | Aire and Calder | WILSDEN BECK | Not Applicable | Not Applicable | Not Applicable | 46:30 | 27 | 33.4 | 2020 | 99.94 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01547
YWS01548 | Yorkshire Water | Live | WALDEN DRIVE NO 2 CSO | WALDEN DRIVE/NO 2 CSO | WRA7997 | WRA7997 | A1 | SO on sewer network | SE1241135305 | 412411 | 435305 | GB104027062862 | Bradford Beck (Clayton Bk to R Aire) | River | 3307 | Middle Aire | 3001 | Aire and Calder | CLVRT TRIB OF CLIFF DIKE | Not Applicable | Not Applicable | Not Applicable | 7:30 | 10 | 10.6 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | Operational investigation completed | Operational improvement completed | No SOAF investigation required | YWS01548
YWS01549 | Yorkshire Water | Live | STALKER WALK NO 2CSO | STALKER WALK/NO 2 CSO | WRA7998 | WRA7998 | A1 | SO on sewer network | SK3415085997 | 434150 | 385997 | GB104027057760 | Porter from Source to River Sheaf | River | 3312 | Middle Don | 3029 | Don and Rother | PORTER BROOK | Not Applicable | Not Applicable | Not Applicable | 5:45 | 7 | 154.5 | 2020 | 5.23 | Sensor failure / issue | Resolved - Dec | High spill threshold not met | N/A - Ongoing investigation | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS01549
YWS01550 | Yorkshire Water | Live | WHITEHALL LANE CSO | WHITEHILL LANE/CSO | WRA7999 | WRA7999 | 1 | SO on sewer network | SK4274088850 | 442745 | 388850 | GB104027057772 | Rother, Doe Lea to Don | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | TRIBUTARY OF THE RIVER ROTHER | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 1.8 | 2020 | 99.34 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01550
YWS01551 | Yorkshire Water | Live | SHUTTLEWOOD CSO | SHUTTLEWOOD/NO 2 CSO | WRA8001 | WRA8001 | 1 | SO on sewer network | SK4708073610 | 447085 | 373618 | GB104027057320 | Hawke Brook from Source to Doe Lea | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | HAWKE BROOK | Not Applicable | Not Applicable | Not Applicable | 48:30 | 26 | 28 | 2020 | 98.52 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01551
YWS01552 | Yorkshire Water | Live | STANLEY MOOR ROAD SPS | STANLEY MOOR RD/CSO | WRA8004 | WRA8004 | 1 | Storm discharge at pumping station | SE3432024960 | 434320 | 424960 | GB104027062680 | Oulton Beck from Source to River Aire | River | 3265 | Lower Aire | 3001 | Aire and Calder | LEE MOOR BECK (VIA SW SEWER) | Not Applicable | Not Applicable | Not Applicable | 167:45 | 29 | 39.6 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01552
YWS01553 | Yorkshire Water | Live | NORTH FRODINGHAM SPS | NORTH FRODINGHAM/CSO | WRA8006 | WRA8006 | 1 | SO on sewer network | TA0950053010 | 509504 | 453015 | GB104026066990 | Mickley Dike Catchment | River | 3492 | Upper Hull | 3039 | Hull and East Riding | FRODINGHAM MILL DRAIN | Not Applicable | Not Applicable | Not Applicable | 72:30 | 30 | 37.8 | 2020 | 99.98 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01553
YWS01554 | Yorkshire Water | Live | FERRIBY HIGH ROAD SPS | FERRIBY HIGH RD/CSO | WRA8007 | WRA8007 | A2 | Storm discharge at pumping station | TA0046225542 | 500462 | 425542 | GB530402609202 | HUMBER MIDDLE | Transitional Water | 3228 | Humber Estuary TraC | 3040 | Humber TraC | RIVER HUMBER | Not Applicable | Not Applicable | Not Applicable | 112:45 | 48 | 57.6 | 2020 | 99.99 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement ongoing | SOAF investigation ongoing | YWS01554
YWS01555 | Yorkshire Water | Live | CATCH BAR CSO | CATCH BAR/CSO | WRA8022 | WRA8022 | 1 | SO on sewer network | SE2206008240 | 422064 | 408244 | GB104027063220 | Dearne from Source to Bentley Brook | River | 3125 | Dearne | 3029 | Don and Rother | RIVER DEARNE | Not Applicable | Not Applicable | Not Applicable | 13:00 | 9 | 6 | 2020 | 99.98 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01555
YWS01556 | Yorkshire Water | Live | PRIMROSE LANE CSO | PRIMROSE LANE/CSO | WRA8041 | WRA8041 | A1 | SO on sewer network | SE1230738139 | 412307 | 438139 | GB104027063034 | Aire (R Worth to Gill Beck) | River | 3307 | Middle Aire | 3001 | Aire and Calder | RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 435:10 | 94 | 78.6 | 2020 | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01556
YWS01557 | Yorkshire Water | Live | GORDON STREET CSO | GORDON STREET/CSO | WRA8055 | WRA8055 | A1 | SO on sewer network | SE1654032390 | 416540 | 432390 | GB104027062862 | Bradford Beck (Clayton Bk to R Aire) | River | 3307 | Middle Aire | 3001 | Aire and Calder | BOWLING BECK (CULVERTED) | Not Applicable | Not Applicable | Not Applicable | 20:00 | 5 | 50 | 2020 | 100 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01557
YWS01558 | Yorkshire Water | Live | LIDGETT PARK ROAD CSO | LIDGETT PARK ROAD/CSO | WRA8059 | WRA8059 | A1 | SO on sewer network | SE3253438030 | 432534 | 438030 | GB104027062880 | Wyke Beck from Source to River Aire | River | 3265 | Lower Aire | 3001 | Aire and Calder | A TRIBUTARY OF WYKE BECK | Not Applicable | Not Applicable | Not Applicable | 95:04 | 64 | 85.4 | 2020 | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement ongoing | SOAF investigation ongoing | YWS01558
YWS01559 | Yorkshire Water | Live | HOLLYM WWTW | HOLLYM/STW | WRA8060 | WRA8060 | 2 | Inlet SO at WwTW | TA3397025000 | 533970 | 425000 | Not part of a WFD catchment | Not part of a WFD catchment | River | N/A | N/A | N/A | N/A | TRIB OF WINESTEAD DRAIN | Not Applicable | Not Applicable | Not Applicable | 2163:30 | 173 | 123.4 | 2020 | 98.54 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement ongoing | SOAF investigation ongoing | YWS01559
YWS01560 | Yorkshire Water | Live | NEW INN BECK CSO | NEW INN BECK/CSO | WRA8063 | WRA8063 | 1 | SO on sewer network | SE0995032480 | 409950 | 432480 | GB104027062861 | Clayton Beck (Source to Bradford Bk) | River | 3307 | Middle Aire | 3001 | Aire and Calder | PINCH BECK | Not Applicable | Not Applicable | Not Applicable | 0:45 | 2 | 1.4 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01560
YWS01561 | Yorkshire Water | Live | STATION ROAD MICKLETOWN SPS | STATION RD MICKLETOWN/CSO | WRA8065 | WRA8065 | A1 | Storm discharge at pumping station | SE3935027370 | 439350 | 427370 | GB104027063032 | Aire from Gill Beck (Baildon) to River Calder | River | 3265 | Lower Aire | 3001 | Aire and Calder | RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 18:15 | 24 | 11.6 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01561
YWS01562 | Yorkshire Water | Live | THORTON GRAMMAR CSO | LEAVENTHORPE LANE 127/CSO | WRA8066 | WRA8066 | A1 | SO on sewer network | SE1262032838 | 412620 | 432838 | GB104027062861 | Clayton Beck (Source to Bradford Bk) | River | 3307 | Middle Aire | 3001 | Aire and Calder | CLAYTON BECK | Not Applicable | Not Applicable | Not Applicable | 0:30 | 1 | 0.2 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01562
YWS01563 | Yorkshire Water | Live | KING GEORGE CSO | KING GEORGE/CSO | WRA8072 | WRA8072 | A1 | SO on sewer network | SE0789041920 | 407890 | 441920 | GB104027063034 | Aire (R Worth to Gill Beck) | River | 3307 | Middle Aire | 3001 | Aire and Calder | RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 38:30 | 20 | 38.2 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01563
YWS01564 | Yorkshire Water | Live | NANNY MARR ROAD NO. 2 CSO | EDDERTHORPE LANE/NO 2 CSO | WRA8080 | WRA8080 | A1 | SO on sewer network | SE4178005210 | 441790 | 405213 | GB104027063172 | Dearne from Lundwood to River Dove | River | 3125 | Dearne | 3029 | Don and Rother | TRIB OF RIVER DEARNE | Not Applicable | Not Applicable | Not Applicable | 15:45 | 15 | 19 | 2020 | 91.88 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01564
YWS01565 | Yorkshire Water | Live | NANNY MARR ROAD NO. 2 CSO | NANNY MARR ROAD/NO 2 CSO | WRA8081 | WRA8081 | A1 | SO on sewer network | SE4178005210 | 441790 | 405213 | GB104027063172 | Dearne from Lundwood to River Dove | River | 3125 | Dearne | 3029 | Don and Rother | TRIB OF RIVER DEARNE | Not Applicable | Not Applicable | Not Applicable | 32:45 | 30 | 32.8 | 2020 | 99.84 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01565
YWS01566 | Yorkshire Water | Live | HIGHTOWN ROAD CSO | HIGHTOWN ROAD/NO 2 CSO | WRA8082 | WRA8082 | 1 | SO on sewer network | SE1880025090 | 418818 | 425097 | GB104027062710 | Spen Beck from Source to River Calder | River | 3268 | Lower Calder | 3001 | Aire and Calder | SYKE BECK | Not Applicable | Not Applicable | Not Applicable | 4:15 | 9 | 6.6 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01566
YWS01567 | Yorkshire Water | Live | MOUNT PELLON CSO | MOUNT PELLON/CSO | WRA8083 | WRA8083 | A1 | SO on sewer network | SE0794826134 | 407948 | 426134 | GB104027062780 | Hebble Brook from Source to River Calder | River | 3310 | Middle Calder | 3001 | Aire and Calder | HEBBLE BROOK CULVERTED | Not Applicable | Not Applicable | Not Applicable | 71:45 | 57 | 72.8 | 2020 | 98.6 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | No investigation activity in reporting period | No improvement action in reporting period | SOAF investigation completed - No work required | YWS01567
YWS01568 | Yorkshire Water | Live | WARREN LANE PUBLIC HOUSE CSO | PARKIN WOOD/NO 2 CSO | WRA8084 | WRA8084 | 1 | SO on sewer network | SK3537097670 | 435374 | 397686 | GB104027057440 | Blackburn Brook from Source to River Don | River | 3312 | Middle Don | 3029 | Don and Rother | TRIB OF BLACKBURN BROOK | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 4.8 | 2020 | 99.97 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01568
YWS01569 | Yorkshire Water | Live | BOBBINMILL LANE CSO | BOBBINMILL LANE/CSO | WRA8085 | WRA8085 | A1 | SO on sewer network | SK3654770595 | 436547 | 370595 | GB104027057660 | Hipper from Source to River Rother | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | RIVER HIPPER | Not Applicable | Not Applicable | Not Applicable | 364:00 | 70 | 69 | 2020 | 84.4 | Sensor failure / issue | Resolved - Sep | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | Operational investigation completed | Operational improvement completed | SOAF investigation completed - Work required | YWS01569
YWS01570 | Yorkshire Water | Live | CARLISLE STREET ROUNDABOUT CSO | ATLAS WORKS/CSO | WRA8086 | WRA8086 | A1 | SO on sewer network | SK3719588881 | 437195 | 388881 | GB104027057412 | Don from River Loxley confl to River Don Works | River | 3312 | Middle Don | 3029 | Don and Rother | RIVER DON | Not Applicable | Not Applicable | Not Applicable | 14:00 | 17 | 20.6 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01570
YWS01571 | Yorkshire Water | Live | CARLISLE STREET ROUNDABOUT CSO | CARLISLE STREET RND/CSO | WRA8087 | WRA8087 | A1 | SO on sewer network | SK3719588881 | 437195 | 388881 | GB104027057412 | Don from River Loxley confl to River Don Works | River | 3312 | Middle Don | 3029 | Don and Rother | RIVER DON | Not Applicable | Not Applicable | Not Applicable | 4:30 | 8 | 8.2 | 2020 | 78.24 | Sensor failure / issue | Resolved - Mar | High spill threshold not met | High spill threshold not met | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01571
YWS01572 | Yorkshire Water | Live | ROUNDHAY 110 CSO | ROUNDHAY 110/CSO | WRA8088 | WRA8088 | A1 | SO on sewer network | SE3358937179 | 433589 | 437179 | GB104027062880 | Wyke Beck from Source to River Aire | River | 3265 | Lower Aire | 3001 | Aire and Calder | WYKE BECK (CULVERTED) | Not Applicable | Not Applicable | Not Applicable | 66:00 | 43 | 16 | 2020 | 99.89 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01572
YWS01573 | Yorkshire Water | Live | ROUNDHAY PARK LANE CSO | ROUNDHAY PARK LANE/CSO | WRA8089 | WRA8089 | A1 | SO on sewer network | SE3288238714 | 432882 | 438714 | GB104027062880 | Wyke Beck from Source to River Aire | River | 3265 | Lower Aire | 3001 | Aire and Calder | TRIB OF WYKE BECK | Not Applicable | Not Applicable | Not Applicable | 54:30 | 45 | 36.4 | 2020 | 99.98 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01573
YWS01574 | Yorkshire Water | Live | BRIGGATE NO 2 CSO | BRIGGATE/NO 2 CSO | WRA8090 | WRA8090 | A1 | SO on sewer network | SE3028333192 | 430283 | 433192 | GB104027063032 | Aire from Gill Beck (Baildon) to River Calder | River | 3265 | Lower Aire | 3001 | Aire and Calder | RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 0:45 | 2 | 2.8 | 2020 | 78.68 | Comms failure / issue | Resolved - Mar | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01574
YWS01575 | Yorkshire Water | Live | ARTHUR AVENUE CSO | ARTHUR AVENUE/CSO | WRA8091 | WRA8091 | A1 | SO on sewer network | SE1316933070 | 413169 | 433070 | GB104027062861 | Clayton Beck (Source to Bradford Bk) | River | 3307 | Middle Aire | 3001 | Aire and Calder | MIDDLE BROOK | Not Applicable | Not Applicable | Not Applicable | 1:00 | 3 | 3.4 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01575
YWS01576 | Yorkshire Water | Live | CROWTHER PLACE CSO | CROWTHER PLACE/CSO | WRA8092 | WRA8092 | A1 | SO on sewer network | SE3018835418 | 430188 | 435418 | GB104027062900 | Meanwood Beck from Source to River Aire | River | 3265 | Lower Aire | 3001 | Aire and Calder | SHEEPSCAR BECK VIA SWS | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0 | 2023 | 99.86 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01576
YWS01577 | Yorkshire Water | Live | CARTMELL DRIVE CSO | CARTMELL DRIVE/CSO | WRA8095 | WRA8095 | A1 | SO on sewer network | SE3403433424 | 434034 | 433424 | GB104027062880 | Wyke Beck from Source to River Aire | River | 3265 | Lower Aire | 3001 | Aire and Calder | WYKE BECK | Not Applicable | Not Applicable | Not Applicable | 68:30 | 26 | 26.4 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01577
YWS01578 | Yorkshire Water | Live | GREEN END NO 2 CSO | GREEN END/NO 2 CSO | WRA8096 | WRA8096 | A1 | SO on sewer network | SE1198032080 | 411980 | 432080 | GB104027062861 | Clayton Beck (Source to Bradford Bk) | River | 3307 | Middle Aire | 3001 | Aire and Calder | TRIB OF CLAYTON BECK (CULVERT) | Not Applicable | Not Applicable | Not Applicable |  |  | 32.75 | 2020 | 0 | Sensor failure / issue | Resolved - January after reporting year | High spill threshold not met | High spill threshold not met | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01578
YWS01581 | Yorkshire Water | Live | ST PAULS STREET CSO | ST PAULS STREET/CSO | WRA8099 | WRA8099 | A1 | SO on sewer network | SE2975033270 | 429751 | 433275 | GB104027063032 | Aire from Gill Beck (Baildon) to River Calder | River | 3265 | Lower Aire | 3001 | Aire and Calder | RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 96:45 | 32 | 22.6 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01581
YWS01582 | Yorkshire Water | Live | CITY SQUARE CSO | CITY SQUARE/CSO | WRA8100 | WRA8100 | A1 | SO on sewer network | SE2979833338 | 429798 | 433338 | GB104027063032 | Aire from Gill Beck (Baildon) to River Calder | River | 3265 | Lower Aire | 3001 | Aire and Calder | RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 644:45 | 57 | 12 | 2020 | 65.4 | Sensor failure / issue | Resolved - Jul | High spill threshold not met | High spill threshold not met | Operational investigation ongoing | Operational improvement ongoing | No SOAF investigation required | YWS01582
YWS01583 | Yorkshire Water | Live | SOUTH GOODS YARD CSO | SOUTH GOODS YARD/CSO | WRA8101 | WRA8101 | A1 | SO on sewer network | SE0655041120 | 406550 | 441120 | GB104027062891 | Worth from Bridgehouse Beck to R Aire | River | 3307 | Middle Aire | 3001 | Aire and Calder | RIVER WORTH | Not Applicable | Not Applicable | Not Applicable | 13:00 | 18 | 20 | 2020 | 99.66 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01583
YWS01584 | Yorkshire Water | Live | PITT STREET CSO | PITT STREET/CSO | WRA8103 | WRA8103 | 1 | SO on sewer network | SE0682041140 | 406830 | 441148 | GB104027062891 | Worth from Bridgehouse Beck to R Aire | River | 3307 | Middle Aire | 3001 | Aire and Calder | RIVER WORTH | Not Applicable | Not Applicable | Not Applicable | 5:30 | 9 | 10 | 2020 | 99.97 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01584
YWS01585 | Yorkshire Water | Live | BELLE ISLE ROAD CSO | BELLE ISLE ROAD/CSO | WRA8104 | WRA8104 | A1 | SO on sewer network | SE0340637009 | 403406 | 437009 | GB104027064200 | Bridgehouse Beck from Source to River Worth | River | 3307 | Middle Aire | 3001 | Aire and Calder | BRIDGEHOUSE BECK | Not Applicable | Not Applicable | Not Applicable | 21:00 | 22 | 29.6 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01585
YWS01586 | Yorkshire Water | Live | THE WALK CSO | THE WALK/CSO | WRA8105 | WRA8105 | A1 | SO on sewer network | SE0631440811 | 406314 | 440811 | GB104027062891 | Worth from Bridgehouse Beck to R Aire | River | 3307 | Middle Aire | 3001 | Aire and Calder | RIVER WORTH | Not Applicable | Not Applicable | Not Applicable | 1:15 | 3 | 15.6 | 2020 | 99.23 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01586
YWS01587 | Yorkshire Water | Live | LITTLE HORTON LANE CSO | LITTLE HORTON LANE/2 CSO | WRA8106 | WRA8106 | 1 | SO on sewer network | SE1606032911 | 416060 | 432910 | GB104027062862 | Bradford Beck (Clayton Bk to R Aire) | River | 3307 | Middle Aire | 3001 | Aire and Calder | BRADFORD BECK | Not Applicable | Not Applicable | Not Applicable | 67:15 | 36 | 46.6 | 2020 | 97.21 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01587
YWS01588 | Yorkshire Water | Live | MORLEY STREET CSO | MORLEY STREET/CSO | WRA8107 | WRA8107 | 1 | SO on sewer network | SE1606032910 | 416060 | 432910 | GB104027062862 | Bradford Beck (Clayton Bk to R Aire) | River | 3307 | Middle Aire | 3001 | Aire and Calder | BRADFORD BECK | Not Applicable | Not Applicable | Not Applicable | 1:45 | 2 | 6.2 | 2020 | 97.05 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01588
YWS01589 | Yorkshire Water | Live | MILL LANE BRADFORD 2 CSO | MILL LANE BRADFORD/2 CSO | WRA8108 | WRA8108 | A1 | SO on sewer network | SE1652032280 | 416520 | 432280 | GB104027062862 | Bradford Beck (Clayton Bk to R Aire) | River | 3307 | Middle Aire | 3001 | Aire and Calder | BOWLING BECK (CULVERTED) | Not Applicable | Not Applicable | Not Applicable | 2:00 | 3 | 4.2 | 2020 | 79.01 | Comms failure / issue | Resolved - Oct | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01589
YWS01590 | Yorkshire Water | Live | CROSS GATES CSO | CROSS GATES/CSO | WRA8109 | WRA8109 | A1 | SO on sewer network | SE3588634350 | 435886 | 434350 | GB104027062880 | Wyke Beck from Source to River Aire | River | 3265 | Lower Aire | 3001 | Aire and Calder | TRIB OF WYKE BECK (CULVERTED) | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01590
YWS01591 | Yorkshire Water | Live | SOUTH STREET KEIGHLEY CSO | SOUTH STREET KEIGHLEY/CSO | WRA8110 | WRA8110 | A1 | SO on sewer network | SE0592040223 | 405920 | 440223 | GB104027062891 | Worth from Bridgehouse Beck to R Aire | River | 3307 | Middle Aire | 3001 | Aire and Calder | RIVER WORTH VIA KNOWLE PK SPNG | Not Applicable | Not Applicable | Not Applicable | 26:30 | 27 | 43.8 | 2020 | 99.99 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | No investigation activity in reporting period | No improvement action in reporting period | SOAF investigation completed - No work required | YWS01591
YWS01592 | Yorkshire Water | Live | PILSEY NO 2 CSO | PILSLEY/NO 2 CSO | WRA8111 | WRA8111 | A1 | SO on sewer network | SK4172562194 | 441725 | 362194 | GB104027052280 | Rother from Source to Redleadmill Brook | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | RIVER ROTHER | Not Applicable | Not Applicable | Not Applicable | 39:15 | 17 | 6 | 2020 | 86.95 | Sensor failure / issue | Resolved - January after reporting year | High spill threshold not met | High spill threshold not met | Operational investigation completed | Operational improvement completed | No SOAF investigation required | YWS01592
YWS01593 | Yorkshire Water | Live | VICKERS ROAD CSO | VICKERS ROAD/CSO | WRA8113 | WRA8113 | A1 | SO on sewer network | SK3679891178 | 436798 | 391178 | GB104027057412 | Don from River Loxley confl to River Don Works | River | 3312 | Middle Don | 3029 | Don and Rother | FIRTH PARK STREAM | Not Applicable | Not Applicable | Not Applicable | 163:15 | 71 | 67 | 2020 | 94.18 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | Operational investigation completed | No improvement action in reporting period | SOAF investigation completed - Work required | YWS01593
YWS01594 | Yorkshire Water | Live | DOLE STREET NO. 2 CSO | DOLE STREET/NO 2 CSO | WRA8123 | WRA8123 | A1 | SO on sewer network | SE1009032420 | 410090 | 432422 | GB104027062861 | Clayton Beck (Source to Bradford Bk) | River | 3307 | Middle Aire | 3001 | Aire and Calder | PINCH BECK | Not Applicable | Not Applicable | Not Applicable | 14:00 | 14 | 19.8 | 2020 | 76.58 | Comms failure / issue | Resolved - Nov | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01594
YWS01595 | Yorkshire Water | Live | ALLERTON GRANGE CSO | ALLERTON GRANGE/CSO | WRA8124 | WRA8124 | A1 | SO on sewer network | SE3104037830 | 431042 | 437830 | GB104027062900 | Meanwood Beck from Source to River Aire | River | 3265 | Lower Aire | 3001 | Aire and Calder | GLEDHOW BECK | Not Applicable | Not Applicable | Not Applicable | 20:00 | 21 | 26.8 | 2020 | 97.75 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01595
YWS01596 | Yorkshire Water | Live | MANOR DRIVE CSO | MANOR DRIVE/CSO | WRA8125 | WRA8125 | A1 | SO on sewer network | SE1201837395 | 412018 | 437395 | GB104027063034 | Aire (R Worth to Gill Beck) | River | 3307 | Middle Aire | 3001 | Aire and Calder | COTTINGLEY BECK | Not Applicable | Not Applicable | Not Applicable | 27:18 | 45 | 63.4 | 2020 | 100 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement ongoing | SOAF investigation ongoing | YWS01596
YWS01597 | Yorkshire Water | Live | MAIN STREET NO 2 CSO | MAIN ST COTTINGLEY/2 CSO | WRA8126 | WRA8126 | A1 | SO on sewer network | SE1188536954 | 411885 | 436954 | GB104027063034 | Aire (R Worth to Gill Beck) | River | 3307 | Middle Aire | 3001 | Aire and Calder | COTTINGLEY BECK | Not Applicable | Not Applicable | Not Applicable | 2:00 | 7 | 1.4 | 2020 | 99.84 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01597
YWS01598 | Yorkshire Water | Live | GILSTEAD LANE 130 2 CSO | GILSTEAD LANE 130/2 CSO | WRA8127 | WRA8127 | A1 | SO on sewer network | SE1242438930 | 412424 | 438930 | GB104027063034 | Aire (R Worth to Gill Beck) | River | 3307 | Middle Aire | 3001 | Aire and Calder | LITTLE BECK CLVRTD VIA SWS | Not Applicable | Not Applicable | Not Applicable | 12:15 | 5 | 17.8 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01598
YWS01599 | Yorkshire Water | Live | SHEARBRIDGE MILL NO. 2 CSO | SHEARBRIDGE MILL/NO 2 CSO | WRA8128 | WRA8128 | A1 | SO on sewer network | SE1531832495 | 415318 | 432495 | GB104027062862 | Bradford Beck (Clayton Bk to R Aire) | River | 3307 | Middle Aire | 3001 | Aire and Calder | DIRK HILL BECK (CULVERTED) | Not Applicable | Not Applicable | Not Applicable | 1:00 | 2 | 5.4 | 2020 | 99.56 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01599
YWS01600 | Yorkshire Water | Live | ST JOHN STREET CSO | ST JOHN STREET/CSO | WRA8129 | WRA8129 | 1 | SO on sewer network | SE0422046330 | 404220 | 446330 | GB104027062990 | Silsden Beck from Source to River Aire | River | 3484 | Upper Aire | 3001 | Aire and Calder | SILSDEN BECK | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0 | 2020 | 99.93 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01600
YWS01601 | Yorkshire Water | Live | MORTON CSO | MORTON/CSO | WRA8130 | WRA8130 | A1 | SO on sewer network | SE0916041040 | 409168 | 441045 | GB104027063034 | Aire (R Worth to Gill Beck) | River | 3307 | Middle Aire | 3001 | Aire and Calder | RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 487:15 | 111 | 108.2 | 2020 | 100 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | Operational investigation completed | No improvement action in reporting period | SOAF investigation completed - No work required | YWS01601
YWS01602 | Yorkshire Water | Live | DODGEHOLME CSO | DODGEHOLME/CSO | WRA8131 | WRA8131 | A1 | SO on sewer network | SE0661527496 | 406615 | 427496 | GB104027062780 | Hebble Brook from Source to River Calder | River | 3310 | Middle Calder | 3001 | Aire and Calder | HEBBLE BROOK | Not Applicable | Not Applicable | Not Applicable | 30:45 | 22 | 42 | 2020 | 99.99 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | No investigation activity in reporting period | No improvement action in reporting period | SOAF investigation completed - No work required | YWS01602
YWS01603 | Yorkshire Water | Live | HEBBLE LANE CSO | HEBBLE LANE/CSO | WRA8132 | WRA8132 | A1 | SO on sewer network | SE0762026310 | 407620 | 426318 | GB104027062780 | Hebble Brook from Source to River Calder | River | 3310 | Middle Calder | 3001 | Aire and Calder | HEBBLE BROOK | Not Applicable | Not Applicable | Not Applicable | 2744:15 | 178 | 145.8 | 2020 | 99.87 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | Operational investigation completed | Operational improvement ongoing | SOAF investigation completed - No work required | YWS01603
YWS01604 | Yorkshire Water | Live | GLEDHOW LANE CSO | GLEDHOW LANE/CSO | WRA8133 | WRA8133 | A1 | SO on sewer network | SE3131137146 | 431311 | 437146 | GB104027062900 | Meanwood Beck from Source to River Aire | River | 3265 | Lower Aire | 3001 | Aire and Calder | GLEDHOW BECK | Not Applicable | Not Applicable | Not Applicable | 71:00 | 37 | 51.4 | 2020 | 54.47 | Sensor failure / issue | Resolved - Oct | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement completed | SOAF investigation ongoing | YWS01604
YWS01605 | Yorkshire Water | Live | BOY LANE CSO | BOY LANE/CSO | WRA8134 | WRA8134 | A1 | SO on sewer network | SE0673927008 | 406739 | 427008 | GB104027062780 | Hebble Brook from Source to River Calder | River | 3310 | Middle Calder | 3001 | Aire and Calder | HEBBLE BROOK | Not Applicable | Not Applicable | Not Applicable | 2:15 | 6 | 1.8 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01605
YWS01606 | Yorkshire Water | Live | JUMPLES CSO | JUMPLES/CSO | WRA8135 | WRA8135 | A1 | SO on sewer network | SE0645327890 | 406453 | 427890 | GB104027062780 | Hebble Brook from Source to River Calder | River | 3310 | Middle Calder | 3001 | Aire and Calder | HEBBLE BROOK | Not Applicable | Not Applicable | Not Applicable | 89:15 | 48 | 60 | 2020 | 100 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | No investigation activity in reporting period | No improvement action in reporting period | SOAF investigation completed - No work required | YWS01606
YWS01607 | Yorkshire Water | Live | ALTOFTS CHURCH ROAD CSO | ALTOFTS CHURCH ROAD/CSO | WRA8136 | WRA8136 | A1 | SO on sewer network | SE3934024470 | 439347 | 424472 | GB104027062590 | Choke Churl Bk from Source to River Calder | River | 3268 | Lower Calder | 3001 | Aire and Calder | CHOKE CHURL BECK | Not Applicable | Not Applicable | Not Applicable | 24:00 | 19 | 74.6 | 2020 | 99.98 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS01607
YWS01608 | Yorkshire Water | Live | STATION ROAD ALTOFTS CSO | STATION ROAD ALTOFTS/CSO | WRA8137 | WRA8137 | 1 | SO on sewer network | SE3890023530 | 438574 | 423680 | GB104027062590 | Choke Churl Bk from Source to River Calder | River | 3268 | Lower Calder | 3001 | Aire and Calder | ASHFIELD BECK | Not Applicable | Not Applicable | Not Applicable | 150:30 | 48 | 37.4 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01608
YWS01609 | Yorkshire Water | Live | GARGRAVE ROAD NO 2 CSO | GARGRAVE ROAD/NO 2 CSO | WRA8138 | WRA8138 | A1 | SO on sewer network | SD9861051740 | 398610 | 451740 | GB104027063020 | Eller Beck from Haw Beck to River Aire | River | 3484 | Upper Aire | 3001 | Aire and Calder | ELLER BECK (VIA PUBLIC SEWER) | Not Applicable | Not Applicable | Not Applicable | 10:15 | 10 | 25.6 | 2020 | 99.93 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01609
YWS01610 | Yorkshire Water | Live | GILSTEAD LANE 128 CSO | GILSTEAD LANE 128/CSO | WRA8139 | WRA8139 | A1 | SO on sewer network | SE1283539264 | 412835 | 439264 | GB104027063034 | Aire (R Worth to Gill Beck) | River | 3307 | Middle Aire | 3001 | Aire and Calder | LOADPIT BECK | Not Applicable | Not Applicable | Not Applicable | 286:44 | 76 | 79.4 | 2020 | 100 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement ongoing | SOAF investigation ongoing | YWS01610
YWS01611 | Yorkshire Water | Live | ROUNDHAY MOUNT NO 2 CSO | ROUNDHAY MOUNT/NO 2 CSO | WRA8140 | WRA8140 | A1 | SO on sewer network | SE3191435892 | 431914 | 435892 | GB104027062900 | Meanwood Beck from Source to River Aire | River | 3265 | Lower Aire | 3001 | Aire and Calder | GIPTON BECK | Not Applicable | Not Applicable | Not Applicable | 8:00 | 14 | 15.8 | 2020 | 99.98 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01611
YWS01612 | Yorkshire Water | Live | HARES ROAD NO 2 CSO | HARES ROAD/NO 2 CSO | WRA8141 | WRA8141 | 1 | SO on sewer network | SE3163435633 | 431634 | 435633 | GB104027062900 | Meanwood Beck from Source to River Aire | River | 3265 | Lower Aire | 3001 | Aire and Calder | GIPTON BECK | Not Applicable | Not Applicable | Not Applicable | 83:00 | 54 | 59.4 | 2020 | 100 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01612
YWS01613 | Yorkshire Water | Live | HAREHILLS LANE NO 2 CSO | HAREHILLS LANE/NO 2 CSO | WRA8142 | WRA8142 | A1 | SO on sewer network | SE3191435890 | 431914 | 435890 | GB104027062900 | Meanwood Beck from Source to River Aire | River | 3265 | Lower Aire | 3001 | Aire and Calder | GIPTON BECK | Not Applicable | Not Applicable | Not Applicable | 56:45 | 51 | 76.4 | 2020 | 99.99 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation completed, Operational investigation completed | No improvement action in reporting period | SOAF investigation completed - No work required | YWS01613
YWS01614 | Yorkshire Water | Live | BECKFOOT LANE CSO | BECKFOOT LANE/CSO | WRA8143 | WRA8143 | A1 | SO on sewer network | SE1121638004 | 411216 | 438004 | GB104027063034 | Aire (R Worth to Gill Beck) | River | 3307 | Middle Aire | 3001 | Aire and Calder | RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 128:34 | 36 | 55.6 | 2020 | 100 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01614
YWS01615 | Yorkshire Water | Live | ATWICK NO.2 STW | ATWICK/NO 2 STW | WRA8144 | WRA8144 | 2 | Inlet SO at WwTW | TA1873050830 | 518730 | 450830 | GB104026077770 | Barmston Sea Drain / Skipsea Drain to Conf | River | 3025 | Barmston Sea Drain | 3039 | Hull and East Riding | TRIB OF STREAM DYKE | Not Applicable | Not Applicable | Not Applicable | 3493:00 | 193 | 121.75 | 2020 | 99.97 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS01615
YWS01616 | Yorkshire Water | Live | KNOSTROP CSO | KNOSTROP/COLTON CSO | WRA8145 | WRA8145 | 1 | SO on sewer network | SE3378031940 | 433783 | 431938 | GB104027062880 | Wyke Beck from Source to River Aire | River | 3265 | Lower Aire | 3001 | Aire and Calder | WYKE BECK | Not Applicable | Not Applicable | Not Applicable | 75:30 | 16 | 9.6 | 2020 | 99.95 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01616
YWS01617 | Yorkshire Water | Live | BURCROFT HILL SPS | BURCROFT HILL/CSO | WRA8153 | WRA8153 | A1 | SO on sewer network | SK5175099350 | 451751 | 399271 | GB104027064244 | Kearsley Bk | River | 3312 | Middle Don | 3029 | Don and Rother | KEARSLEY BROOK | Not Applicable | Not Applicable | Not Applicable | 51:45 | 20 | 17.2 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01617
YWS01618 | Yorkshire Water | Live | CALOW OAKS FARM CSO | CALOW OAKS FARM/NO 2 CSO | WRA8154 | WRA8154 | 1 | SO on sewer network | SK4121070800 | 441196 | 370775 | GB104027057640 | Spital/Calow/Muster Brook | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | TRIB OF CALOW BROOK | Not Applicable | Not Applicable | Not Applicable | 236:45 | 68 | 61.8 | 2020 | 96.73 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement ongoing | SOAF investigation ongoing | YWS01618
YWS01619 | Yorkshire Water | Live | STATION LANE CSO | STATION LANE W17/NO 2 CSO | WRA8155 | WRA8155 | 1 | SO on sewer network | SK3080093370 | 430795 | 393368 | GB104027057411 | Don from Little Don to River Loxley confluence | River | 3490 | Upper Don | 3029 | Don and Rother | RIVER DON | Not Applicable | Not Applicable | Not Applicable | 38:15 | 15 | 20.6 | 2020 | 99.82 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01619
YWS01620 | Yorkshire Water | Live | GREENLAND ROAD CSO | GREENLAND ROAD/CSO | WRA8156 | WRA8156 | A1 | SO on sewer network | SK3915089340 | 439158 | 389345 | GB104027057360 | Car Brook from Source to River Don | River | 3312 | Middle Don | 3029 | Don and Rother | CAR BROOK | Not Applicable | Not Applicable | Not Applicable | 31:15 | 25 | 23.2 | 2020 | 95.84 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01620
YWS01621 | Yorkshire Water | Live | CORKER BOTTOMS LANE CSO | CORKER BOTTOMS LANE/CSO | WRA8157 | WRA8157 | A1 | SO on sewer network | SK3828886959 | 438288 | 386959 | GB104027057412 | Don from River Loxley confl to River Don Works | River | 3312 | Middle Don | 3029 | Don and Rother | KIRK BRIDGE DIKE | Not Applicable | Not Applicable | Not Applicable | 94:45 | 44 | 53.6 | 2020 | 99.99 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01621
YWS01622 | Yorkshire Water | Live | GREENLAND WAY CSO | GREENLAND WAY/CSO | WRA8158 | WRA8158 | A1 | SO on sewer network | SK3940188631 | 439401 | 388631 | GB104027057360 | Car Brook from Source to River Don | River | 3312 | Middle Don | 3029 | Don and Rother | CAR BROOK | Not Applicable | Not Applicable | Not Applicable | 11:45 | 13 | 10.4 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01622
YWS01623 | Yorkshire Water | Live | HANDSWORTH ROAD NO 2 CSO | HANDSWORTH ROAD/NO 2 CSO | WRA8159 | WRA8159 | A1 | SO on sewer network | SK3999787421 | 439997 | 387421 | GB104027057360 | Car Brook from Source to River Don | River | 3312 | Middle Don | 3029 | Don and Rother | CAR BROOK | Not Applicable | Not Applicable | Not Applicable | 39:30 | 32 | 39.6 | 2020 | 97.87 |  |  | High spill threshold not met | High spill threshold not met | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01623
YWS01624 | Yorkshire Water | Live | CATCLIFFE ROAD CSO | CATCLIFFE ROAD/NO 2 CSO | WRA8160 | WRA8160 | A1 | SO on sewer network | SK3945087890 | 439457 | 387902 | GB104027057360 | Car Brook from Source to River Don | River | 3312 | Middle Don | 3029 | Don and Rother | CAR BROOK | Not Applicable | Not Applicable | Not Applicable | 354:45 | 40 | 66.8 | 2020 | 100 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01624
YWS01625 | Yorkshire Water | Live | LONGLEY HALL NO. 2 CSO | LONGLEY HALL/NO 2 CSO | WRA8161 | WRA8161 | A1 | SO on sewer network | SK3600791197 | 436007 | 391197 | GB104027057412 | Don from River Loxley confl to River Don Works | River | 3312 | Middle Don | 3029 | Don and Rother | BAGLEY DIKE | Not Applicable | Not Applicable | Not Applicable | 37:45 | 19 | 14.2 | 2020 | 99.52 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01625
YWS01626 | Yorkshire Water | Live | NORWOOD ROAD NO2 CSO | NORWOOD ROAD/NO 2 CSO | WRA8162 | WRA8162 | A1 | SO on sewer network | SK3585890336 | 435858 | 390336 | GB104027057412 | Don from River Loxley confl to River Don Works | River | 3312 | Middle Don | 3029 | Don and Rother | TRIB OF BAGLEY DIKE | Not Applicable | Not Applicable | Not Applicable | 58:45 | 29 | 39.8 | 2020 | 99.95 |  |  | High spill threshold not met | High spill threshold not met | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01626
YWS01627 | Yorkshire Water | Live | NORTHERN GENERAL HOSPITAL CSO | NORTHERN GENERAL HOSP/CSO | WRA8163 | WRA8163 | A1 | SO on sewer network | SK3647890392 | 436478 | 390392 | GB104027057412 | Don from River Loxley confl to River Don Works | River | 3312 | Middle Don | 3029 | Don and Rother | BAGLEY DIKE | Not Applicable | Not Applicable | Not Applicable | 122:15 | 43 | 47.2 | 2020 | 100 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS01627
YWS01628 | Yorkshire Water | Live | FAIRTHORN ROAD NO 2 CSO | FAIRTHORN ROAD/NO 2 CSO | WRA8164 | WRA8164 | A1 | SO on sewer network | SK3678991616 | 436789 | 391616 | GB104027057412 | Don from River Loxley confl to River Don Works | River | 3312 | Middle Don | 3029 | Don and Rother | FIRTH PARK STREAM | Not Applicable | Not Applicable | Not Applicable | 14:30 | 15 | 18.6 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01628
YWS01629 | Yorkshire Water | Live | BALLOTINI WORKS CSO | BALLOTINI WORKS/CSO | WRA8165 | WRA8165 | A1 | SO on sewer network | SE3596406126 | 435964 | 406126 | GB104027063171 | Dearne from Cawthorne Dyke to Lundwood STW | River | 3125 | Dearne | 3029 | Don and Rother | MEASBOROUGH DIKE | Not Applicable | Not Applicable | Not Applicable | 69:00 | 40 | 43.6 | 2020 | 100 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS01629
YWS01630 | Yorkshire Water | Live | SICEY AVENUE CSO | SICEY AVENUE/HLR | WRA8166 | WRA8166 | A1 | SO on sewer network | SK3662793759 | 436627 | 393759 | GB104027057440 | Blackburn Brook from Source to River Don | River | 3312 | Middle Don | 3029 | Don and Rother | HARTLEY BROOK DIKE | Not Applicable | Not Applicable | Not Applicable | 98:00 | 33 | 35 | 2020 | 99.76 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01630
YWS01631 | Yorkshire Water | Live | DEERLANDS AVENUE 178 NO 2 CSO | DEERLANDS AVE 178/2 CSO | WRA8167 | WRA8167 | A1 | SO on sewer network | SK3592292564 | 435922 | 392564 | GB104027057440 | Blackburn Brook from Source to River Don | River | 3312 | Middle Don | 3029 | Don and Rother | SHEFFIELD LANE DIKE | Not Applicable | Not Applicable | Not Applicable | 155:00 | 50 | 55.6 | 2020 | 100 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01631
YWS01632 | Yorkshire Water | Live | DEERLANDS AVENUE 177 CSO | DEERLANDS AVENUE 177/CSO | WRA8168 | WRA8168 | A1 | SO on sewer network | SK3553892511 | 435538 | 392511 | GB104027057440 | Blackburn Brook from Source to River Don | River | 3312 | Middle Don | 3029 | Don and Rother | SHEFFIELD LANE DIKE | Not Applicable | Not Applicable | Not Applicable | 4:00 | 4 | 24.8 | 2020 | 99.89 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01632
YWS01633 | Yorkshire Water | Live | STEETON CSO | STEETON/CSO | WRA8169 | WRA8169 | A1 | SO on sewer network | SE0361045030 | 416339 | 431987 | GB104027062862 | Bradford Beck (Clayton Bk to R Aire) | River | 3307 | Middle Aire | 3001 | Aire and Calder | STEETON BECK | Not Applicable | Not Applicable | Not Applicable | 121:30 | 65 | 71.8 | 2020 | 91.97 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | No investigation activity in reporting period | No improvement action in reporting period | SOAF investigation completed - No work required | YWS01633
YWS01634 | Yorkshire Water | Live | RAVENSCLIFFE AVENUE CSO | RAVENSCLIFFE AVENUE/CSO | WRA8170 | WRA8170 | A1 | SO on sewer network | SE1930035370 | 419300 | 435370 | GB104027062830 | Low/Wortley/Pudsey Bks | River | 3265 | Lower Aire | 3001 | Aire and Calder | FAGLEY BECK | Not Applicable | Not Applicable | Not Applicable | 154:45 | 47 | 48.2 | 2020 | 84.42 | Sensor failure / issue | Resolved - Oct | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement ongoing | SOAF investigation ongoing | YWS01634
YWS01635 | Yorkshire Water | Live | FEATHERSTONE NO 2 CSO | FEATHERSTONE/NO 2 CSO | WRA8171 | WRA8171 | A1 | SO on sewer network | SE4224520005 | 442245 | 420005 | GB104027063380 | Went from Source to Hoyle Mill Stream | River | 3272 | Lower Don | 3029 | Don and Rother | TRIB OF WENT BECK | Not Applicable | Not Applicable | Not Applicable | 38:45 | 24 | 30.2 | 2020 | 88.17 | Sensor failure / issue | Resolved - Sep | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01635
YWS01636 | Yorkshire Water | Live | BRACKENHILL PARK NO. 2 CSO | BRACKENHILL PARK/NO 2 CSO | WRA8172 | WRA8172 | A1 | SO on sewer network | SE1377031590 | 413769 | 431588 | GB104027062861 | Clayton Beck (Source to Bradford Bk) | River | 3307 | Middle Aire | 3001 | Aire and Calder | HORTON BECK (CULVERTED) | Not Applicable | Not Applicable | Not Applicable | 0:45 | 1 | 13.2 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01636
YWS01637 | Yorkshire Water | Live | ROSEVILLE ROAD CSO | ROSEVILLE ROAD/CSO | WRA8173 | WRA8173 | A1 | SO on sewer network | SE3092134375 | 430921 | 434375 | GB104027062900 | Meanwood Beck from Source to River Aire | River | 3265 | Lower Aire | 3001 | Aire and Calder | LADY BECK CULVERTED | Not Applicable | Not Applicable | Not Applicable | 40:45 | 23 | 29.2 | 2020 | 95.59 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01637
YWS01638 | Yorkshire Water | Live | HAREHILLS AVENUE NO 2 CSO | HAREHILLS AVENUE/NO 2 CSO | WRA8174 | WRA8174 | A1 | SO on sewer network | SE3206436085 | 432064 | 436085 | GB104027062880 | Wyke Beck from Source to River Aire | River | 3265 | Lower Aire | 3001 | Aire and Calder | GIPTON BECK | Not Applicable | Not Applicable | Not Applicable | 128:00 | 61 | 61.8 | 2020 | 100 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01638
YWS01639 | Yorkshire Water | Live | WHELDON ROAD CSO | WHELDON ROAD/CSO | WRA8175 | WRA8175 | A1 | SO on sewer network | SE4304025958 | 443040 | 425958 | GB104027062760 | Aire from River Calder to River Ouse | River | 3265 | Lower Aire | 3001 | Aire and Calder | RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 199:45 | 59 | 54.6 | 2020 | 100 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation completed | No improvement action in reporting period | SOAF investigation completed - Work required | YWS01639
YWS01640 | Yorkshire Water | Live | MELTON GREEN CSO | MELTON GREEN/CSO | WRA8176 | WRA8176 | 1 | SO on sewer network | SE4203000430 | 442036 | 400434 | GB104027057470 | Knoll Beck from Source to River Dearne | River | 3125 | Dearne | 3029 | Don and Rother | BROOK DIKE | Not Applicable | Not Applicable | Not Applicable | 6:00 | 9 | 6.4 | 2020 | 99.88 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01640
YWS01641 | Yorkshire Water | Live | MEAN BRIDGE CSO | MEAN BRIDGE/CSO | WRA8177 | WRA8177 | A1 | SO on sewer network | SE0997410819 | 409974 | 410819 | GB104027063590 | Mag Brook from Source to River Holme | River | 3097 | Colne and Holme | 3001 | Aire and Calder | MELTHAM DIKE | Not Applicable | Not Applicable | Not Applicable | 21:30 | 12 | 12.4 | 2020 | 99.8 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01641
YWS01642 | Yorkshire Water | Live | VICTORIA AVENUE NO 2 CSO | VICTORIA AVENUE/NO 2 CSO | WRA8179 | WRA8179 | A1 | SO on sewer network | SE3378031930 | 433738 | 431938 | GB104027062880 | Wyke Beck from Source to River Aire | River | 3265 | Lower Aire | 3001 | Aire and Calder | WYKE BECK | Not Applicable | Not Applicable | Not Applicable | 8:15 | 14 | 11 | 2020 | 99.9 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01642
YWS01643 | Yorkshire Water | Live | POOLE ROAD EAST CSO | POOLE ROAD EAST/CSO | WRA8180 | WRA8180 | A1 | SO on sewer network | SK3931087580 | 439298 | 387547 | GB104027057360 | Car Brook from Source to River Don | River | 3312 | Middle Don | 3029 | Don and Rother | CAR BROOK | Not Applicable | Not Applicable | Not Applicable | 44:15 | 33 | 25.2 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01643
YWS01644 | Yorkshire Water | Live | LANE END FARM CSO | LANE END FARM/CSO | WRA8182 | WRA8182 | A1 | SO on sewer network | SE1242438930 | 412424 | 438930 | GB104027063034 | Aire (R Worth to Gill Beck) | River | 3307 | Middle Aire | 3001 | Aire and Calder | LITTLE BECK (CULVERTED) | Not Applicable | Not Applicable | Not Applicable | 3:24 | 11 | 9.6 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01644
YWS01645 | Yorkshire Water | Live | WOODLANDS DONCASTER ROAD CSO | WOODLANDS DONC ROAD/CSO | WRA8183 | WRA8183 | A1 | SO on sewer network | SE5469408050 | 454694 | 408050 | GB104027057591 | Ea Beck from the Skell to River Don | River | 3272 | Lower Don | 3029 | Don and Rother | MILL DIKE | Not Applicable | Not Applicable | Not Applicable | 64:15 | 44 | 91 | 2020 | 99.99 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation completed, Operational investigation completed | Operational improvement ongoing | SOAF investigation completed - No work required | YWS01645
YWS01646 | Yorkshire Water | Live | LYME TERRACE CSO | LYME TERRACE/CSO | WRA8184 | WRA8184 | A1 | SO on sewer network | SE8240209974 | 452402 | 409974 | GB104027063200 | Ea Beck from Frickley Beck to the Skell | River | 3272 | Lower Don | 3029 | Don and Rother | OLD EA BECK | Not Applicable | Not Applicable | Not Applicable | 0:45 | 2 | 5.6 | 2020 | 99.61 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01646
YWS01647 | Yorkshire Water | Live | RETFORD ROAD ORRGREAVE NO 2 CSO | RETFORD RD ORGREAVE/2 CSO | WRA8185 | WRA8185 | A1 | SO on sewer network | SK4243386307 | 442433 | 386307 | GB104027057772 | Rother, Doe Lea to Don | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | ORGREAVE COMMON DRAIN | Not Applicable | Not Applicable | Not Applicable | 21:15 | 26 | 23.4 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01647
YWS01648 | Yorkshire Water | Live | FIRTH PARK ROAD NO 2 CSO | FIRTH PARK ROAD/NO 2 CSO | WRA8186 | WRA8186 | A1 | SO on sewer network | SK3678391359 | 436783 | 391359 | GB104027057412 | Don from River Loxley confl to River Don Works | River | 3312 | Middle Don | 3029 | Don and Rother | FIRTH PARK STREAM | Not Applicable | Not Applicable | Not Applicable | 2:30 | 6 | 15.8 | 2020 | 50.62 | Comms failure / issue | Scheduled | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01648
YWS01649 | Yorkshire Water | Live | WOODHALL ROAD NO 2 CSO | WOODHALL ROAD/NO 2 CSO | WRA8187 | WRA8187 | A1 | SO on sewer network | SE1932034850 | 419320 | 434850 | GB104027062830 | Low/Wortley/Pudsey Bks | River | 3265 | Lower Aire | 3001 | Aire and Calder | FAGLEY BECK | Not Applicable | Not Applicable | Not Applicable | 14:45 | 17 | 21.4 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01649
YWS01650 | Yorkshire Water | Live | TYERSAL LANE CSO | TYERSAL LANE/CSO | WRA8188 | WRA8188 | 1 | SO on sewer network | SE1952031560 | 419520 | 431560 | GB104027062830 | Low/Wortley/Pudsey Bks | River | 3265 | Lower Aire | 3001 | Aire and Calder | TRIB OF HOLME BECK | Not Applicable | Not Applicable | Not Applicable | 1:30 | 3 | 1.4 | 2020 | 99.88 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01650
YWS01651 | Yorkshire Water | Live | SPRINGMILL STREET 2 CSO | SPRINGMILL STREET/2 CSO | WRA8189 | WRA8189 | A1 | SO on sewer network | SE1633931987 | 416339 | 431987 | GB104027062862 | Bradford Beck (Clayton Bk to R Aire) | River | 3307 | Middle Aire | 3001 | Aire and Calder | CLVRT TRIB OF BOWLING BECK | Not Applicable | Not Applicable | Not Applicable | 5:45 | 10 | 10.6 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01651
YWS01652 | Yorkshire Water | Live | BAR LANE CSO | BAR LANE/CSO | WRA8190 | WRA8190 | A1 | SO on sewer network | SE0741042243 | 407410 | 442243 | GB104027063033 | Aire (Eshton Beck to R Worth) | River | 3484 | Upper Aire | 3001 | Aire and Calder | RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 2:30 | 8 | 21.4 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01652
YWS01653 | Yorkshire Water | Live | PELLON LANE CSO | PELLON LANE/CSO | WRA8191 | WRA8191 | A1 | SO on sewer network | SE0804825985 | 408048 | 425985 | GB104027062780 | Hebble Brook from Source to River Calder | River | 3310 | Middle Calder | 3001 | Aire and Calder | HEBBLE BROOK CULVERTED | Not Applicable | Not Applicable | Not Applicable | 1:15 | 2 | 2.2 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01653
YWS01654 | Yorkshire Water | Live | LIVINGSTONE ROAD CSO | LIVINGSTONE ROAD/CSO | WRA8194 | WRA8194 | 1 | SO on sewer network | SE1573035960 | 415730 | 435966 | GB104027062862 | Bradford Beck (Clayton Bk to R Aire) | River | 3307 | Middle Aire | 3001 | Aire and Calder | TRAP SIKE | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0.2 | 2020 | 97.67 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01654
YWS01655 | Yorkshire Water | Live | SHIRLEY ROAD CSO | SHIRLEY ROAD/CSO | WRA8195 | WRA8195 | 1 | SO on sewer network | SE1487032550 | 414872 | 432560 | GB104027062862 | Bradford Beck (Clayton Bk to R Aire) | River | 3307 | Middle Aire | 3001 | Aire and Calder | HORTON BECK | Not Applicable | Not Applicable | Not Applicable | 0:45 | 1 | 9.6 | 2020 | 9.44 | Sensor failure / issue | Resolved - Nov | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01655
YWS01656 | Yorkshire Water | Live | BRADFORD ROAD 213 CSO | BRADFORD ROAD 213/CSO | WRA8196 | WRA8196 | A1 | SO on sewer network | SE1214032270 | 412140 | 432270 | GB104027062861 | Clayton Beck (Source to Bradford Bk) | River | 3307 | Middle Aire | 3001 | Aire and Calder | CLAYTON BECK | Not Applicable | Not Applicable | Not Applicable | 10:15 | 9 | 9.67 | 2020 | 99.52 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01656
YWS01657 | Yorkshire Water | Live | LIDGET FM/LOWER LIDGET FM CSO'S | LIDGET BRIDGE/CSO | WRA8198 | WRA8198 | 1 | SO on sewer network | SE1306032060 | 413060 | 432060 | GB104027062861 | Clayton Beck (Source to Bradford Bk) | River | 3307 | Middle Aire | 3001 | Aire and Calder | BULL GREAVE BECK | Not Applicable | Not Applicable | Not Applicable | 174:15 | 22 | 31.6 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01657
YWS01658 | Yorkshire Water | Live | THEARNE GREEN CSO | THEARNE GREEN/CSO | WRA8199 | WRA8199 | 1 | SO on sewer network | SE1270031760 | 412730 | 431750 | GB104027062861 | Clayton Beck (Source to Bradford Bk) | River | 3307 | Middle Aire | 3001 | Aire and Calder | BULL GREAVE BECK | Not Applicable | Not Applicable | Not Applicable | 116:15 | 54 | 60.4 | 2020 | 99.73 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01658
YWS01659 | Yorkshire Water | Live | PASTURE LANE NO 2 CSO | PASTURE LANE/NO 2 CSO | WRA8200 | WRA8200 | A1 | SO on sewer network | SE1290531821 | 412905 | 431821 | GB104027062861 | Clayton Beck (Source to Bradford Bk) | River | 3307 | Middle Aire | 3001 | Aire and Calder | BULL GREAVE BECK (CULVERTED) | Not Applicable | Not Applicable | Not Applicable | 88:30 | 52 | 65.8 | 2020 | 96.39 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01659
YWS01660 | Yorkshire Water | Live | ALLERTON ROAD CSO | ALLERTON ROAD/CSO | WRA8201 | WRA8201 | A1 | SO on sewer network | SE1269034280 | 412690 | 434280 | GB104027062861 | Clayton Beck (Source to Bradford Bk) | River | 3307 | Middle Aire | 3001 | Aire and Calder | CHELLOW DEAN BECK | Not Applicable | Not Applicable | Not Applicable | 36:15 | 32 | 19.4 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01660
YWS01661 | Yorkshire Water | Live | BOWDEN HOWSTEAD NO 2 CSO | BOWDEN HOWSTEADS/NO 2 CSO | WRA8202 | WRA8202 | A1 | SO on sewer network | SK3951087060 | 439510 | 387060 | GB104027057360 | Car Brook from Source to River Don | River | 3312 | Middle Don | 3029 | Don and Rother | CAR BROOK | Not Applicable | Not Applicable | Not Applicable | 1:30 | 5 | 18 | 2020 | 85.66 | Comms failure / issue | Resolved - Dec | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01661
YWS01662 | Yorkshire Water | Live | CUT ROAD NO.2 CSO | CUT ROAD/NO 2 CSO | WRA8203 | WRA8203 | A1 | SO on sewer network | SE4678227204 | 446782 | 427204 | GB104027062760 | Aire from River Calder to River Ouse | River | 3265 | Lower Aire | 3001 | Aire and Calder | RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 26:15 | 26 | 24.6 | 2020 | 95.9 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01662
YWS01663 | Yorkshire Water | Live | EASTGATE LEEDS NO 2 CSO | EASTGATE LEEDS/NO 2 CSO | WRA8204 | WRA8204 | A1 | SO on sewer network | SE3088133093 | 430881 | 433093 | GB104027063032 | Aire from Gill Beck (Baildon) to River Calder | River | 3265 | Lower Aire | 3001 | Aire and Calder | LADY BECK | Not Applicable | Not Applicable | Not Applicable | 118:45 | 6 | 1.6 | 2020 | 91.42 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01663
YWS01664 | Yorkshire Water | Live | OWSTON ROAD CSO | OWSTON ROAD/CSO | WRA8205 | WRA8205 | A1 | SO on sewer network | SE5460010020 | 454604 | 410025 | GB104027057591 | Ea Beck from the Skell to River Don | River | 3272 | Lower Don | 3029 | Don and Rother | WELLSYKE DRAIN | Not Applicable | Not Applicable | Not Applicable | 2:15 | 2 | 3 | 2020 | 88.67 | Sensor failure / issue | Resolved - Jul | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01664
YWS01665 | Yorkshire Water | Live | SYKE ING NO 2 CSO | SYKE ING/NO 2 CSO | WRA8206 | WRA8206 | A1 | SO on sewer network | SE2615621346 | 426156 | 421346 | GB104027062631 | Calder from River Colne to River Chald | River | 3268 | Lower Calder | 3001 | Aire and Calder | CHICKENLEY BECK | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0 | 2020 | 95.95 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01665
YWS01666 | Yorkshire Water | Live | THURLESTONE NO 2 CSO | THURLSTONE ROAD/NO 2 CSO | WRA8207 | WRA8207 | 1 | SO on sewer network | SE2362003520 | 423621 | 403516 | GB104027057500 | Don from Source to Scout Dyke | River | 3490 | Upper Don | 3029 | Don and Rother | RIVE DON | Not Applicable | Not Applicable | Not Applicable | 26:00 | 14 | 16 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01666
YWS01667 | Yorkshire Water | Live | HECKMONDWIKE NO 2 CSO | HECKMONDWIKE/NO 2 CSO | WRA8208 | WRA8208 | A1 | SO on sewer network | SE2206622513 | 422066 | 422513 | GB104027062710 | Spen Beck from Source to River Calder | River | 3268 | Lower Calder | 3001 | Aire and Calder | RIVER SPEN | Not Applicable | Not Applicable | Not Applicable | 243:00 | 28 | 46.6 | 2020 | 100 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | No investigation activity in reporting period | No improvement action in reporting period | SOAF investigation completed - No work required | YWS01667
YWS01668 | Yorkshire Water | Live | HIGH STREET HECKMONDWIKE NO 2 CSO | HIGH ST HECKMONDWIK/2 CSO | WRA8209 | WRA8209 | A1 | SO on sewer network | SE2176923569 | 421769 | 423569 | GB104027062710 | Spen Beck from Source to River Calder | River | 3268 | Lower Calder | 3001 | Aire and Calder | CULVERTED TRIB OF SPEN RIVER | Not Applicable | Not Applicable | Not Applicable | 35:00 | 32 | 40 | 2020 | 99.98 |  |  | High spill threshold not met | High spill threshold not met | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01668
YWS01669 | Yorkshire Water | Live | APPERLEY ROAD PUBLIC SEWER | APPERLEY ROAD XXX/CSO | WRA8210 | WRA8210 | 2 | SO on sewer network | SE1927038170 | 419277 | 438175 | GB104027063032 | Aire from Gill Beck (Baildon) to River Calder | River | 3265 | Lower Aire | 3001 | Aire and Calder | RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 0:30 | 2 | 1.4 | 2020 | 99.73 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01669
YWS01670 | Yorkshire Water | Live | APPERLEY ROAD PUBLIC SEWER | APPERLEY ROAD 292/CSO | WRA8210 | WRA8210 | 3 | SO on sewer network | SE1927038170 | 419277 | 438175 | GB104027063032 | Aire from Gill Beck (Baildon) to River Calder | River | 3265 | Lower Aire | 3001 | Aire and Calder | RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 310:00 | 104 | 87 | 2023 | 99.76 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS01670
YWS01671 | Yorkshire Water | Live | APPERLEY ROAD PUBLIC SEWER | APPERLEY ROAD 294/CSO | WRA8210 | WRA8210 | 4 | SO on sewer network | SE1927038170 | 419277 | 438175 | GB104027063032 | Aire from Gill Beck (Baildon) to River Calder | River | 3265 | Lower Aire | 3001 | Aire and Calder | RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0 | 2020 | 99.81 |  |  | High spill threshold not met | High spill threshold not met | Operational investigation ongoing | No improvement action in reporting period | No SOAF investigation required | YWS01671
YWS01672 | Yorkshire Water | Live | RAWMARSH NO 2 CSO | RAWMARSH/NO 2 CSO | WRA8211 | WRA8211 | 1 | SO on sewer network | SK4514096440 | 445147 | 396447 | GB104027057452 | Don from River Rother to River Dearne | River | 3312 | Middle Don | 3029 | Don and Rother | ROUNDWOOD BROOK | Not Applicable | Not Applicable | Not Applicable | 91:30 | 16 | 22.2 | 2020 | 99.95 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01672
YWS01673 | Yorkshire Water | Live | PRINCE OF WALES ROAD 2 CSO | PRINCE OF WALES RD/2 CSO | WRA8212 | WRA8212 | A1 | SO on sewer network | SK3931087320 | 439310 | 387310 | GB104027057360 | Car Brook from Source to River Don | River | 3312 | Middle Don | 3029 | Don and Rother | CAR BROOK | Not Applicable | Not Applicable | Not Applicable | 5:15 | 14 | 21.8 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01673
YWS01674 | Yorkshire Water | Live | NORTH BROOK STREET NO 1 CSO | NORTH BROOK ST/NO 1 CSO | WRA8213 | WRA8213 | A1 | SO on sewer network | SE1653033650 | 416526 | 433651 | GB104027062862 | Bradford Beck (Clayton Bk to R Aire) | River | 3307 | Middle Aire | 3001 | Aire and Calder | BRADFORD BECK (CULVERTED) | Not Applicable | Not Applicable | Not Applicable | 83:30 | 51 | 56.6 | 2020 | 89.79 | Sensor failure / issue | Resolved - Jun | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01674
YWS01675 | Yorkshire Water | Live | NORTH BROOK STREET NO 1 CSO | NORTH BROOK ST/NO 2 CSO | WRA8213 | EPR/RB3790DD | A1 | SO on sewer network | SE1653033650 | 416526 | 433651 | GB104027062862 | Bradford Beck (Clayton Bk to R Aire) | River | 3307 | Middle Aire | 3001 | Aire and Calder | BRADFORD BECK (CULVERTED) | Not Applicable | Not Applicable | Not Applicable | 1:30 | 4 | 1.4 | 2020 | 99.74 |  |  | High spill threshold not met | High spill threshold not met | Operational investigation ongoing | No improvement action in reporting period | No SOAF investigation required | YWS01675
YWS01676 | Yorkshire Water | Live | RAIKES LANE CSO | RAIKESWOOD DRIVE/CSO | WRA8214 | WRA8214 | 1 | SO on sewer network | SE1921029320 | 419213 | 429327 | GB104027062710 | Spen Beck from Source to River Calder | River | 3268 | Lower Calder | 3001 | Aire and Calder | HIGH ROYDS BECK | Not Applicable | Not Applicable | Not Applicable | 8:45 | 12 | 12.6 | 2020 | 98.69 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01676
YWS01677 | Yorkshire Water | Live | HAMMERTON ST/LEEDS RD/HARRIS ST CSO | GEORGE ST BRADFORD/SCC | WRA8215 | WRA8215 | 1 | SO on sewer network | SE1685032920 | 416845 | 432917 | GB104027062862 | Bradford Beck (Clayton Bk to R Aire) | River | 3307 | Middle Aire | 3001 | Aire and Calder | EAST BROOK (CULVERTED) | Not Applicable | Not Applicable | Not Applicable | 44:00 | 16 | 14.4 | 2020 | 99.49 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01677
YWS01678 | Yorkshire Water | Live | HAMMERTON STREET 256 NO 2 CSO | HAMMERTON ST 256/2 CSO | WRA8217 | WRA8217 | 1 | SO on sewer network | SE1719332828 | 417193 | 432828 | GB104027062862 | Bradford Beck (Clayton Bk to R Aire) | River | 3307 | Middle Aire | 3001 | Aire and Calder | EAST BROOK (CULVERTED) | Not Applicable | Not Applicable | Not Applicable | 5:30 | 6 | 6.5 | 2021 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01678
YWS01679 | Yorkshire Water | Live | PRINCE OF WALES PUBLIC SEWER | PIPWORTH ROAD/CSO | WRA8224 | WRA8224 | 10 | SO on sewer network | SK3931087310 | 439310 | 387310 | GB104027057360 | Car Brook from Source to River Don | River | 3312 | Middle Don | 3029 | Don and Rother | CAR BROOK (VIA PUBLIC SEWER) | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 1.2 | 2020 | 99.95 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01679
YWS01680 | Yorkshire Water | Live | PRINCE OF WALES PUBLIC SEWER | HARBOROUGH AVENUE/CSO | EPR/RB3254TX | EPR/RB3254TX | A1 | SO on sewer network | SK3931087310 | 439310 | 387310 | GB104027057360 | Car Brook from Source to River Don | River | 3312 | Middle Don | 3029 | Don and Rother | CAR BROOK (VIA PUBLIC SEWER) | Not Applicable | Not Applicable | Not Applicable | 0:30 | 2 | 7.2 | 2020 | 99.69 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01680
YWS01681 | Yorkshire Water | Live | PRINCE OF WALES PUBLIC SEWER | HASTILAR ROAD/CSO | EPR/RB3352TM | EPR/RB3352TM | A1 | SO on sewer network | SK3931087310 | 439310 | 387310 | GB104027057360 | Car Brook from Source to River Don | River | 3312 | Middle Don | 3029 | Don and Rother | CAR BROOK (VIA PUBLIC SEWER) | Not Applicable | Not Applicable | Not Applicable | 8:15 | 10 | 16.8 | 2020 | 99.78 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01681
YWS01682 | Yorkshire Water | Live | PRINCE OF WALES PUBLIC SEWER | BEAUMONT ROAD/CSO | EPR/RB3354TK | EPR/RB3354TK | A1 | SO on sewer network | SK3931087310 | 439310 | 387310 | GB104027057360 | Car Brook from Source to River Don | River | 3312 | Middle Don | 3029 | Don and Rother | CAR BROOK (VIA PUBLIC SEWER) | Not Applicable | Not Applicable | Not Applicable | 9:30 | 11 | 14.2 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01682
YWS01683 | Yorkshire Water | Live | PRINCE OF WALES PUBLIC SEWER | RAVENCARR ROAD/CSO | EPR/RB3791NK | EPR/RB3791NK | A1 | SO on sewer network | SK3931087310 | 439310 | 387310 | GB104027057360 | Car Brook from Source to River Don | River | 3312 | Middle Don | 3029 | Don and Rother | CAR BROOK (VIA PUBLIC SEWER) | Not Applicable | Not Applicable | Not Applicable | 61:00 | 30 | 26.4 | 2020 | 99.76 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01683
YWS01684 | Yorkshire Water | Live | PRINCE OF WALES PUBLIC SEWER | FAIRLEIGH/CSO | WRA8224 | WRA8224 | 6 | SO on sewer network | SK3931087310 | 439310 | 387310 | GB104027057360 | Car Brook from Source to River Don | River | 3312 | Middle Don | 3029 | Don and Rother | CAR BROOK (VIA PUBLIC SEWER) | Not Applicable | Not Applicable | Not Applicable | 5:30 | 9 | 10.8 | 2020 | 99.76 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01684
YWS01685 | Yorkshire Water | Live | PRINCE OF WALES PUBLIC SEWER | HALSALL AVENUE/CSO | WRA8224 | WRA8224 | 7 | SO on sewer network | SK3931087310 | 439310 | 387310 | GB104027057360 | Car Brook from Source to River Don | River | 3312 | Middle Don | 3029 | Don and Rother | CAR BROOK (VIA PUBLIC SEWER) | Not Applicable | Not Applicable | Not Applicable | 88:30 | 44 | 55.4 | 2020 | 99.8 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01685
YWS01686 | Yorkshire Water | Live | PRINCE OF WALES PUBLIC SEWER | QUEEN MARY ROAD/CSO | EPR/RB3452TX | EPR/RB3452TX | A1 | SO on sewer network | SK3931087310 | 439310 | 387310 | GB104027057360 | Car Brook from Source to River Don | River | 3312 | Middle Don | 3029 | Don and Rother | CAR BROOK (VIA PUBLIC SEWER) | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0.8 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01686
YWS01687 | Yorkshire Water | Live | PRINCE OF WALES PUBLIC SEWER | FITZHUBERT ROAD/CSO | EPR/RB3454TH | EPR/RB3454TH | A1 | SO on sewer network | SK3931087310 | 439310 | 387310 | GB104027057360 | Car Brook from Source to River Don | River | 3312 | Middle Don | 3029 | Don and Rother | CAR BROOK (VIA PUBLIC SEWER) | Not Applicable | Not Applicable | Not Applicable | 0:15 | 1 | 8.4 | 2020 | 93.58 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01687
YWS01688 | Yorkshire Water | Live | COMBS HILL NO 2 CSO | COMBS HILL/NO 2 CSO | WRA8228 | WRA8228 | A1 | SO on sewer network | SE2517019090 | 425174 | 419096 | GB70410521 | Calder and Hebble Navigation (river and canal sections) | Canal | 2007 | Calder Canals | 2001 | Humber AWB | TRIB OF CALDER & HEBBLE NAV. | Not Applicable | Not Applicable | Not Applicable | 27:30 | 28 | 19.6 | 2020 | 99.5 |  |  | High spill threshold not met | High spill threshold not met | UWWTR investigation ongoing, Operational investigation completed | Operational improvement ongoing | SOAF investigation ongoing | YWS01688
YWS01689 | Yorkshire Water | Live | HECK CEMETERY ROAD NO 2 CSO | HECK CEMETERY ROAD/2 CSO | WRA8229 | WRA8229 | A1 | SO on sewer network | SE2176923571 | 421769 | 423571 | GB104027062710 | Spen Beck from Source to River Calder | River | 3268 | Lower Calder | 3001 | Aire and Calder | UNNA. CUL. TRIB. OF SPEN RIVER | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0.6 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01689
YWS01690 | Yorkshire Water | Live | BATLEY ROAD NO 2 CSO | BATLEY ROAD/NO 2 CSO | WRA8230 | WRA8230 | A1 | SO on sewer network | SE2181523586 | 421815 | 423586 | GB104027062710 | Spen Beck from Source to River Calder | River | 3268 | Lower Calder | 3001 | Aire and Calder | TRIBUTARY OF RIVER SPEN | Not Applicable | Not Applicable | Not Applicable | 0:45 | 1 | 1.4 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01690
YWS01691 | Yorkshire Water | Live | GREEN LANE 206 CSO | GREEN LANE 206/CSO | WRA8231 | WRA8231 | 1 | SO on sewer network | SE1028032370 | 410275 | 432376 | GB104027062861 | Clayton Beck (Source to Bradford Bk) | River | 3307 | Middle Aire | 3001 | Aire and Calder | PINCH BECK | Not Applicable | Not Applicable | Not Applicable | 196:30 | 14 | 13.6 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01691
YWS01692 | Yorkshire Water | Live | CANAL ROAD 331 CSO | CANAL ROAD 331/CSO | WRA8232 | WRA8232 | 1 | SO on sewer network | SE1576035410 | 415763 | 435411 | GB104027062862 | Bradford Beck (Clayton Bk to R Aire) | River | 3307 | Middle Aire | 3001 | Aire and Calder | BRADFORD BECK | Not Applicable | Not Applicable | Not Applicable | 31:00 | 19 | 20.6 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01692
YWS01693 | Yorkshire Water | Live | HIGHFIELD LANE ORGREAVE SPS | HIGHFIELD LN ORGREAVE/CSO | WRA8237 | WRA8237 | 1 | SO on sewer network | SK4167086970 | 441700 | 386958 | GB104027057772 | Rother, Doe Lea to Don | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | HANDSWORTH BECK | Not Applicable | Not Applicable | Not Applicable | 5:15 | 3 | 3.6 | 2020 | 99.96 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01693
YWS01694 | Yorkshire Water | Live | SKEFFLING WWTW | SKEFFLING/STW | WRA8238 | WRA8238 | 2 | Inlet SO at WwTW | TA3720019160 | 537200 | 419160 | Not part of a WFD catchment | Not part of a WFD catchment | River | N/A | N/A | N/A | N/A | TRIB OF SKEFFLING CLOUGH DRAIN | Not Applicable | Not Applicable | Not Applicable | 1647:00 | 99 | 106.8 | 2020 | 100 |  |  | Performance - Infiltration | Performance - Infiltration | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS01694
YWS01695 | Yorkshire Water | Live | WORRY GOOSE LANE CSO AT SPS | WORRY GOOSE LANE/CSO | WRA8239 | WRA8239 | A1 | SO on sewer network | SK4600890178 | 446008 | 390178 | GB104027057772 | Rother, Doe Lea to Don | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | TRIB WHISTON BROOK VIA PUB SWR | Not Applicable | Not Applicable | Not Applicable | 56:45 | 22 | 28.8 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01695
YWS01696 | Yorkshire Water | Live | BOWER GRN/CHESTNUT ST/MYRTLE ST/ | MULGRAVE ST 258/CSO | WRA8241 | WRA8241 | 1 | SO on sewer network | SE1734032810 | 417347 | 432817 | GB104027062862 | Bradford Beck (Clayton Bk to R Aire) | River | 3307 | Middle Aire | 3001 | Aire and Calder | EAST BROOK (CULVERTED) | Not Applicable | Not Applicable | Not Applicable | 3:00 | 5 | 2.8 | 2020 | 99.82 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01696
YWS01697 | Yorkshire Water | Live | BOWER GRN/CHESTNUT ST/MYRTLE ST/ | CHESTNUT STREET/CSO | WRA8241 | EPR/AP3620PH | A1 | SO on sewer network | SE1734032810 | 417347 | 432817 | GB104027062862 | Bradford Beck (Clayton Bk to R Aire) | River | 3307 | Middle Aire | 3001 | Aire and Calder | EAST BROOK (CULVERTED) | Not Applicable | Not Applicable | Not Applicable | 7:00 | 8 | 36 | 2020 | 21.64 | Comms failure / issue | Scheduled | High spill threshold not met | High spill threshold not met | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01697
YWS01698 | Yorkshire Water | Live | BOWER GRN/CHESTNUT ST/MYRTLE ST/ | BOWER GREEN/CSO | WRA8241 | EPR/AP3720PC | A1 | SO on sewer network | SE1734032810 | 417347 | 432817 | GB104027062862 | Bradford Beck (Clayton Bk to R Aire) | River | 3307 | Middle Aire | 3001 | Aire and Calder | EAST BROOK (CULVERTED) | Not Applicable | Not Applicable | Not Applicable | 182:30 | 40 | 82.2 | 2020 | 59.12 | Sensor failure / issue | Resolved - Aug | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement ongoing | SOAF investigation ongoing | YWS01698
YWS01699 | Yorkshire Water | Live | BOWER GRN/CHESTNUT ST/MYRTLE ST/ | MYRTLE STREET/CSO | WRA8241 | WRA8241 | 4 | SO on sewer network | SE1734032810 | 417347 | 432817 | GB104027062862 | Bradford Beck (Clayton Bk to R Aire) | River | 3307 | Middle Aire | 3001 | Aire and Calder | EAST BROOK (CULVERTED) | Not Applicable | Not Applicable | Not Applicable | 143:15 | 75 | 116.8 | 2020 | 99.73 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS01699
YWS01700 | Yorkshire Water | Live | CARR HILL ROAD CSO | CARR HILL ROAD/CSO | WRA8243 | WRA8243 | A1 | SO on sewer network | SE1784028320 | 417851 | 428330 | GB104027062710 | Spen Beck from Source to River Calder | River | 3268 | Lower Calder | 3001 | Aire and Calder | HIGH ROYDS BECK | Not Applicable | Not Applicable | Not Applicable | 131:45 | 47 | 53.2 | 2020 | 84.73 | Sensor failure / issue | Resolved - Jul | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01700
YWS01701 | Yorkshire Water | Live | NEW STREET CSO | NEW STREET/CSO | WRA8244 | WRA8244 | 1 | SO on sewer network | SE1769028060 | 417690 | 428060 | GB104027062710 | Spen Beck from Source to River Calder | River | 3268 | Lower Calder | 3001 | Aire and Calder | HIGH ROYDS BECK | Not Applicable | Not Applicable | Not Applicable | 0:15 | 1 | 16 | 2020 | 98.01 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01701
YWS01702 | Yorkshire Water | Live | SHETCLIFFE LANE NO 2 CSO | SHETCLIFFE LANE/NO 2 CSO | WRA8245 | WRA8245 | A1 | SO on sewer network | SE1845029710 | 418451 | 429709 | GB104027062710 | Spen Beck from Source to River Calder | River | 3268 | Lower Calder | 3001 | Aire and Calder | HIGH ROYDS BECK | Not Applicable | Not Applicable | Not Applicable | 72:15 | 31 | 28 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01702
YWS01703 | Yorkshire Water | Live | CLIFF HOLLINS LANE CSO | CLIFF HOLLINS LANE/CSO | WRA8246 | WRA8246 | A1 | SO on sewer network | SE1816628814 | 418166 | 428814 | GB104027062710 | Spen Beck from Source to River Calder | River | 3268 | Lower Calder | 3001 | Aire and Calder | HIGHROYDS BECK | Not Applicable | Not Applicable | Not Applicable | 0:15 | 1 | 3.2 | 2020 | 89.09 | Comms failure / issue | Resolved - Aug | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01703
YWS01704 | Yorkshire Water | Live | EDGE END LANE CSO | EDGE END LANE/NO 2 CSO | WRA8247 | WRA8247 | 1 | SO on sewer network | SE1308029300 | 413080 | 429300 | GB104027062700 | Clifton Beck from Source to River Calder | River | 3310 | Middle Calder | 3001 | Aire and Calder | BLACKSHAW BECK | Not Applicable | Not Applicable | Not Applicable | 44:00 | 36 | 89 | 2020 | 98.76 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS01704
YWS01705 | Yorkshire Water | Live | MOUNT STREET NO 2 CSO | MOUNT STREET/NO 2 CSO | WRA8248 | WRA8248 | A1 | SO on sewer network | SE1734032810 | 417347 | 432817 | GB104027062862 | Bradford Beck (Clayton Bk to R Aire) | River | 3307 | Middle Aire | 3001 | Aire and Calder | EAST BROOK (CULVERTED) | Not Applicable | Not Applicable | Not Applicable | 35:30 | 24 | 26.2 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01705
YWS01706 | Yorkshire Water | Live | MULGRAVE STREET 259 CSO | MOUNT STREET/NO 3 CSO | WRA8249 | WRA8249 | 1 | SO on sewer network | SE1734032810 | 417347 | 432817 | GB104027062862 | Bradford Beck (Clayton Bk to R Aire) | River | 3307 | Middle Aire | 3001 | Aire and Calder | EAST BROOK (CULVERTED) | Not Applicable | Not Applicable | Not Applicable | 1:15 | 1 | 9.2 | 2020 | 9.69 | Comms failure / issue | Resolved - Aug | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01706
YWS01707 | Yorkshire Water | Live | CROSS SUN STREET CSO | CROSS SUN STREET/CSO | WRA8250 | WRA8250 | 1 | SO on sewer network | SE1664233580 | 416642 | 433580 | GB104027062862 | Bradford Beck (Clayton Bk to R Aire) | River | 3307 | Middle Aire | 3001 | Aire and Calder | BRADFORD BECK (CULVERTED) | Not Applicable | Not Applicable | Not Applicable | 5:45 | 9 | 9.8 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01707
YWS01708 | Yorkshire Water | Live | CUTLER HEIGHTS CSO | CUTLER HEIGHTS/CSO | WRA8251 | WRA8251 | A1 | SO on sewer network | SE1937031174 | 419370 | 431174 | GB104027062830 | Low/Wortley/Pudsey Bks | River | 3265 | Lower Aire | 3001 | Aire and Calder | HOLME BECK (CULVERTED) | Not Applicable | Not Applicable | Not Applicable | 43:30 | 18 | 21.25 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01708
YWS01709 | Yorkshire Water | Live | CANAL ROAD 330 NO 2 CSO | CANAL ROAD 330/NO 2 CSO | WRA8253 | WRA8253 | A1 | SO on sewer network | SE1587035120 | 415870 | 435120 | GB104027062862 | Bradford Beck (Clayton Bk to R Aire) | River | 3307 | Middle Aire | 3001 | Aire and Calder | BRADFORD BECK (CULVERTED) | Not Applicable | Not Applicable | Not Applicable | 6:15 | 8 | 7.8 | 2020 | 95.94 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01709
YWS01710 | Yorkshire Water | Live | BALME ROAD NO 2 CSO | BALME ROAD/NO 2 CSO | WRA8255 | WRA8255 | A1 | SO on sewer network | SE1893725964 | 418937 | 425964 | GB104027062710 | Spen Beck from Source to River Calder | River | 3268 | Lower Calder | 3001 | Aire and Calder | RIVER SPEN | Not Applicable | Not Applicable | Not Applicable | 1:00 | 1 | 2.2 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01710
YWS01711 | Yorkshire Water | Live | BROOMFIELD LANE NO 2 CSO | BROOMFIELD LANE/NO 2 CSO | WRA8256 | WRA8256 | A1 | SO on sewer network | SE2414313223 | 424143 | 413223 | GB104027063310 | Bentley Brook from Source to River Dearne | River | 3125 | Dearne | 3029 | Don and Rother | OUT LANE DYKE | Not Applicable | Not Applicable | Not Applicable | 144:45 | 31 | 31.2 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01711
YWS01712 | Yorkshire Water | Live | STONEYROCK LANE CSO | STONEYROCK LANE/CSO | WRA8259 | WRA8259 | A1 | SO on sewer network | SE3105034220 | 431050 | 434220 | GB104027062900 | Meanwood Beck from Source to River Aire | River | 3265 | Lower Aire | 3001 | Aire and Calder | STONEY ROCK BECK | Not Applicable | Not Applicable | Not Applicable | 24:00 | 15 | 11.2 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01712
YWS01713 | Yorkshire Water | Live | STONEYROCK LANE CSO | COMPTON PLACE/CSO | WRA8259 | EPR/RB3790EY | A1 | SO on sewer network | SE3105034220 | 431050 | 434220 | GB104027062900 | Meanwood Beck from Source to River Aire | River | 3265 | Lower Aire | 3001 | Aire and Calder | STONEY ROCK BECK | Not Applicable | Not Applicable | Not Applicable | 154:00 | 77 | 84.2 | 2020 | 100 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01713
YWS01714 | Yorkshire Water | Live | ROOMS LANE NO 2 CSO | ROOMS LANE/NO 2 CSO | WRA8260 | WRA8260 | A1 | SO on sewer network | SE2585829820 | 425858 | 429820 | GB104027062750 | Milshaw Beck from Source to Low/Wortley/Pudsey Bks | River | 3265 | Lower Aire | 3001 | Aire and Calder | CLVRTD TRIB OF DEAN BECK | Not Applicable | Not Applicable | Not Applicable | 103:30 | 35 | 35.6 | 2020 | 92.88 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01714
YWS01715 | Yorkshire Water | Live | HERRIES ROAD NO 2 CSO | HERRIES ROAD/NO 2 CSO | WRA8261 | WRA8261 | A1 | SO on sewer network | SK3377090740 | 433767 | 390737 | GB104027057411 | Don from Little Don to River Loxley confluence | River | 3490 | Upper Don | 3029 | Don and Rother | TODD HOLE DIKE/MILL STREAM | Not Applicable | Not Applicable | Not Applicable | 225:30 | 79 | 74.6 | 2020 | 99.98 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | Operational investigation completed | No improvement action in reporting period | SOAF investigation completed - No work required | YWS01715
YWS01716 | Yorkshire Water | Live | WESTTHORPE NO 2 CSO | WESTHORPE/NO 2 CSO | WRA8262 | WRA8262 | A1 | SO on sewer network | SK4548579482 | 445485 | 379482 | GB104027057772 | Rother, Doe Lea to Don | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | PARK BROOK | Not Applicable | Not Applicable | Not Applicable | 9:45 | 8 | 5.8 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01716
YWS01717 | Yorkshire Water | Live | WAT CHURCH STREET CSO | WATH CHURCH STREET/CSO | WRA8264 | WRA8264 | A1 | SO on sewer network | SE4309400971 | 443094 | 400971 | GB104027057470 | Knoll Beck from Source to River Dearne | River | 3125 | Dearne | 3029 | Don and Rother | BROOK DIKE CULVERTED | Not Applicable | Not Applicable | Not Applicable | 3:00 | 8 | 5.2 | 2020 | 99.93 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01717
YWS01718 | Yorkshire Water | Live | GILBERDYKE STW | GILBERDYKE/STW | WRA8281 | WRA8281 | 2 | Inlet SO at WwTW | SE8470024110 | 484700 | 424110 | GB530402609203 | HUMBER UPPER | Transitional Water | 3228 | Humber Estuary TraC | 3040 | Humber TraC | RIVER OUSE | Not Applicable | Not Applicable | Not Applicable | 547:45 | 129 | 128.4 | 2020 | 96.29 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement ongoing | SOAF investigation ongoing | YWS01718
YWS01719 | Yorkshire Water | Live | MELTON STW | MELTON/STW | WRA8282 | WRA8282 | A2 | Inlet SO at WwTW | SE9756024810 | 497560 | 424810 | GB530402609202 | HUMBER MIDDLE | Transitional Water | 3228 | Humber Estuary TraC | 3040 | Humber TraC | RIVER HUMBER | Not Applicable | Not Applicable | Not Applicable | 2065:30 | 213 | 231.8 | 2020 | 98.51 |  |  | Performance - Infiltration | Performance - Infiltration | UWWTR investigation ongoing, Operational investigation completed | Operational improvement completed | SOAF investigation ongoing | YWS01719
YWS01720 | Yorkshire Water | Live | MELTON STW | MELTON/STW | WRA8282 | WRA8282 | A3 | Inlet SO at WwTW | SE9756024810 | 497560 | 424810 | GB530402609202 | HUMBER MIDDLE | Transitional Water | 3228 | Humber Estuary TraC | 3040 | Humber TraC | RIVER HUMBER | Not Applicable | Not Applicable | Not Applicable | 1868:45 | 154 | 127.33 | 2020 | 99.99 |  |  | Performance - Infiltration | Performance - Infiltration | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01720
YWS01721 | Yorkshire Water | Live | BROUGH NO 1 SPS | BROUGH/CSO | WRA8283 | WRA8283 | 1 | SO on sewer network | SE9363026200 | 493630 | 426200 | Not part of a WFD catchment | Not part of a WFD catchment | River | N/A | N/A | N/A | N/A | RIVER HUMBER | Not Applicable | Not Applicable | Not Applicable | 11:00 | 8 | 101.5 | 2020 | 16.66 | Installation set-up/design issue | Resolved - Nov | High spill threshold not met | Data collection - Tidal / river inundation | UWWTR investigation ongoing, Operational investigation completed | Operational improvement ongoing | SOAF investigation ongoing | YWS01721
YWS01722 | Yorkshire Water | Live | WELTON SPS | WELTON/CSO | WRA8284 | WRA8284 | 1 | Storm discharge at pumping station | SE9536025760 | 495360 | 425760 | Not part of a WFD catchment | Not part of a WFD catchment | River | N/A | N/A | N/A | N/A | WELTON BANK DRAIN | Not Applicable | Not Applicable | Not Applicable | 306:15 | 54 | 44.4 | 2020 | 99.87 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01722
YWS01723 | Yorkshire Water | Live | CASTLEFORD LANE/CASTLEFORD RD CSO | CASTLEFORD ROAD/CSO | WRA8302 | WRA8302 | A1 | SO on sewer network | SE3966024070 | 439660 | 424070 | GB104027062590 | Choke Churl Bk from Source to River Calder | River | 3268 | Lower Calder | 3001 | Aire and Calder | WAIN DIKE BECK | Not Applicable | Not Applicable | Not Applicable | 146:00 | 37 | 30.4 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01723
YWS01724 | Yorkshire Water | Live | CASTLEFORD LANE/CASTLEFORD RD CSO | CASTLEFORD RD/CSO | WRA8302 | WRA8302 | A2 | Storm discharge at pumping station | SE3966024070 | 439660 | 424070 | GB104027062590 | Choke Churl Bk from Source to River Calder | River | 3268 | Lower Calder | 3001 | Aire and Calder | WAIN DIKE BECK | Not Applicable | Not Applicable | Not Applicable | 39:00 | 10 | 4.8 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01724
YWS01725 | Yorkshire Water | Live | FELL VIEW CSO | FELL VIEW EMBSAY/NO 2 CSO | WRA8309 | WRA8309 | 1 | SO on sewer network | SE0133053590 | 401330 | 453599 | GB104027063060 | Haw Beck from Source to Eller beck | River | 3484 | Upper Aire | 3001 | Aire and Calder | GREEN BOTTOM BECK | Not Applicable | Not Applicable | Not Applicable | 3:15 | 4 | 14.6 | 2020 | 98.86 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01725
YWS01726 | Yorkshire Water | Live | VICAR LANE 2 CSO | VICAR LANE/NO 2 CSO | WRA8317 | WRA8317 | A1 | SO on sewer network | SE1672033010 | 416720 | 433010 | GB104027062862 | Bradford Beck (Clayton Bk to R Aire) | River | 3307 | Middle Aire | 3001 | Aire and Calder | EAST BROOK (CULVERTED) | Not Applicable | Not Applicable | Not Applicable | 31:30 | 26 | 32.8 | 2020 | 90.49 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01726
YWS01727 | Yorkshire Water | Live | LOWER KIPPING LANE 2 CSO | LOWER KIPPING LANE/2 CSO | WRA8323 | WRA8323 | A1 | SO on sewer network | SE0979632499 | 409796 | 432499 | GB104027062861 | Clayton Beck (Source to Bradford Bk) | River | 3307 | Middle Aire | 3001 | Aire and Calder | PINCH BECK | Not Applicable | Not Applicable | Not Applicable | 50:45 | 34 | 36.4 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01727
YWS01728 | Yorkshire Water | Live | DONCASTER INTERCHANGE CSO | DONCASTER INTERCHANGE/CSO | WRA8327 | WRA8327 | A1 | SO on sewer network | SE5718003434 | 457180 | 403434 | GB70410281 | Sheffield and South Yorkshire Navigation (New Junction and Stainforth and Keadby | Canal | 2018 | Don and Rother Canals | 2001 | Humber AWB | CULVERTED RIVER CHESWOLD | Not Applicable | Not Applicable | Not Applicable | 25:45 | 8 | 3.6 | 2020 | 99.84 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01728
YWS01729 | Yorkshire Water | Live | WEST SCHOLES CSO | WEST SCHOLES/CSO | WRA8334 | WRA8334 | A1 | SO on sewer network | SE0979431675 | 409794 | 431675 | GB104027062861 | Clayton Beck (Source to Bradford Bk) | River | 3307 | Middle Aire | 3001 | Aire and Calder | HIGH BIRKS BECK | Not Applicable | Not Applicable | Not Applicable | 37:30 | 33 | 60.6 | 2020 | 56.11 | Comms failure / issue | Resolved - February after reporting year | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement completed | SOAF investigation ongoing | YWS01729
YWS01730 | Yorkshire Water | Live | BEWHOLME WWTW | BEWHOLME/STW | WRA8337 | WRA8337 | A2 | Inlet SO at WwTW | TA1690050190 | 516900 | 450190 | GB104026077770 | Barmston Sea Drain / Skipsea Drain to Conf | River | 3025 | Barmston Sea Drain | 3039 | Hull and East Riding | UNNAMED TRIB OF STREAM DIKE | Not Applicable | Not Applicable | Not Applicable | 240:15 | 34 | 31.6 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01730
YWS01731 | Yorkshire Water | Live | RUSTON PARVA WWTW | RUSTON PARVA/STW | WRA8338 | WRA8338 | 2 | Inlet SO at WwTW | TA0669061620 | 506690 | 461620 | GB104026067101 | Lowthorpe/Kelk/Foston Bks from Source to Frodingham Beck | River | 3492 | Upper Hull | 3039 | Hull and East Riding | UNNAMED TRIB OF WHITE DIKE | Not Applicable | Not Applicable | Not Applicable | 3862:00 | 186 | 97.6 | 2020 | 100 |  |  | Performance - GW inundation | Performance - GW inundation | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS01731
YWS01732 | Yorkshire Water | Live | BEWHOLME SEWAGE PUMPING STATION | SEATON ROAD BEWHOLME/CSO | WRA8339 | WRA8339 | 1 | Storm discharge at pumping station | TA1684049730 | 516840 | 449726 | GB104026077770 | Barmston Sea Drain / Skipsea Drain to Conf | River | 3025 | Barmston Sea Drain | 3039 | Hull and East Riding | UNNAMED TRIB OF STREAM DIKE | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 1.2 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01732
YWS01733 | Yorkshire Water | Live | BURTON AGNES SOUTH CSO | BURTON AGNES SOUTH/CSO | WRA8341 | WRA8341 | A1 | SO on sewer network | TA1045762532 | 510457 | 462532 | GB104026066630 | Gransmoor Drain (Burton Agnes to Lissett Area) | River | 3025 | Barmston Sea Drain | 3039 | Hull and East Riding | CLVRT TRIB GRANSMOOR DRAIN | Not Applicable | Not Applicable | Not Applicable | 239:00 | 44 | 57.8 | 2020 | 99.95 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS01733
YWS01734 | Yorkshire Water | Live | STANDBRIDGE LANE CSO | STANDBRIDGE LANE/CSO | WRA8342 | WRA8342 | A1 | SO on sewer network | SE3340017098 | 433400 | 417098 | GB104027062530 | Owler Beck from Source to River Calder | River | 3268 | Lower Calder | 3001 | Aire and Calder | OWLER BECK | Not Applicable | Not Applicable | Not Applicable | 106:15 | 50 | 63.2 | 2020 | 100 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01734
YWS01735 | Yorkshire Water | Live | MEMORIAL GARDENS SPS | MEMORIAL GDNS/CSO | WRA8365 | WRA8365 | 1 | Storm discharge at pumping station | TA3440027940 | 534970 | 427010 | GB640402491000 | Yorkshire South | Coastal Water | 3179 | Esk TraC | 3040 | Humber TraC | NORTH SEA | Not Applicable | Withernsea | Not Applicable | 36:14 | 8 | 72 | 2020 | 100 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01735
YWS01736 | Yorkshire Water | Live | WAKEFIELD ROAD SCISSET CSO | WAKEFIELD RD SCISSET/CSO | WRA8374 | WRA8374 | A1 | SO on sewer network | SE2522510797 | 425225 | 410797 | GB104027063220 | Dearne from Source to Bentley Brook | River | 3125 | Dearne | 3029 | Don and Rother | RIVER DEARNE | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0.8 | 2020 | 90.09 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01736
YWS01737 | Yorkshire Water | Live | KINSLEY WAKEFIELD ROAD CSO | KINSLEY WAKEFIELD RD/CSO | WRA8375 | WRA8375 | A1 | SO on sewer network | SE4169814797 | 441698 | 414797 | GB104027063320 | Hoyle Mill Stream from Source to River Went | River | 3272 | Lower Don | 3029 | Don and Rother | TRIBUTARY OF RIVER WENT | Not Applicable | Not Applicable | Not Applicable | 9:45 | 9 | 12.8 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01737
YWS01738 | Yorkshire Water | Live | WELLAND CRESCENT CSO | WELLAND CRESCENT/CSO | WRA8383 | WRA8383 | A1 | SO on sewer network | SE3892000630 | 438920 | 400630 | GB104027057470 | Knoll Beck from Source to River Dearne | River | 3125 | Dearne | 3029 | Don and Rother | JUMP VALLEY STREAM | Not Applicable | Not Applicable | Not Applicable | 120:45 | 46 | 40.8 | 2020 | 100 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS01738
YWS01739 | Yorkshire Water | Live | CHURCH STREET JUMP CSO | CHURCH STREET JUMP/2 CSO | WRA8384 | WRA8384 | A1 | SO on sewer network | SE3773100993 | 437731 | 400993 | GB104027057470 | Knoll Beck from Source to River Dearne | River | 3125 | Dearne | 3029 | Don and Rother | JUMP VALLEY STREAM | Not Applicable | Not Applicable | Not Applicable | 171:30 | 61 | 56.4 | 2020 | 98.74 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement ongoing | SOAF investigation ongoing | YWS01739
YWS01740 | Yorkshire Water | Live | COBCAR LANE CSO | COBCAR LANE/CSO | WRA8385 | WRA8385 | A1 | SO on sewer network | SE3830100795 | 438301 | 400795 | GB104027057470 | Knoll Beck from Source to River Dearne | River | 3125 | Dearne | 3029 | Don and Rother | JUMP VALLEY STREAM | Not Applicable | Not Applicable | Not Applicable | 101:00 | 45 | 50 | 2020 | 100 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS01740
YWS01741 | Yorkshire Water | Live | WAR MEMORIAL NO 2 CSO | WAR MEMORIAL/NO 2 CSO | WRA8387 | WRA8387 | A1 | SO on sewer network | SE5460006940 | 454607 | 406949 | GB104027057541 | Bentley Mill Stream | River | 3272 | Lower Don | 3029 | Don and Rother | TRIBUTARY OF LANGTHWAITE DYKE | Not Applicable | Not Applicable | Not Applicable | 4:45 | 12 | 30.6 | 2020 | 98.03 |  |  | High spill threshold not met | High spill threshold not met | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS01741
YWS01742 | Yorkshire Water | Live | TROUGHBROOK ROAD NO 2 CSO | TROUGHBROOK ROAD/NO 2 CSO | WRA8392 | WRA8392 | A1 | SO on sewer network | SK4170874516 | 441708 | 374516 | GB70410054 | Chesterfield Canal (River Rother) | Canal | 2018 | Don and Rother Canals | 2001 | Humber AWB | TROUGH BROOK | Not Applicable | Not Applicable | Not Applicable | 175:15 | 43 | 46.4 | 2020 | 99.59 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01742
YWS01743 | Yorkshire Water | Live | GREAT HATFIELD STW | GREAT HATFIELD/NO 2 STW | WRA8394 | WRA8394 | A2 | Inlet SO at WwTW | TA1821042730 | 518210 | 442730 | GB104026066860 | Lambwath Stream from Source to Foredyke Stream | River | 3274 | Lower Hull | 3039 | Hull and East Riding | UNNAMED TRIB OF CATCHWATER DRN | Not Applicable | Not Applicable | Not Applicable | 584:00 | 50 | 37 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01743
YWS01744 | Yorkshire Water | Live | HOLMPTON STW | HOLMPTON/STW | WRA8395 | WRA8395 | A2 | Inlet SO at WwTW | TA3662023800 | 536620 | 423800 | Not part of a WFD catchment | Not part of a WFD catchment | River | N/A | N/A | N/A | N/A | UNNAMED TRIB OF NEVILLS DRAIN | Not Applicable | Not Applicable | Not Applicable | 667:45 | 80 | 106.6 | 2020 | 99.59 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS01744
YWS01745 | Yorkshire Water | Live | WARLEY CLOUGH CSO | WARLEY CLOUGH/CSO | WRA8412 | WRA8412 | A1 | SO on sewer network | SE0637924339 | 406379 | 424339 | GB104027062642 | Calder from Ryburn Confluence to River Colne | River | 3310 | Middle Calder | 3001 | Aire and Calder | WARLEY CLOUGH DAMS | Not Applicable | Not Applicable | Not Applicable | 0:30 | 1 | 0.8 | 2020 | 99.93 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01745
YWS01746 | Yorkshire Water | Live | WATSON MILL LANE CSO | WATSON MILL LANE/CSO | WRA8413 | WRA8413 | A1 | SO on sewer network | SE0558422995 | 405584 | 422995 | GB104027062580 | Ryburn from Booth Dean Clough to R Calder | River | 3310 | Middle Calder | 3001 | Aire and Calder | RIVER RYBURN | Not Applicable | Not Applicable | Not Applicable | 8:04 | 8 | 38.5 | 2020 | 10.59 | Sensor failure / issue | Resolved - Nov | High spill threshold not met | High spill threshold not met | Operational investigation ongoing | No improvement action in reporting period | No SOAF investigation required | YWS01746
YWS01747 | Yorkshire Water | Live | SOWERBY CROFT LANE NO 2 CSO | SOWERBY CROFT LANE/2 CSO | WRA8414 | WRA8414 | A1 | SO on sewer network | SE0577922925 | 405779 | 422925 | GB104027062580 | Ryburn from Booth Dean Clough to R Calder | River | 3310 | Middle Calder | 3001 | Aire and Calder | TRIBUTARY OF THE RIVER RYBURN | Not Applicable | Not Applicable | Not Applicable | 0:34 | 1 | 5.8 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01747
YWS01748 | Yorkshire Water | Live | HEPTONSTALL ROAD CSO | HEPTONSTALL ROAD/CSO | WRA8417 | WRA8417 | A1 | SO on sewer network | SD9914927765 | 399149 | 427765 | GB104027062731 | Hebden Water from Widdop Beck to R Calder | River | 3487 | Upper Calder | 3001 | Aire and Calder | HEBDEN WATER | Not Applicable | Not Applicable | Not Applicable | 66:30 | 22 | 40.4 | 2020 | 100 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01748
YWS01749 | Yorkshire Water | Live | BIRCHCLIFFE ROAD CSO | BIRCHCLIFFE ROAD/NO 2 CSO | WRA8418 | WRA8418 | 1 | SO on sewer network | SD9934027310 | 399342 | 427319 | GB104027062731 | Hebden Water from Widdop Beck to R Calder | River | 3487 | Upper Calder | 3001 | Aire and Calder | TRIBUTARY OF HEBDEN WATER | Not Applicable | Not Applicable | Not Applicable | 1:45 | 4 | 1.6 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01749
YWS01750 | Yorkshire Water | Live | SALEM CRICKET GROUND CSO | SALEM CRICKET GROUND/CSO | WRA8419 | WRA8419 | A1 | SO on sewer network | SD9920728060 | 399207 | 428060 | GB104027062731 | Hebden Water from Widdop Beck to R Calder | River | 3487 | Upper Calder | 3001 | Aire and Calder | HEBDEN WATER | Not Applicable | Not Applicable | Not Applicable | 173:30 | 19 | 57.6 | 2020 | 79.65 | Comms failure / issue | Resolved - Dec | High spill threshold not met | Not asset maintenance - Hydraulic capacity | Operational investigation completed | Operational improvement completed | SOAF investigation completed - No work required | YWS01750
YWS01751 | Yorkshire Water | Live | WHARFE HOUSE CSO | WHARFE HOUSE/CSO | WRA8420 | WRA8420 | A1 | SO on sewer network | SE0646323638 | 406463 | 423638 | GB104027062642 | Calder from Ryburn Confluence to River Colne | River | 3310 | Middle Calder | 3001 | Aire and Calder | RIVER CALDER | Not Applicable | Not Applicable | Not Applicable | 194:30 | 80 | 103.4 | 2020 | 97.06 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01751
YWS01752 | Yorkshire Water | Live | DALTON ICI NORTH NO 2 CSO | DALTON ICI NORTH/NO 2 CSO | WRA8422 | WRA8422 | A1 | SO on sewer network | SE1699117662 | 416991 | 417662 | GB104027063340 | Fenay beck from Source to River Colne | River | 3097 | Colne and Holme | 3001 | Aire and Calder | LEES HEAD BECK | Not Applicable | Not Applicable | Not Applicable | 402:15 | 80 | 89.8 | 2020 | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | No investigation activity in reporting period | No improvement action in reporting period | SOAF investigation completed - No work required | YWS01752
YWS01753 | Yorkshire Water | Live | WATERLOO ROAD NO2 CSO | WATERLOO ROAD/NO 2 CSO | WRA8423 | WRA8423 | A1 | SO on sewer network | SE1766016625 | 417660 | 416625 | GB104027063340 | Fenay beck from Source to River Colne | River | 3097 | Colne and Holme | 3001 | Aire and Calder | ROUND WOOD BECK | Not Applicable | Not Applicable | Not Applicable | 511:15 | 87 | 97.4 | 2020 | 100 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | No investigation activity in reporting period | No improvement action in reporting period | SOAF investigation completed - No work required | YWS01753
YWS01754 | Yorkshire Water | Live | ALMONDBURY CSO | ALMONDBURY/CSO | WRA8424 | WRA8424 | A1 | SO on sewer network | SE1803815888 | 418038 | 415888 | GB104027063340 | Fenay beck from Source to River Colne | River | 3097 | Colne and Holme | 3001 | Aire and Calder | FENAY BECK | Not Applicable | Not Applicable | Not Applicable | 2:45 | 7 | 21.2 | 2020 | 99.95 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01754
YWS01755 | Yorkshire Water | Live | DOBB LANE NO 2 CSO | DOBB LANE/NO 2 CSO | WRA8425 | WRA8425 | A1 | SO on sewer network | SE1261207087 | 412612 | 407087 | GB104027057600 | Holme from Source to New Mill Dike | River | 3097 | Colne and Holme | 3001 | Aire and Calder | STUBBIN CLOUGH | Not Applicable | Not Applicable | Not Applicable | 130:00 | 33 | 48.4 | 2020 | 99.98 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS01755
YWS01756 | Yorkshire Water | Live | WYKE OLD LANE CSO | WYKE OLD LANE/CSO | WRA8426 | WRA8426 | A1 | SO on sewer network | SE1485825134 | 414858 | 425134 | GB104027062700 | Clifton Beck from Source to River Calder | River | 3310 | Middle Calder | 3001 | Aire and Calder | CLIFTON BECK | Not Applicable | Not Applicable | Not Applicable | 272:15 | 80 | 94 | 2020 | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | Operational investigation completed | Operational improvement ongoing | SOAF investigation completed - No work required | YWS01756
YWS01757 | Yorkshire Water | Live | BIRDS ROYD LANE CSO | BIRDS ROYD LANE/NO 2 CSO | WRA8428 | WRA8428 | A1 | SO on sewer network | SE1472622552 | 414726 | 422552 | GB104027062642 | Calder from Ryburn Confluence to River Colne | River | 3310 | Middle Calder | 3001 | Aire and Calder | RIVER CALDER | Not Applicable | Not Applicable | Not Applicable | 55:32 | 55 | 47.4 | 2020 | 100 |  |  | High spill threshold not met | Performance - Infiltration | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01757
YWS01758 | Yorkshire Water | Live | HELLIWELL SYKE CSO | HELLIWELL SYKE/NO 3 CSO | WRA8430 | WRA8430 | 1 | SO on sewer network | SE2359026060 | 413500 | 426000 | GB104027062700 | Clifton Beck from Source to River Calder | River | 3310 | Middle Calder | 3001 | Aire and Calder | HELLIWELL SYKE | Not Applicable | Not Applicable | Not Applicable | 2:15 | 2 | 2.6 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01758
YWS01759 | Yorkshire Water | Live | SWAN BANK NO 2 CSO | SWAN BANK/NO 2 CSO | WRA8431 | WRA8431 | A1 | SO on sewer network | SE1448607860 | 414486 | 407860 | GB104027057600 | Holme from Source to New Mill Dike | River | 3097 | Colne and Holme | 3001 | Aire and Calder | RIVER RIBBLE | Not Applicable | Not Applicable | Not Applicable | 6:15 | 4 | 8.6 | 2020 | 99.95 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01759
YWS01760 | Yorkshire Water | Live | ST GEORGE'S ROAD CSO | ST GEORGES ROAD/NO 2 CSO | WRA8432 | WRA8432 | 1 | SO on sewer network | SE1605007560 | 416048 | 407558 | GB104027057610 | New Mill Dike from Source to River Holme | River | 3097 | Colne and Holme | 3001 | Aire and Calder | TRIB OF JACKSON BRIDGE DIKE | Not Applicable | Not Applicable | Not Applicable | 20:30 | 17 | 13.2 | 2020 | 99.39 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01760
YWS01761 | Yorkshire Water | Live | DALTON LONG LANE NO 2 CSO | DALTON LONG LANE/NO 2 CSO | WRA8433 | WRA8433 | A1 | SO on sewer network | SE1707017400 | 417070 | 417400 | GB104027063340 | Fenay beck from Source to River Colne | River | 3097 | Colne and Holme | 3001 | Aire and Calder | LEES HEAD BECK | Not Applicable | Not Applicable | Not Applicable | 29:45 | 24 | 24.2 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01761
YWS01762 | Yorkshire Water | Live | FENAY LANE CSO | FENAY LANE/CSO | WRA8434 | WRA8434 | A1 | SO on sewer network | SE1812115508 | 418121 | 415508 | GB104027063340 | Fenay beck from Source to River Colne | River | 3097 | Colne and Holme | 3001 | Aire and Calder | FENAY BECK | Not Applicable | Not Applicable | Not Applicable | 77:30 | 30 | 40.6 | 2020 | 100 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01762
YWS01763 | Yorkshire Water | Live | WATER STREET NO 2 CSO | WATER STREET/NO 2 CSO | WRA8435 | WRA8435 | A1 | SO on sewer network | SE1369015140 | 413693 | 415139 | GB104027063301 | Holme from New Mill Dike to R Colne | River | 3097 | Colne and Holme | 3001 | Aire and Calder | RIVER HOLME | Not Applicable | Not Applicable | Not Applicable | 32:30 | 33 | 24 | 2020 | 99.88 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01763
YWS01764 | Yorkshire Water | Live | THIRSTIN ROAD NO2 CSO | THIRSTIN ROAD/NO 2 CSO | WRA8436 | WRA8436 | A1 | SO on sewer network | SE1343412200 | 413434 | 412200 | GB104027063590 | Mag Brook from Source to River Holme | River | 3097 | Colne and Holme | 3001 | Aire and Calder | TRIBUTARY OF MAG BROOK | Not Applicable | Not Applicable | Not Applicable | 198:30 | 58 | 68 | 2020 | 98.39 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | No investigation activity in reporting period | No improvement action in reporting period | SOAF investigation completed - No work required | YWS01764
YWS01765 | Yorkshire Water | Live | CORN MILL NO 2 CSO | CORN MILL/NO 2 CSO | WRA8437 | WRA8437 | A1 | SO on sewer network | SE1401512140 | 414015 | 412140 | GB104027063301 | Holme from New Mill Dike to R Colne | River | 3097 | Colne and Holme | 3001 | Aire and Calder | RIVER HOLME | Not Applicable | Not Applicable | Not Applicable | 104:15 | 41 | 41 | 2020 | 100 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | No investigation activity in reporting period | No improvement action in reporting period | SOAF investigation completed - Work required | YWS01765
YWS01766 | Yorkshire Water | Live | HONLEY BRIDGE NO 2 CSO | HONLEY BRIDGE/NO 2 CSO | WRA8438 | WRA8438 | A1 | SO on sewer network | SE1404512015 | 414045 | 412015 | GB104027063301 | Holme from New Mill Dike to R Colne | River | 3097 | Colne and Holme | 3001 | Aire and Calder | RIVER HOLME | Not Applicable | Not Applicable | Not Applicable | 5:00 | 6 | 12.8 | 2020 | 98.94 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01766
YWS01767 | Yorkshire Water | Live | BONEGATE LANE CSO | BONEGATE LANE/CSO | WRA8439 | WRA8439 | A1 | SO on sewer network | SE1509022520 | 415090 | 422520 | GB104027062642 | Calder from Ryburn Confluence to River Colne | River | 3310 | Middle Calder | 3001 | Aire and Calder | RIVER CALDER | Not Applicable | Not Applicable | Not Applicable | 596:15 | 144 | 149 | 2020 | 99.95 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation ongoing | Operational improvement ongoing | SOAF investigation ongoing | YWS01767
YWS01768 | Yorkshire Water | Live | BONEGATE LANE CSO | ALEGER STREET/CSO | WRA8439 | EPR/RB3790WE | A1 | SO on sewer network | SE1509022520 | 415090 | 422520 | GB104027062642 | Calder from Ryburn Confluence to River Colne | River | 3310 | Middle Calder | 3001 | Aire and Calder | RIVER CALDER | Not Applicable | Not Applicable | Not Applicable | 84:45 | 38 | 124.4 | 2020 | 99.86 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation completed | No improvement action in reporting period | SOAF investigation completed - No work required | YWS01768
YWS01769 | Yorkshire Water | Live | BONEGATE LANE CSO | THORNHILLS BECK LANE/CSO | WRA8439 | EPR/RB3791AR | A1 | SO on sewer network | SE1509022520 | 415090 | 422520 | GB104027062642 | Calder from Ryburn Confluence to River Colne | River | 3310 | Middle Calder | 3001 | Aire and Calder | RIVER CALDER | Not Applicable | Not Applicable | Not Applicable | 1067:00 | 149 | 136.8 | 2020 | 100 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation completed, Operational investigation ongoing | Operational improvement ongoing | SOAF investigation completed - No work required | YWS01769
YWS01770 | Yorkshire Water | Live | HOULTS LANE CSO | HOULTS LANE/CSO | WRA8440 | WRA8440 | A1 | SO on sewer network | SE0967821322 | 409678 | 421322 | GB104027062570 | Black Brook from Source to River Calder | River | 3310 | Middle Calder | 3001 | Aire and Calder | BLACK BROOK | Not Applicable | Not Applicable | Not Applicable | 1:45 | 4 | 15.4 | 2020 | 79.18 | Sensor failure / issue | Resolved - Apr | High spill threshold not met | High spill threshold not met | Operational investigation completed | Operational improvement completed | No SOAF investigation required | YWS01770
YWS01771 | Yorkshire Water | Live | HONLEY HUDDERSFIELD ROAD NO 2 | HONLEY HUDDSFLD RD/2 CSO | WRA8441 | WRA8441 | A1 | SO on sewer network | SE1404212580 | 414042 | 412580 | GB104027063301 | Holme from New Mill Dike to R Colne | River | 3097 | Colne and Holme | 3001 | Aire and Calder | RIVER HOLME | Not Applicable | Not Applicable | Not Applicable | 336:00 | 67 | 60.2 | 2020 | 98.34 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS01771
YWS01772 | Yorkshire Water | Live | ROCHDALE ROAD CSO | ROCHDALE ROAD/CSO | WRA8442 | WRA8442 | A1 | SO on sewer network | SE0967821322 | 409678 | 421322 | GB104027062570 | Black Brook from Source to River Calder | River | 3310 | Middle Calder | 3001 | Aire and Calder | BLACK BROOK | Not Applicable | Not Applicable | Not Applicable | 0:30 | 2 | 1.8 | 2020 | 99.48 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01772
YWS01773 | Yorkshire Water | Live | DARK LANE NO 2 CSO | DARK LANE/NO 2 CSO | WRA8444 | WRA8444 | A1 | SO on sewer network | SE1198023370 | 411985 | 423379 | GB104027062642 | Calder from Ryburn Confluence to River Colne | River | 3310 | Middle Calder | 3001 | Aire and Calder | TRIBUTARY OF THE RIVER CALDER | Not Applicable | Not Applicable | Not Applicable | 29:45 | 26 | 39.6 | 2020 | 93.57 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | SOAF investigation completed - Work required | YWS01773
YWS01774 | Yorkshire Water | Live | PICKWICK MILL CSO | PICKWICK MILL/CSO | WRA8445 | WRA8445 | 1 | SO on sewer network | SE1469009430 | 414693 | 409433 | GB104027057600 | Holme from Source to New Mill Dike | River | 3097 | Colne and Holme | 3001 | Aire and Calder | RIVER HOLME | Not Applicable | Not Applicable | Not Applicable | 98:15 | 25 | 26 | 2020 | 99.72 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01774
YWS01775 | Yorkshire Water | Live | NEW INN WEST STREET CSO | NEW INN WEST STREET/CSO | WRA8446 | WRA8446 | A1 | SO on sewer network | SE0589023460 | 405892 | 423460 | GB104027062580 | Ryburn from Booth Dean Clough to R Calder | River | 3310 | Middle Calder | 3001 | Aire and Calder | RIVER RYBURN | Not Applicable | Not Applicable | Not Applicable | 1392:56 | 122 | 113 | 2020 | 95.42 |  |  | Performance - Infiltration | Performance - Infiltration | Operational investigation completed | Operational improvement completed | SOAF investigation completed - No work required | YWS01775
YWS01776 | Yorkshire Water | Live | TOWNGATE HOLMFIRTH 2 CSO | TOWNGATE HOLMFIRTH/2 CSO | WRA8447 | WRA8447 | A1 | SO on sewer network | SE1424708232 | 414247 | 408232 | GB104027057600 | Holme from Source to New Mill Dike | River | 3097 | Colne and Holme | 3001 | Aire and Calder | RIVER HOLME | Not Applicable | Not Applicable | Not Applicable | 56:00 | 25 | 32.4 | 2020 | 99.98 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01776
YWS01777 | Yorkshire Water | Live | POLLARD STREET NO 2 CSO | POLLARD STREET/NO 2 CSO | WRA8448 | WRA8448 | A1 | SO on sewer network | SE1483022550 | 414834 | 422555 | GB104027062642 | Calder from Ryburn Confluence to River Colne | River | 3310 | Middle Calder | 3001 | Aire and Calder | RIVER CALDER | Not Applicable | Not Applicable | Not Applicable | 84:14 | 34 | 35.4 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01777
YWS01778 | Yorkshire Water | Live | LONGLANDS ROAD CSO | LONGLANDS ROAD/NO 2 CSO | WRA8449 | WRA8449 | A1 | SO on sewer network | SE1502010040 | 415013 | 410048 | GB104027057600 | Holme from Source to New Mill Dike | River | 3097 | Colne and Holme | 3001 | Aire and Calder | RIVER HOLME | Not Applicable | Not Applicable | Not Applicable | 2152:15 | 106 | 116 | 2020 | 99.98 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | Operational investigation completed | No improvement action in reporting period | SOAF investigation completed - No work required | YWS01778
YWS01779 | Yorkshire Water | Live | SINKING WOOD NO2 CSO | SINKING WOOD/NO 2 CSO | WRA8450 | WRA8450 | A1 | SO on sewer network | SE1569509881 | 415695 | 409881 | GB104027057610 | New Mill Dike from Source to River Holme | River | 3097 | Colne and Holme | 3001 | Aire and Calder | NEW MILL DIKE | Not Applicable | Not Applicable | Not Applicable | 891:30 | 70 | 86.4 | 2020 | 100 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01779
YWS01780 | Yorkshire Water | Live | TIMOTHY LANE TANK CSO | TIMOTHY LANE/CSO | WRA8451 | WRA8451 | A1 | SO on sewer network | SE2477925318 | 424779 | 425318 | GB104027062670 | Batley Beck from Source to River Calder | River | 3268 | Lower Calder | 3001 | Aire and Calder | HOWLEY BECK | Not Applicable | Not Applicable | Not Applicable | 45:00 | 5 | 5.8 | 2020 | 99.92 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01780
YWS01781 | Yorkshire Water | Live | LOW MILL LANE CSO | LOW MILL LANE 27/CSO | WRA8453 | WRA8453 | 1 | SO on sewer network | SE0668041160 | 406680 | 441160 | GB104027062891 | Worth from Bridgehouse Beck to R Aire | River | 3307 | Middle Aire | 3001 | Aire and Calder | RIVER WORTH | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0 | 2020 | 89.47 | Installation set-up/design issue | Resolved - Feb | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01781
YWS01782 | Yorkshire Water | Live | LANGSETT ROAD CSO | LANGSETT ROAD/CSO | WRA8454 | WRA8454 | A1 | SO on sewer network | SK3151492502 | 431514 | 392502 | GB104027057411 | Don from Little Don to River Loxley confluence | River | 3490 | Upper Don | 3029 | Don and Rother | RIVER DON | Not Applicable | Not Applicable | Not Applicable | 237:30 | 57 | 52.2 | 2020 | 100 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS01782
YWS01783 | Yorkshire Water | Live | CARR PIT ROAD CSO | CARR PIT ROAD/NO 2 CSO | WRA8455 | WRA8455 | A1 | SO on sewer network | SE1514716495 | 415147 | 416495 | GB104027062550 | Colne from River Holme to River Calder | River | 3097 | Colne and Holme | 3001 | Aire and Calder | RIVER COLNE | Not Applicable | Not Applicable | Not Applicable | 19:45 | 9 | 7 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01783
YWS01784 | Yorkshire Water | Live | WOODLANDS CLOSE CSO | WOODLANDS CLOSE/CSO | WRA8456 | WRA8456 | A1 | SO on sewer network | SE2032838274 | 420328 | 438274 | GB104027063032 | Aire from Gill Beck (Baildon) to River Calder | River | 3265 | Lower Aire | 3001 | Aire and Calder | RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 52:30 | 17 | 22 | 2023 | 46.87 | Sensor failure / issue | Scheduled | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01784
YWS01785 | Yorkshire Water | Live | LOWTOWN CSO | LOWTOWN/CSO | WRA8458 | WRA8458 | A1 | SO on sewer network | SE2287633566 | 422876 | 433566 | GB104027062830 | Low/Wortley/Pudsey Bks | River | 3265 | Lower Aire | 3001 | Aire and Calder | CLVRTDTRIB OF PUDSEY BECK | Not Applicable | Not Applicable | Not Applicable | 87:00 | 56 | 62.4 | 2020 | 99.99 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01785
YWS01786 | Yorkshire Water | Live | RIVERDALE ROAD NO 2 CSO | RIVERDALE ROAD/NO 2 CSO | WRA8462 | WRA8462 | A1 | SO on sewer network | SK3234985928 | 432349 | 385928 | GB104027057760 | Porter from Source to River Sheaf | River | 3312 | Middle Don | 3029 | Don and Rother | OAK BROOK | Not Applicable | Not Applicable | Not Applicable | 12:00 | 16 | 19.8 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01786
YWS01787 | Yorkshire Water | Live | BELGRAVE ROAD WEST CSO | BELGRAVE ROAD WEST/CSO | WRA8463 | WRA8463 | A1 | SO on sewer network | SK3122286137 | 431222 | 386137 | GB104027057760 | Porter from Source to River Sheaf | River | 3312 | Middle Don | 3029 | Don and Rother | TRIBUTARY OF PORTER BROOK | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0.2 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01787
YWS01788 | Yorkshire Water | Live | HIGH BRIDGE HILLSBOROUGH CSO | HIGH BRIDGE HILLSBORO/CSO | WRA8464 | WRA8464 | 1 | SO on sewer network | SK3344090530 | 433440 | 390530 | GB104027057411 | Don from Little Don to River Loxley confluence | River | 3490 | Upper Don | 3029 | Don and Rother | RIVER DON | Not Applicable | Not Applicable | Not Applicable | 706:15 | 106 | 108.4 | 2020 | 100 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS01788
YWS01789 | Yorkshire Water | Live | MAIN ROAD FARM CSO | MAIN ROAD FARM/CSO | WRA8465 | WRA8465 | A1 | SO on sewer network | SK3852069962 | 438520 | 369962 | GB104027057630 | Rother from Redleadmill Brook to Spital Brook | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | RIVER ROTHER | Not Applicable | Not Applicable | Not Applicable | 142:30 | 42 | 50.6 | 2020 | 100 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | No investigation activity in reporting period | No improvement action in reporting period | SOAF investigation completed - No work required | YWS01789
YWS01790 | Yorkshire Water | Live | MAYMAN LANE TANK CSO | MAYMAN LANE/CSO | WRA8467 | WRA8467 | A1 | SO on sewer network | SE2384024222 | 423840 | 424222 | GB104027062670 | Batley Beck from Source to River Calder | River | 3268 | Lower Calder | 3001 | Aire and Calder | TRIBUTARY OF BATLEY CARR | Not Applicable | Not Applicable | Not Applicable | 0:15 | 1 | 0.2 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01790
YWS01791 | Yorkshire Water | Live | COOPER LANE CSO | COOPER LANE/NO 2 CSO | WRA8468 | WRA8468 | A1 | SO on sewer network | SE1424008204 | 414240 | 408204 | GB104027057600 | Holme from Source to New Mill Dike | River | 3097 | Colne and Holme | 3001 | Aire and Calder | RIVER HOLME | Not Applicable | Not Applicable | Not Applicable | 0:15 | 1 | 3.6 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01791
YWS01792 | Yorkshire Water | Live | ST AUGUSTINES AVENUE CSO | ST AUGUSTINES AVENUE/CSO | WRA8469 | WRA8469 | A1 | SO on sewer network | SK3844069970 | 438209 | 370044 | GB104027057630 | Rother from Redleadmill Brook to Spital Brook | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | RIVER ROTHER | Not Applicable | Not Applicable | Not Applicable | 23:15 | 24 | 20.4 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01792
YWS01793 | Yorkshire Water | Live | CROW LANE WORKS CSO | CROW LANE WORKS/CSO | WRA8470 | WRA8470 | 1 | SO on sewer network | SK3887071440 | 438974 | 371443 | GB104027057771 | Rother, Spittal Brook to Doe Lea | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | RIVER ROTHER | Not Applicable | Not Applicable | Not Applicable | 526:30 | 69 | 66.4 | 2020 | 100 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement completed | SOAF investigation ongoing | YWS01793
YWS01794 | Yorkshire Water | Live | BRIMINGTON ROAD CSO | BRIMINGHAM ROAD/CSO | WRA8471 | WRA8471 | A1 | SO on sewer network | SK3877171951 | 438765 | 371951 | GB104027057771 | Rother, Spittal Brook to Doe Lea | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | RIVER ROTHER | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 9.2 | 2020 | 6.14 | Comms failure / issue | Scheduled | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | SOAF investigation completed - operational solution completed | YWS01794
YWS01795 | Yorkshire Water | Live | COACH ROAD BAILDON CSO | COACH ROAD BAILDON/CSO | WRA8472 | WRA8472 | A1 | SO on sewer network | SE1444038140 | 414460 | 438140 | GB104027063034 | Aire (R Worth to Gill Beck) | River | 3307 | Middle Aire | 3001 | Aire and Calder | RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 177:30 | 53 | 51 | 2020 | 99.99 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation completed | No improvement action in reporting period | SOAF investigation completed - No work required | YWS01795
YWS01796 | Yorkshire Water | Live | HIGHER COACH ROAD NO 2 CSO | HIGHER COACH RD/NO 2 CSO | WRA8473 | WRA8473 | A1 | SO on sewer network | SE1398138536 | 413998 | 438241 | GB104027063034 | Aire (R Worth to Gill Beck) | River | 3307 | Middle Aire | 3001 | Aire and Calder | TRIBUTARY OF RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 88:30 | 33 | 37.6 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01796
YWS01797 | Yorkshire Water | Live | VALLEY ROAD SHIPLEY 2 CSO | VALLEY ROAD SHIPLEY/2 CSO | WRA8477 | WRA8477 | A1 | SO on sewer network | SE1528036440 | 415280 | 436440 | GB104027062862 | Bradford Beck (Clayton Bk to R Aire) | River | 3307 | Middle Aire | 3001 | Aire and Calder | BRADFORD BECK | Not Applicable | Not Applicable | Not Applicable | 11:45 | 23 | 37.8 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01797
YWS01798 | Yorkshire Water | Live | POWELL ROAD CSO | POWELL ROAD/NO 2 CSO | WRA8479 | WRA8479 | 1 | SO on sewer network | SE1564035930 | 415640 | 435940 | GB104027062862 | Bradford Beck (Clayton Bk to R Aire) | River | 3307 | Middle Aire | 3001 | Aire and Calder | TRAP SIKE | Not Applicable | Not Applicable | Not Applicable | 4:30 | 11 | 19 | 2020 | 99.97 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01798
YWS01799 | Yorkshire Water | Live | SHEFFIELD ROAD WOODHOUSE NO 2 CSO | SHEFF RD WOODHOUSE/2 CSO | WRA8480 | WRA8480 | A1 | SO on sewer network | SK4114284582 | 441142 | 384582 | GB104027057773 | Shire Brook | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | CLVRT TRIBUTARY OF SHIRE BROOK | Not Applicable | Not Applicable | Not Applicable | 2:15 | 3 | 3.6 | 2020 | 99.91 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01799
YWS01800 | Yorkshire Water | Live | POPLAR ROAD CSO | POPLAR ROAD/CSO | WRA8481 | WRA8481 | 1 | SO on sewer network | SE1526036500 | 415260 | 436510 | GB104027062862 | Bradford Beck (Clayton Bk to R Aire) | River | 3307 | Middle Aire | 3001 | Aire and Calder | BRADFORD BECK | Not Applicable | Not Applicable | Not Applicable | 0:30 | 2 | 1.25 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01800
YWS01801 | Yorkshire Water | Live | BRADFORD BECK 2 CSO | BRADFORD BECK/NO 2 CSO | WRA8482 | WRA8482 | A1 | SO on sewer network | SE1493137046 | 414931 | 437046 | GB104027062862 | Bradford Beck (Clayton Bk to R Aire) | River | 3307 | Middle Aire | 3001 | Aire and Calder | BRADFORD BECK | Not Applicable | Not Applicable | Not Applicable | 16:30 | 13 | 16 | 2020 | 79.64 | Comms failure / issue | Resolved - Jun | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01801
YWS01802 | Yorkshire Water | Live | HIRD STREET NO 2 CSO | HIRD STREET/NO 2 CSO | WRA8483 | WRA8483 | A1 | SO on sewer network | SE1468737916 | 414687 | 437916 | GB104027063032 | Aire from Gill Beck (Baildon) to River Calder | River | 3265 | Lower Aire | 3001 | Aire and Calder | TRIBUTARY OF THE RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 1:15 | 1 | 2.2 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01802
YWS01803 | Yorkshire Water | Live | BIRKENSHAW CSO | BIRKENSHAW/NO 4 CSO | WRA8486 | WRA8486 | 1 | SO on sewer network | SE2112026890 | 421123 | 426892 | GB104027062670 | Batley Beck from Source to River Calder | River | 3268 | Lower Calder | 3001 | Aire and Calder | NUTTER BECK | Not Applicable | Not Applicable | Not Applicable | 80:15 | 12 | 12.4 | 2020 | 99.86 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01803
YWS01804 | Yorkshire Water | Live | PRINCESS BRIDGE NO 2 CSO | PRINCESS BRIDGE/NO 2 CSO | WRA8487 | WRA8487 | A1 | SO on sewer network | SD9947026932 | 399470 | 426932 | GB104027062641 | Calder from Colden Water to Ryburn Confluence | River | 3310 | Middle Calder | 3001 | Aire and Calder | RIVER CALDER | Not Applicable | Not Applicable | Not Applicable | 1168:30 | 116 | 113.2 | 2020 | 99.97 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | Operational investigation ongoing | Operational improvement ongoing | SOAF investigation completed - No work required | YWS01804
YWS01805 | Yorkshire Water | Live | OLD LANE NO 2 CSO | OLD LANE/NO 2 CSO | WRA8488 | WRA8488 | 1 | SO on sewer network | SE2088028160 | 420878 | 428162 | GB104027062670 | Batley Beck from Source to River Calder | River | 3268 | Lower Calder | 3001 | Aire and Calder | WORMALDS DRAIN | Not Applicable | Not Applicable | Not Applicable | 12:15 | 11 | 6 | 2020 | 99.91 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01805
YWS01806 | Yorkshire Water | Live | IVY STREET CSO | IVY STREET/CSO | WRA8489 | WRA8489 | A1 | SO on sewer network | SE1514716495 | 415147 | 416495 | GB104027062550 | Colne from River Holme to River Calder | River | 3097 | Colne and Holme | 3001 | Aire and Calder | RIVER COLNE | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 1.8 | 2020 | 99.91 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01806
YWS01807 | Yorkshire Water | Live | JACKSON BRIDGE NO 2 CSO | JACKSON BRIDGE/NO 2 CSO | WRA8490 | WRA8490 | 1 | SO on sewer network | SE1641007420 | 416413 | 407423 | GB104027057610 | New Mill Dike from Source to River Holme | River | 3097 | Colne and Holme | 3001 | Aire and Calder | JACKSON BRIDGE DYKE | Not Applicable | Not Applicable | Not Applicable | 27:00 | 20 | 14.6 | 2020 | 99.56 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01807
YWS01808 | Yorkshire Water | Live | ESHOLT LANE 291 CSO | ESHOLT LANE 291/CSO | WRA8497 | WRA8497 | A1 | SO on sewer network | SE1792840126 | 417928 | 440126 | GB104027063032 | Aire from Gill Beck (Baildon) to River Calder | River | 3265 | Lower Aire | 3001 | Aire and Calder | RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 10:00 | 6 | 10.8 | 2020 | 94 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01808
YWS01809 | Yorkshire Water | Live | ESHOLT LANE CSO | ESHOLT LANE/NO 1 CSO | WRA8498 | WRA8498 | 1 | SO on sewer network | SE1727039570 | 417270 | 439570 | GB104027063034 | Aire (R Worth to Gill Beck) | River | 3307 | Middle Aire | 3001 | Aire and Calder | RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 210:15 | 67 | 62.6 | 2020 | 99.72 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS01809
YWS01810 | Yorkshire Water | Live | ESHOLT LANE CSO | ESHOLT LANE/NO 2 CSO | WRA8498 | WRA8498 | 2 | SO on sewer network | SE1727039570 | 417270 | 439570 | GB104027063034 | Aire (R Worth to Gill Beck) | River | 3307 | Middle Aire | 3001 | Aire and Calder | RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0 | 2020 | 99.91 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01810
YWS01811 | Yorkshire Water | Live | BROADFIELD ROAD CSO | BROADFIELD ROAD/CSO | WRA8499 | WRA8499 | A1 | SO on sewer network | SK3470084800 | 434762 | 384768 | GB104027057750 | Sheaf from Source to River Don | River | 3312 | Middle Don | 3029 | Don and Rother | RIVER SHEAF | Not Applicable | Not Applicable | Not Applicable | 96:45 | 27 | 40.2 | 2020 | 99.51 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | No investigation activity in reporting period | No improvement action in reporting period | SOAF investigation completed - No work required | YWS01811
YWS01812 | Yorkshire Water | Live | LEYBURN ROAD SHEFFIELD NO2 CSO | LEYBURN RD SHEFFLD/2 CSO | WRA8500 | WRA8500 | A1 | SO on sewer network | SK3459384631 | 434593 | 384631 | GB104027057750 | Sheaf from Source to River Don | River | 3312 | Middle Don | 3029 | Don and Rother | RIVER SHEAF | Not Applicable | Not Applicable | Not Applicable | 115:30 | 41 | 37.4 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01812
YWS01813 | Yorkshire Water | Live | CANAL ROAD CSO | CANAL ROAD/CSO | WRA8501 | WRA8501 | A1 | SO on sewer network | SE2774134099 | 427741 | 434099 | GB104027063032 | Aire from Gill Beck (Baildon) to River Calder | River | 3265 | Lower Aire | 3001 | Aire and Calder | RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 10:15 | 18 | 19.2 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01813
YWS01814 | Yorkshire Water | Live | CATCHBAR LANE CSO | CATCHBAR LANE/CSO | WRA8504 | WRA8504 | A1 | SO on sewer network | SK3309290625 | 433092 | 390625 | GB104027057411 | Don from Little Don to River Loxley confluence | River | 3490 | Upper Don | 3029 | Don and Rother | CLVRT TRIB OF RIVER DON | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01814
YWS01815 | Yorkshire Water | Live | REDBROOK ROAD CSO | REDBROOK ROAD/CSO | WRA8507 | WRA8507 | A1 | SO on sewer network | SE3216007740 | 432165 | 407744 | GB104027063171 | Dearne from Cawthorne Dyke to Lundwood STW | River | 3125 | Dearne | 3029 | Don and Rother | RED BROOK | Not Applicable | Not Applicable | Not Applicable | 154:30 | 48 | 21.4 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01815
YWS01816 | Yorkshire Water | Live | HOLME LANE CSO | HOLME LANE SHEFFIELD/CSO | WRA8509 | WRA8509 | A1 | SO on sewer network | SK3342589701 | 433425 | 389701 | GB104027057370 | Loxley from Strines Dyke to River Don | River | 3490 | Upper Don | 3029 | Don and Rother | RIVER LOXLEY | Not Applicable | Not Applicable | Not Applicable | 15:30 | 21 | 35.4 | 2020 | 99.86 |  |  | High spill threshold not met | High spill threshold not met | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01816
YWS01817 | Yorkshire Water | Live | DANESMOOR NO 3 CSO | DANESMOOR/NO 3 CSO | WRA8510 | WRA8510 | 1 | SO on sewer network | SK4047062810 | 440470 | 362819 | GB104027052280 | Rother from Source to Redleadmill Brook | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | TRIBUTARY OF THE RIVER ROTHER | Not Applicable | Not Applicable | Not Applicable | 200:15 | 29 | 38.4 | 2020 | 76.34 | Sensor failure / issue | Resolved - Mar | High spill threshold not met | High spill threshold not met | Operational investigation completed | No improvement action in reporting period | No SOAF investigation required | YWS01817
YWS01818 | Yorkshire Water | Live | CLAYTON STREET SOUTH CSO | CLAYTON STREET/NO 2 CSO | WRA8512 | WRA8512 | 1 | SO on sewer network | SK3885070760 | 438852 | 370759 | GB104027057771 | Rother, Spittal Brook to Doe Lea | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | RIVER ROTHER | Not Applicable | Not Applicable | Not Applicable | 8:45 | 1 | 1.2 | 2020 | 97.65 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01818
YWS01819 | Yorkshire Water | Live | POTTERY LANE EAST CSO | POTTERY LANE EAST/CSO | WRA8513 | WRA8513 | A1 | SO on sewer network | SK3874473251 | 438744 | 373251 | GB104027057771 | Rother, Spittal Brook to Doe Lea | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | RIVER ROTHER | Not Applicable | Not Applicable | Not Applicable | 177:45 | 51 | 45.2 | 2020 | 99.9 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS01819
YWS01820 | Yorkshire Water | Live | HOLME LANE SYPTE CSO | HOLME LANE SYPTE/CSO | WRA8514 | WRA8514 | A1 | SO on sewer network | SK3279989335 | 432799 | 389335 | GB104027057370 | Loxley from Strines Dyke to River Don | River | 3490 | Upper Don | 3029 | Don and Rother | RIVER LOXLEY | Not Applicable | Not Applicable | Not Applicable | 7:00 | 10 | 25.8 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01820
YWS01821 | Yorkshire Water | Live | CLOUGHS MILL NO 2 CSO | CLOUGHS MILL/NO 2 CSO | WRA8515 | WRA8515 | A1 | SO on sewer network | SE0545639682 | 405456 | 439682 | GB104027062891 | Worth from Bridgehouse Beck to R Aire | River | 3307 | Middle Aire | 3001 | Aire and Calder | RIVER WORTH | Not Applicable | Not Applicable | Not Applicable | 160:30 | 15 | 3.2 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01821
YWS01822 | Yorkshire Water | Live | WHITELEY WOODS CSO | WHITELEY WOODS/CSO | WRA8517 | WRA8517 | A1 | SO on sewer network | SK3214585886 | 432145 | 385886 | GB104027057760 | Porter from Source to River Sheaf | River | 3312 | Middle Don | 3029 | Don and Rother | PORTER BROOK | Not Applicable | Not Applicable | Not Applicable | 86:15 | 32 | 37.4 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01822
YWS01823 | Yorkshire Water | Live | GIBSON LANE NO 2 CSO | GIBSON LANE/NO 2 CSO | WRA8520 | WRA8520 | A1 | SO on sewer network | SK2699298596 | 426992 | 398596 | GB104027057460 | Little Don from Source to River Don | River | 3490 | Upper Don | 3029 | Don and Rother | LITTLE DON RIVER | Not Applicable | Not Applicable | Not Applicable | 69:00 | 54 | 53.4 | 2020 | 81.7 | Comms failure / issue | Resolved - Nov | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01823
YWS01824 | Yorkshire Water | Live | MANCHESTER ROAD GARAGE CSO | MANCHESTER RD GARAGE/CSO | WRA8521 | WRA8521 | A1 | SO on sewer network | SK2902997973 | 429029 | 397973 | GB104027057460 | Little Don from Source to River Don | River | 3490 | Upper Don | 3029 | Don and Rother | THE PORTER OR LITTLE DON RIVER | Not Applicable | Not Applicable | Not Applicable | 3:30 | 3 | 4 | 2020 | 95.2 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01824
YWS01825 | Yorkshire Water | Live | MANCHESTER ROAD WEIR CSO | MANCHESTER ROAD WEIR/CSO | WRA8523 | WRA8523 | A1 | SO on sewer network | SK2848398153 | 428483 | 398153 | GB104027057460 | Little Don from Source to River Don | River | 3490 | Upper Don | 3029 | Don and Rother | THE PORTER OR LITTLE DON RIVER | Not Applicable | Not Applicable | Not Applicable | 695:15 | 104 | 97.6 | 2020 | 100 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | Operational investigation completed | No improvement action in reporting period | SOAF investigation completed - No work required | YWS01825
YWS01826 | Yorkshire Water | Live | HUNSHELF ROAD NO 2 CSO | HUNSHELF ROAD/NO 2 CSO | WRA8524 | WRA8524 | A1 | SO on sewer network | SK2730498452 | 427304 | 398452 | GB104027057460 | Little Don from Source to River Don | River | 3490 | Upper Don | 3029 | Don and Rother | LITTLE DON RIVER | Not Applicable | Not Applicable | Not Applicable | 461:15 | 86 | 55 | 2020 | 96.47 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01826
YWS01827 | Yorkshire Water | Live | FIELD LANE | BATLEY FIELD LANE/CSO | WRA8526 | WRA8526 | 1 | SO on sewer network | SE2446023980 | 424468 | 423986 | GB104027062670 | Batley Beck from Source to River Calder | River | 3268 | Lower Calder | 3001 | Aire and Calder | TRIBUTARY OF BATLEY BECK | Not Applicable | Not Applicable | Not Applicable | 0:30 | 1 | 0.2 | 2020 | 99.89 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01827
YWS01828 | Yorkshire Water | Live | KIRK LANE NO 1 CSO | KIRK LANE/NO 1 CSO | WRA8527 | WRA8527 | A1 | SO on sewer network | SE1956041350 | 419560 | 441350 | GB104027062910 | Gill Beck Guisley from Source to River Aire | River | 3265 | Lower Aire | 3001 | Aire and Calder | NUN ROYD BECK | Not Applicable | Not Applicable | Not Applicable | 51:30 | 40 | 41 | 2020 | 99.77 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01828
YWS01829 | Yorkshire Water | Live | HEALEY ROAD OSSETT CSO | HEALEY ROAD OSSETT/CSO | WRA8528 | WRA8528 | A1 | SO on sewer network | SE2703919166 | 427039 | 419166 | GB104027062631 | Calder from River Colne to River Chald | River | 3268 | Lower Calder | 3001 | Aire and Calder | RIVER CALDER | Not Applicable | Not Applicable | Not Applicable | 189:45 | 66 | 51.4 | 2020 | 99.96 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01829
YWS01830 | Yorkshire Water | Live | WELL LANE CSO | WELL LANE/CSO | WRA8530 | WRA8530 | 1 | SO on sewer network | SE2469023181 | 424690 | 423188 | GB104027062670 | Batley Beck from Source to River Calder | River | 3268 | Lower Calder | 3001 | Aire and Calder | BATLEY BECK | Not Applicable | Not Applicable | Not Applicable | 1:00 | 2 | 3 | 2020 | 86.3 | Comms failure / issue | Resolved - Mar | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01830
YWS01831 | Yorkshire Water | Live | HEADINGLEY STATION CSO | HEADINGLEY STATION/CSO | WRA8532 | WRA8532 | A1 | SO on sewer network | SE2674035798 | 426740 | 435798 | GB104027063032 | Aire from Gill Beck (Baildon) to River Calder | River | 3265 | Lower Aire | 3001 | Aire and Calder | CULVERTED TRIB OF RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 29:26 | 29 | 32.8 | 2020 | 92.48 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01831
YWS01832 | Yorkshire Water | Live | VESPER ROAD CSO | VESPER ROAD/CSO | WRA8533 | WRA8533 | A1 | SO on sewer network | SE2605036637 | 426050 | 436637 | GB104027063032 | Aire from Gill Beck (Baildon) to River Calder | River | 3265 | Lower Aire | 3001 | Aire and Calder | CULVERTED TRIB OF RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 48:50 | 53 | 33.8 | 2020 | 97.71 |  |  | High spill threshold not met | High spill threshold not met | Operational investigation completed | No improvement action in reporting period | No SOAF investigation required | YWS01832
YWS01833 | Yorkshire Water | Live | SPEN LANE 184 CSO | SPEN LANE 184/CSO | WRA8534 | WRA8534 | A1 | SO on sewer network | SE2609736717 | 426097 | 436717 | GB104027063032 | Aire from Gill Beck (Baildon) to River Calder | River | 3265 | Lower Aire | 3001 | Aire and Calder | CULVERTED TRIB OF RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 4:22 | 7 | 39.4 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01833
YWS01834 | Yorkshire Water | Live | MORRIS LANE CSO | MORRIS LANE/CSO | WRA8535 | WRA8535 | A1 | SO on sewer network | SE2600035560 | 426000 | 435560 | GB104027063032 | Aire from Gill Beck (Baildon) to River Calder | River | 3265 | Lower Aire | 3001 | Aire and Calder | CULVERTED TRIB OF RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 366:24 | 73 | 15 | 2020 | 99.99 |  |  | N/A - Ongoing investigation | High spill threshold not met | UWWTR investigation ongoing, Operational investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01834
YWS01835 | Yorkshire Water | Live | LONDESBOROUGH PARK SPS | LONDESBOROUGH PARK/CSO | WRA8538 | WRA8538 | A2 | SO on sewer network | SE8714445128 | 487144 | 445128 | GB104026066720 | Foulness from Source to Black Beck (South) | River | 3191 | Foulness | 3039 | Hull and East Riding | TRIBUTARY OF TOWTHORPE BECK | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0.2 | 2020 | 99.95 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01835
YWS01836 | Yorkshire Water | Live | VICTORIA GARDENS CSO | VICTORIA GARDENS/CSO | WRA8539 | WRA8539 | A1 | SO on sewer network | SE2386036940 | 423866 | 436949 | GB104027063032 | Aire from Gill Beck (Baildon) to River Calder | River | 3265 | Lower Aire | 3001 | Aire and Calder | RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 4:45 | 8 | 6.4 | 2020 | 99.82 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01836
YWS01837 | Yorkshire Water | Live | TOWN STREET RODLEY CSO | TOWN STREET RODLEY/CSO | WRA8540 | WRA8540 | A1 | SO on sewer network | SE2232836359 | 422328 | 436359 | GB104027063032 | Aire from Gill Beck (Baildon) to River Calder | River | 3265 | Lower Aire | 3001 | Aire and Calder | BAGLEY BECK | Not Applicable | Not Applicable | Not Applicable | 0:30 | 1 | 0.4 | 2020 | 99.76 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01837
YWS01838 | Yorkshire Water | Live | WHITECOTE RISE CSO | WHITECOTE RISE/CSO | WRA8541 | WRA8541 | 1 | SO on sewer network | SE2377035630 | 423525 | 435881 | GB104027063032 | Aire from Gill Beck (Baildon) to River Calder | River | 3265 | Lower Aire | 3001 | Aire and Calder | TRIBUTARY OF THE RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 0:15 | 1 | 0.6 | 2020 | 99.77 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01838
YWS01839 | Yorkshire Water | Live | JACK LANE CSO | JACK LANE/CSO | WRA8543 | WRA8543 | A1 | SO on sewer network | SE3216031220 | 432160 | 431220 | GB104027063032 | Aire from Gill Beck (Baildon) to River Calder | River | 3265 | Lower Aire | 3001 | Aire and Calder | AIRE AND CALDER NAVIGATION | Not Applicable | Not Applicable | Not Applicable | 391:15 | 115 | 71.5 | 2020 | 99.75 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation ongoing | Operational improvement ongoing | SOAF investigation ongoing | YWS01839
YWS01840 | Yorkshire Water | Live | JACK LANE CSO | OLD RUN ROAD/CSO | WRA8543 | EPR/ZB3593EG | A1 | SO on sewer network | SE3216031220 | 432160 | 431220 | GB104027063032 | Aire from Gill Beck (Baildon) to River Calder | River | 3265 | Lower Aire | 3001 | Aire and Calder | AIRE AND CALDER NAVIGATION | Not Applicable | Not Applicable | Not Applicable | 6:15 | 12 | 9.4 | 2020 | 99.6 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01840
YWS01841 | Yorkshire Water | Live | JACK LANE CSO | WESTLAND ROAD/CSO | WRA8543 | EPR/SB3499DT | A1 | SO on sewer network | SE3216031220 | 432160 | 431220 | GB104027063032 | Aire from Gill Beck (Baildon) to River Calder | River | 3265 | Lower Aire | 3001 | Aire and Calder | AIRE AND CALDER NAVIGATION | Not Applicable | Not Applicable | Not Applicable | 10:15 | 17 | 17 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01841
YWS01842 | Yorkshire Water | Live | JACK LANE CSO | MIDDLETON GROVE/CSO | WRA8543 | EPR/SB3499RQ | A1 | SO on sewer network | SE3216031220 | 432160 | 431220 | GB104027063032 | Aire from Gill Beck (Baildon) to River Calder | River | 3265 | Lower Aire | 3001 | Aire and Calder | AIRE AND CALDER NAVIGATION | Not Applicable | Not Applicable | Not Applicable | 24:45 | 18 | 4 | 2020 | 99.78 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01842
YWS01843 | Yorkshire Water | Live | JACK LANE CSO | SUSSEX AVENUE/CSO | WRA8543 | EPR/SB3499VL | A1 | SO on sewer network | SE3216031220 | 432160 | 431220 | GB104027063032 | Aire from Gill Beck (Baildon) to River Calder | River | 3265 | Lower Aire | 3001 | Aire and Calder | AIRE AND CALDER NAVIGATION | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01843
YWS01844 | Yorkshire Water | Live | JACK LANE CSO | THE WELLINGTON/CSO | WRA8543 | EPR/SB3499WM | A1 | SO on sewer network | SE3216031220 | 432160 | 431220 | GB104027063032 | Aire from Gill Beck (Baildon) to River Calder | River | 3265 | Lower Aire | 3001 | Aire and Calder | AIRE AND CALDER NAVIGATION | Not Applicable | Not Applicable | Not Applicable | 3:45 | 6 | 5.8 | 2020 | 99.39 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01844
YWS01845 | Yorkshire Water | Live | JACK LANE CSO | MEADOW ROAD/CSO | WRA8543 | EPR/SB3590AN | A1 | SO on sewer network | SE3216031220 | 432160 | 431220 | GB104027063032 | Aire from Gill Beck (Baildon) to River Calder | River | 3265 | Lower Aire | 3001 | Aire and Calder | AIRE AND CALDER NAVIGATION | Not Applicable | Not Applicable | Not Applicable |  |  | 5.25 | 2020 | 0 | Sensor failure / issue | Scheduled | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01845
YWS01846 | Yorkshire Water | Live | SOUTH DRIVE NO 2 CSO | SOUTH DRIVE/NO 2 CSO | WRA8551 | WRA8551 | A1 | SO on sewer network | SE2156834980 | 421568 | 434980 | GB104027063032 | Aire from Gill Beck (Baildon) to River Calder | River | 3265 | Lower Aire | 3001 | Aire and Calder | TRIBUTARY OF BAGLEY BECK | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 3 | 2020 | 95.51 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01846
YWS01847 | Yorkshire Water | Live | UPPER ROAD CSO | UPPER ROAD/NO 2 CSO | WRA8553 | WRA8553 | A1 | SO on sewer network | SE2376022830 | 423760 | 422830 | GB104027062670 | Batley Beck from Source to River Calder | River | 3268 | Lower Calder | 3001 | Aire and Calder | BATLEY CARR DYKE CULVERTED | Not Applicable | Not Applicable | Not Applicable | 10:30 | 11 | 13.8 | 2020 | 93.42 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01847
YWS01848 | Yorkshire Water | Live | WARWICK ROAD NO2 CSO | WARWICK ROAD/NO 2 CSO | WRA8554 | WRA8554 | A1 | SO on sewer network | SE2469123182 | 424691 | 423182 | GB104027062670 | Batley Beck from Source to River Calder | River | 3268 | Lower Calder | 3001 | Aire and Calder | BATLEY BECK | Not Applicable | Not Applicable | Not Applicable | 173:15 | 70 | 66.6 | 2020 | 100 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement completed | SOAF investigation ongoing | YWS01848
YWS01849 | Yorkshire Water | Live | WILLOW ROAD CSO | WILLOW ROAD/CSO | WRA8555 | WRA8555 | A1 | SO on sewer network | SE2793034100 | 427930 | 434109 | GB104027063032 | Aire from Gill Beck (Baildon) to River Calder | River | 3265 | Lower Aire | 3001 | Aire and Calder | RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 69:30 | 37 | 43.2 | 2020 | 100 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01849
YWS01850 | Yorkshire Water | Live | WILLOW ROAD CSO | BURLEY LODGE ROAD/CSO | WRA8555 | EPR/RB3792NH | A1 | SO on sewer network | SE2793034100 | 427930 | 434109 | GB104027063032 | Aire from Gill Beck (Baildon) to River Calder | River | 3265 | Lower Aire | 3001 | Aire and Calder | RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 62:45 | 27 | 25.6 | 2020 | 76.14 | Comms failure / issue | Scheduled | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01850
YWS01851 | Yorkshire Water | Live | WILLOW ROAD CSO | THORNVILLE ROAD/CSO | WRA8555 | EPR/RB3792WR | A1 | SO on sewer network | SE2793034100 | 427930 | 434109 | GB104027063032 | Aire from Gill Beck (Baildon) to River Calder | River | 3265 | Lower Aire | 3001 | Aire and Calder | RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 0:45 | 3 | 4 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01851
YWS01852 | Yorkshire Water | Live | COLNE ROAD CSO | COLNE ROAD/CSO | WRA8557 | WRA8557 | A1 | SO on sewer network | SE1503716169 | 415037 | 416169 | GB104027062550 | Colne from River Holme to River Calder | River | 3097 | Colne and Holme | 3001 | Aire and Calder | RIVER COLNE | Not Applicable | Not Applicable | Not Applicable | 13:30 | 9 | 7 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01852
YWS01853 | Yorkshire Water | Live | NEWLAY LANE 266 CSO | NEWLAY LANE 266/CSO | WRA8559 | WRA8559 | A1 | SO on sewer network | SE2386636949 | 423866 | 436949 | GB104027063032 | Aire from Gill Beck (Baildon) to River Calder | River | 3265 | Lower Aire | 3001 | Aire and Calder | RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 5:30 | 9 | 3 | 2020 | 97.93 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01853
YWS01854 | Yorkshire Water | Live | CLAREMONT 271 CSO | CLAREMONT 271/CSO | WRA8560 | WRA8560 | A1 | SO on sewer network | SE2386636949 | 423866 | 436949 | GB104027063032 | Aire from Gill Beck (Baildon) to River Calder | River | 3265 | Lower Aire | 3001 | Aire and Calder | RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 12:45 | 12 | 26.8 | 2020 | 99.41 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01854
YWS01855 | Yorkshire Water | Live | ST AUGUSTINES DRIVE CSO | ST AUGUSTINES DRIVE/CSO | WRA8565 | WRA8565 | 1 | SO on sewer network | SK3844069971 | 438053 | 370068 | GB104027057630 | Rother from Redleadmill Brook to Spital Brook | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | RIVER ROTHER | Not Applicable | Not Applicable | Not Applicable | 5:30 | 12 | 14.8 | 2020 | 99.68 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01855
YWS01856 | Yorkshire Water | Live | CALVERLEY EAST NO 2 CSO | CALVERLEY EAST/NO 2 CSO | WRA8566 | WRA8566 | A1 | SO on sewer network | SE2098337084 | 420983 | 437084 | GB70410231 | Leeds and Liverpool Canal, summit to Leeds | Canal | 2031 | Leeds and Liverpool Canal | 2001 | Humber AWB | LEEDS & LIVERPOOL CANAL | Not Applicable | Not Applicable | Not Applicable | 95:15 | 56 | 52.4 | 2020 | 70.35 | Comms failure / issue | Resolved - Aug | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01856
YWS01857 | Yorkshire Water | Live | THORNHILL DEWSBURY NO1 CSO | THORNHILL DEWSBURY/1 CSO | WRA8568 | WRA8568 | A1 | SO on sewer network | SE2548920237 | 425489 | 420237 | GB104027062631 | Calder from River Colne to River Chald | River | 3268 | Lower Calder | 3001 | Aire and Calder | RIVER CALDER | Not Applicable | Not Applicable | Not Applicable | 218:15 | 41 | 51.5 | 2020 | 99.96 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01857
YWS01858 | Yorkshire Water | Live | THISTLE STREET CSO | THISTLE STREET/CSO | WRA8569 | WRA8569 | A1 | SO on sewer network | SE1521817544 | 415218 | 417544 | GB104027062550 | Colne from River Holme to River Calder | River | 3097 | Colne and Holme | 3001 | Aire and Calder | RIVER COLNE | Not Applicable | Not Applicable | Not Applicable | 235:30 | 66 | 64 | 2020 | 99.98 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01858
YWS01859 | Yorkshire Water | Live | OSSETT WAKEFIELD ROAD 2 CSO | OSSETT WAKEFIELD RD/2 CSO | WRA8570 | WRA8570 | A1 | SO on sewer network | SE2844621111 | 428446 | 421111 | GB104027062620 | Chald from Source to River Calder | River | 3268 | Lower Calder | 3001 | Aire and Calder | CLVRT TRIB SPRINGFIELD BECK | Not Applicable | Not Applicable | Not Applicable | 1:00 | 3 | 7.8 | 2020 | 99.5 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01859
YWS01860 | Yorkshire Water | Live | ALBION MILLS CSO | ALBION MILLS/CSO | WRA8571 | WRA8571 | A1 | SO on sewer network | SE2858917934 | 428589 | 417934 | GB104027062631 | Calder from River Colne to River Chald | River | 3268 | Lower Calder | 3001 | Aire and Calder | RIVER CALDER | Not Applicable | Not Applicable | Not Applicable | 379:15 | 55 | 86.4 | 2020 | 100 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01860
YWS01861 | Yorkshire Water | Live | PILDACRE LANE CSO | PILDACRE LANE/NO 2 CSO | WRA8572 | WRA8572 | A1 | SO on sewer network | SE2653920667 | 426539 | 420667 | GB104027062631 | Calder from River Colne to River Chald | River | 3268 | Lower Calder | 3001 | Aire and Calder | PILDACRE MILL BECK | Not Applicable | Not Applicable | Not Applicable | 82:30 | 35 | 40.4 | 2020 | 99.94 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01861
YWS01862 | Yorkshire Water | Live | HOUGHSIDE ROAD CSO | HOUGH SIDE/CSO | WRA8575 | WRA8575 | A1 | SO on sewer network | SE2310733317 | 423110 | 433311 | GB104027062830 | Low/Wortley/Pudsey Bks | River | 3265 | Lower Aire | 3001 | Aire and Calder | TRIBUTARY OF PUDESY BECK | Not Applicable | Not Applicable | Not Applicable | 34:15 | 24 | 41.5 | 2020 | 80.3 | Sensor failure / issue | Resolved - May | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01862
YWS01863 | Yorkshire Water | Live | STANNINGLEY CSO | STANNINGLEY/CSO | WRA8576 | WRA8576 | A1 | SO on sewer network | SE2202334371 | 422023 | 434371 | GB104027062830 | Low/Wortley/Pudsey Bks | River | 3265 | Lower Aire | 3001 | Aire and Calder | FARSLEY BECK (CULVERTED) | Not Applicable | Not Applicable | Not Applicable | 76:00 | 54 | 53.8 | 2020 | 100 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01863
YWS01864 | Yorkshire Water | Live | FRASER AVENUE NO 2 CSO | FRASER AVENUE/NO 2 CSO | WRA8577 | WRA8577 | A1 | SO on sewer network | SE2299037650 | 423010 | 437673 | GB104027063032 | Aire from Gill Beck (Baildon) to River Calder | River | 3265 | Lower Aire | 3001 | Aire and Calder | TRIBUTARY OF RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 21:45 | 20 | 25.4 | 2020 | 69.29 | Sensor failure / issue | Resolved - Oct | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01864
YWS01865 | Yorkshire Water | Live | GAWTHORPE MAIN STREET CSO | GAWTHORPE MAIN ST/CSO | WRA8578 | WRA8578 | A1 | SO on sewer network | SE2766222211 | 427662 | 422211 | GB104027062631 | Calder from River Colne to River Chald | River | 3268 | Lower Calder | 3001 | Aire and Calder | TRIBUTARY OF BUSHY BECK | Not Applicable | Not Applicable | Not Applicable | 0:45 | 3 | 3 | 2020 | 94.72 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01865
YWS01866 | Yorkshire Water | Live | CHARLES STREET NO 2 CSO | CHARLES STREET/NO 2 CSO | WRA8579 | WRA8579 | A1 | SO on sewer network | SE3042117474 | 430421 | 417474 | GB104027062631 | Calder from River Colne to River Chald | River | 3268 | Lower Calder | 3001 | Aire and Calder | OLD MILL STREAM | Not Applicable | Not Applicable | Not Applicable | 40:15 | 13 | 15.4 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01866
YWS01867 | Yorkshire Water | Live | OSSETT TOWNGATE NO 2 CSO | OSSETT TOWNGATE/NO 2 CSO | WRA8580 | WRA8580 | A1 | SO on sewer network | SE2873620541 | 428736 | 420541 | GB104027062620 | Chald from Source to River Calder | River | 3268 | Lower Calder | 3001 | Aire and Calder | SPRING MILL BECK | Not Applicable | Not Applicable | Not Applicable | 8:00 | 12 | 12 | 2020 | 99.98 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01867
YWS01868 | Yorkshire Water | Live | DERWENT ROAD NO 2 CSO | DERWENT ROAD/NO 2 CSO | WRA8582 | WRA8582 | A1 | SO on sewer network | SE3150020900 | 431518 | 420950 | GB104027062620 | Chald from Source to River Calder | River | 3268 | Lower Calder | 3001 | Aire and Calder | ALVERTHORPE BECK | Not Applicable | Not Applicable | Not Applicable | 3:30 | 6 | 7.4 | 2020 | 99.85 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01868
YWS01869 | Yorkshire Water | Live | FLANSHAW ROAD CSO | FLANSHAW ROAD/CSO | WRA8583 | WRA8583 | A1 | SO on sewer network | SE3138220938 | 431382 | 420938 | GB104027062620 | Chald from Source to River Calder | River | 3268 | Lower Calder | 3001 | Aire and Calder | ALVERTHORPE BECK | Not Applicable | Not Applicable | Not Applicable | 10:45 | 15 | 18.8 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01869
YWS01870 | Yorkshire Water | Live | BROADLEA HILL CSO | BROADLEA HILL/CSO | WRA8584 | WRA8584 | A1 | SO on sewer network | SE2533035968 | 425330 | 435968 | GB104027063032 | Aire from Gill Beck (Baildon) to River Calder | River | 3265 | Lower Aire | 3001 | Aire and Calder | TRIBUTARY OF THE RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0 | 2020 | 95.28 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01870
YWS01871 | Yorkshire Water | Live | TOWNGATE NO 2 CSO | TOWNGATE/NO 2 CSO | WRA8585 | WRA8585 | A1 | SO on sewer network | SE1548339698 | 415483 | 439698 | GB104027063034 | Aire (R Worth to Gill Beck) | River | 3307 | Middle Aire | 3001 | Aire and Calder | BARNSLEY BECK | Not Applicable | Not Applicable | Not Applicable | 1:00 | 2 | 3 | 2020 | 89.65 | Comms failure / issue | Scheduled | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01871
YWS01872 | Yorkshire Water | Live | LEYMOOR ROAD CSO | LEYMOOR ROAD/CSO | WRA8587 | WRA8587 | A1 | SO on sewer network | SE1086316644 | 410863 | 416644 | GB104027063330 | Colne from Wessenden Brook to R Holme | River | 3097 | Colne and Holme | 3001 | Aire and Calder | LONGWOOD BROOK | Not Applicable | Not Applicable | Not Applicable | 211:30 | 85 | 63.8 | 2020 | 99.42 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | Operational investigation completed | No improvement action in reporting period | SOAF investigation completed - No work required | YWS01872
YWS01873 | Yorkshire Water | Live | MORLEY LANE CSO | MORLEY LANE/CSO | WRA8588 | WRA8588 | A1 | SO on sewer network | SE1152815933 | 411528 | 415933 | GB104027063330 | Colne from Wessenden Brook to R Holme | River | 3097 | Colne and Holme | 3001 | Aire and Calder | RIVER COLNE | Not Applicable | Not Applicable | Not Applicable | 43:45 | 33 | 47.8 | 2020 | 97.22 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | No investigation activity in reporting period | No improvement action in reporting period | SOAF investigation completed - No work required | YWS01873
YWS01874 | Yorkshire Water | Live | BROOM MILLS CSO | BROOM MILLS/CSO | WRA8589 | WRA8589 | A1 | SO on sewer network | SE2238235440 | 422382 | 435440 | GB104027063032 | Aire from Gill Beck (Baildon) to River Calder | River | 3265 | Lower Aire | 3001 | Aire and Calder | BAGLEY BECK CULVERTED | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0 | 2020 | 99.95 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01874
YWS01875 | Yorkshire Water | Live | FULNECK CSO | FULNECK/CSO | WRA8590 | WRA8590 | A1 | SO on sewer network | SE2231834862 | 422318 | 434862 | GB104027063032 | Aire from Gill Beck (Baildon) to River Calder | River | 3265 | Lower Aire | 3001 | Aire and Calder | FARSLEY BECK | Not Applicable | Not Applicable | Not Applicable | 1:45 | 2 | 10.6 | 2020 | 99.93 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01875
YWS01876 | Yorkshire Water | Live | CARR FORGE ROAD CSO | CARR FORGE ROAD/CSO | WRA8594 | WRA8594 | A1 | SO on sewer network | SK4210283911 | 442102 | 383911 | GB104027057773 | Shire Brook | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | TRIBUTARY OF SHIRE BROOK | Not Applicable | Not Applicable | Not Applicable | 9:30 | 13 | 12.6 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01876
YWS01877 | Yorkshire Water | Live | SWINTON ROAD CSO | SWINTON ROAD/CSO | WRA8600 | WRA8600 | A1 | SO on sewer network | SK4753799599 | 447537 | 399599 | GB104027057452 | Don from River Rother to River Dearne | River | 3312 | Middle Don | 3029 | Don and Rother | RIVER DON VIA PUBIC SEWER | Not Applicable | Not Applicable | Not Applicable | 83:30 | 39 | 34.6 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01877
YWS01878 | Yorkshire Water | Live | BRITAIN STREET CSO | BRITAIN STREET/CSO | WRA8601 | WRA8601 | A1 | SO on sewer network | SK4753099590 | 447537 | 399599 | GB104027057452 | Don from River Rother to River Dearne | River | 3312 | Middle Don | 3029 | Don and Rother | RIVER DON VIA PUBLIC SEWER | Not Applicable | Not Applicable | Not Applicable | 189:45 | 54 | 74.2 | 2020 | 100 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation completed, Operational investigation completed | No improvement action in reporting period | SOAF investigation completed - No work required | YWS01878
YWS01879 | Yorkshire Water | Live | CROSLAND ST/BLACKMOORFOOT RD CSO | BLACKMOORFOOT ROAD/HLR | WRA8603 | WRA8603 | A1 | SO on sewer network | SE1328016060 | 413280 | 416060 | GB104027063330 | Colne from Wessenden Brook to R Holme | River | 3097 | Colne and Holme | 3001 | Aire and Calder | RIVER COLNE | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0.2 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01879
YWS01880 | Yorkshire Water | Live | CROSLAND ST/BLACKMOORFOOT RD CSO | CROSLAND STREET/HLR | WRA8603 | EPR/AP3729PX | A1 | SO on sewer network | SE1328016060 | 413280 | 416060 | GB104027063330 | Colne from Wessenden Brook to R Holme | River | 3097 | Colne and Holme | 3001 | Aire and Calder | RIVER COLNE | Not Applicable | Not Applicable | Not Applicable | 15:15 | 27 | 18.8 | 2020 | 99.97 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01880
YWS01881 | Yorkshire Water | Live | SEAGRAVE CRESCENT 2 CSO | SEAGRAVE CRESCENT/2 CSO | WRA8608 | WRA8608 | A1 | SO on sewer network | SK3851483411 | 438514 | 383411 | GB104027057773 | Shire Brook | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | SHIRE BROOK | Not Applicable | Not Applicable | Not Applicable | 54:45 | 29 | 40.8 | 2020 | 99.99 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01881
YWS01882 | Yorkshire Water | Live | NETTLETON HILL CSO | NETTLETON HILL/CSO | WRA8609 | WRA8609 | 1 | SO on sewer network | SE0942016640 | 410864 | 416642 | GB104027063330 | Colne from Wessenden Brook to R Holme | River | 3097 | Colne and Holme | 3001 | Aire and Calder | CLAY WOOD BROOK | Not Applicable | Not Applicable | Not Applicable |  |  | 0 | 2020 | 0 | Sensor failure / issue | Scheduled | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01882
YWS01883 | Yorkshire Water | Live | DARTON CHURCH STREET CSO | DARTON CHURCH ST/NO 2 CSO | WRA8610 | WRA8610 | A1 | SO on sewer network | SE3131710026 | 431317 | 410026 | GB104027063260 | Dearne from Bentley Brook to Cawthorne Dyke | River | 3125 | Dearne | 3029 | Don and Rother | RIVER DEARNE | Not Applicable | Not Applicable | Not Applicable | 68:30 | 42 | 43.6 | 2020 | 99.98 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01883
YWS01884 | Yorkshire Water | Live | HALL TERRACE CLAY CROSS & HIGH HAZE | HALL TERRACE/CSO | WRA8620 | EPR/AP3820PN | A1 | SO on sewer network | SK4037064190 | 440370 | 364190 | GB104027052280 | Rother from Source to Redleadmill Brook | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | RIVER ROTHER | Not Applicable | Not Applicable | Not Applicable | 26:30 | 25 | 27 | 2020 | 98.43 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01884
YWS01885 | Yorkshire Water | Live | HALL TERRACE CLAY CROSS & HIGH HAZE | HIGH HAZEL COURT/CSO | WRA8620 | WRA8620 | 3 | SO on sewer network | SK4037064190 | 440370 | 364190 | GB104027052280 | Rother from Source to Redleadmill Brook | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | RIVER ROTHER | Not Applicable | Not Applicable | Not Applicable | 124:00 | 52 | 23.8 | 2020 | 96.12 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01885
YWS01886 | Yorkshire Water | Live | HOOK STW | HOOK WATER LANE/SPS | WRA8624 | WRA8624 | 2 | Storm discharge at pumping station | SE7631025520 | 476310 | 425520 | GB530402609203 | HUMBER UPPER | Transitional Water | 3228 | Humber Estuary TraC | 3040 | Humber TraC | RIVER OUSE (TIDAL) | Not Applicable | Not Applicable | Not Applicable | 80:18 | 19 | 60.6 | 2020 | 99.99 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS01886
YWS01887 | Yorkshire Water | Live | THORNTON IN CRAVEN SPS | THORNTON IN CRAVEN/CSO | WRA8627 | WRA8627 | 1 | Storm discharge at pumping station | SD9077048170 | 390770 | 448170 | GB104027062980 | Earby Beck from source to River Aire | River | 3484 | Upper Aire | 3001 | Aire and Calder | THORNTON BECK | Not Applicable | Not Applicable | Not Applicable | 354:00 | 58 | 64.4 | 2020 | 99.89 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01887
YWS01888 | Yorkshire Water | Live | WANSFORD SEWAGE PUMPING STATION | WANSFORD THE SQUARE/CSO | WRA8630 | WRA8630 | 1 | SO on sewer network | TA0644056460 | 506442 | 456471 | GB104026067090 | Nafferton Beck from Source to to Driffield Canal | River | 3492 | Upper Hull | 3039 | Hull and East Riding | UNNAMED TRIB OF NAFFERTON BECK | Not Applicable | Not Applicable | Not Applicable | 104:30 | 9 | 1.8 | 2020 | 12.79 | Sensor failure / issue | Scheduled | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01888
YWS01889 | Yorkshire Water | Live | DALE STREET CSO | DALE STREET/CSO | WRA8632 | WRA8632 | A1 | SO on sewer network | SE1100716576 | 411007 | 416576 | GB104027063330 | Colne from Wessenden Brook to R Holme | River | 3097 | Colne and Holme | 3001 | Aire and Calder | LONGWOOD BROOK | Not Applicable | Not Applicable | Not Applicable | 25:30 | 15 | 12 | 2020 | 32.66 | Comms failure / issue | Resolved - Nov | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01889
YWS01890 | Yorkshire Water | Live | BRIMMINGTON ROAD CSO | BRIMINGTON ROAD/CSO | WRA8635 | WRA8635 | A1 | SO on sewer network | SK3873271525 | 438732 | 371525 | GB104027057771 | Rother, Spittal Brook to Doe Lea | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | RIVER ROTHER | Not Applicable | Not Applicable | Not Applicable | 2:45 | 1 | 2 | 2020 | 99.88 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01890
YWS01891 | Yorkshire Water | Live | BRADLEY LEEDS ROAD CSO | BRADLEY LEEDS ROAD/CSO | WRA8636 | WRA8636 | A1 | SO on sewer network | SE1691319753 | 416913 | 419753 | GB70410176 | Huddersfield Broad Canal | Canal | 2007 | Calder Canals | 2001 | Humber AWB | CINDERFIELD DIKE | Not Applicable | Not Applicable | Not Applicable | 140:30 | 52 | 55 | 2020 | 99.98 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01891
YWS01892 | Yorkshire Water | Live | DEARNE HALL ROAD CSO | DEARNE HALL ROAD/CSO | WRA8637 | WRA8637 | A1 | SO on sewer network | SE3195009080 | 431955 | 409087 | GB104027063171 | Dearne from Cawthorne Dyke to Lundwood STW | River | 3125 | Dearne | 3029 | Don and Rother | RIVER DEARNE | Not Applicable | Not Applicable | Not Applicable | 47:30 | 18 | 34.4 | 2020 | 85.49 | Comms failure / issue | Resolved - Oct | High spill threshold not met | High spill threshold not met | UWWTR investigation ongoing, Operational investigation completed | Operational improvement ongoing | SOAF investigation ongoing | YWS01892
YWS01893 | Yorkshire Water | Live | CONEY LANE CSO | CONEY LANE/CSO | WRA8639 | WRA8639 | 1 | SO on sewer network | SE0642040950 | 406424 | 440943 | GB104027062891 | Worth from Bridgehouse Beck to R Aire | River | 3307 | Middle Aire | 3001 | Aire and Calder | RIVER WORTH | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0 | 2023 | 95.8 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01893
YWS01894 | Yorkshire Water | Live | DAMEMS ROAD CSO | DAMEMS ROAD/CSO | WRA8640 | WRA8640 | A1 | SO on sewer network | SE0527939100 | 405279 | 439100 | GB104027062891 | Worth from Bridgehouse Beck to R Aire | River | 3307 | Middle Aire | 3001 | Aire and Calder | RIVER WORTH | Not Applicable | Not Applicable | Not Applicable | 1:45 | 3 | 2.6 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01894
YWS01895 | Yorkshire Water | Live | HAWORTH COMBINED SEWER OVERFLOW | HAWORTH/CSO | WRA8641 | WRA8641 | A1 | SO on sewer network | SE0480038450 | 404800 | 438450 | GB104027062891 | Worth from Bridgehouse Beck to R Aire | River | 3307 | Middle Aire | 3001 | Aire and Calder | RIVER WORTH | Not Applicable | Not Applicable | Not Applicable | 180:45 | 56 | 65 | 2020 | 99.99 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS01895
YWS01896 | Yorkshire Water | Live | SPRING BANK CSO | SPRING BANK/CSO | WRA8642 | WRA8642 | A1 | SO on sewer network | SE0585139951 | 405851 | 439951 | GB104027062891 | Worth from Bridgehouse Beck to R Aire | River | 3307 | Middle Aire | 3001 | Aire and Calder | GINGERBREAD CLOUGH | Not Applicable | Not Applicable | Not Applicable | 4:30 | 4 | 4.6 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01896
YWS01897 | Yorkshire Water | Live | BRADFORD ROAD 5 CSO | BRADFORD ROAD 5/CSO | WRA8643 | WRA8643 | A1 | SO on sewer network | SE0801642087 | 408016 | 442087 | GB104027063032 | Aire from Gill Beck (Baildon) to River Calder | River | 3265 | Lower Aire | 3001 | Aire and Calder | TRIBUTARY OF THE RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 77:15 | 54 | 63.8 | 2020 | 100 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement ongoing | SOAF investigation ongoing | YWS01897
YWS01898 | Yorkshire Water | Live | WAVERLEY AVENUE CSO | WAVERLEY AVENUE/CSO | WRA8645 | WRA8645 | A1 | SO on sewer network | SE0893741422 | 408937 | 441422 | GB104027063034 | Aire (R Worth to Gill Beck) | River | 3307 | Middle Aire | 3001 | Aire and Calder | RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 2:00 | 6 | 3.4 | 2020 | 99.98 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01898
YWS01899 | Yorkshire Water | Live | BRANKSOME DRIVE CSO | BRANKSOME DRIVE/CSO | WRA8646 | WRA8646 | A1 | SO on sewer network | SE1235537874 | 412355 | 437874 | GB104027063034 | Aire (R Worth to Gill Beck) | River | 3307 | Middle Aire | 3001 | Aire and Calder | RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 85:46 | 24 | 61.75 | 2020 | 38.13 | Power failure / issue | Resolved - Aug | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01899
YWS01900 | Yorkshire Water | Live | HARROGATE ROAD 298 CSO | HARROGATE ROAD 298/2 CSO | WRA8655 | WRA8655 | A1 | SO on sewer network | SE1955037670 | 419550 | 437670 | GB104027063032 | Aire from Gill Beck (Baildon) to River Calder | River | 3265 | Lower Aire | 3001 | Aire and Calder | CARR BECK | Not Applicable | Not Applicable | Not Applicable | 20:00 | 23 | 20.8 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01900
YWS01901 | Yorkshire Water | Live | EASTGATE, ELLAND CSO | EASTGATE ELLAND/CSO | WRA8657 | WRA8657 | 1 | SO on sewer network | SE1101121420 | 410995 | 421475 | GB104027062642 | Calder from Ryburn Confluence to River Colne | River | 3310 | Middle Calder | 3001 | Aire and Calder | CANKER DYKE | Not Applicable | Not Applicable | Not Applicable | 28:00 | 30 | 31.6 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01901
YWS01902 | Yorkshire Water | Live | HUDDERSFIELD ROAD 106 CSO | HUDDERSFIELD RD 106/CSO | WRA8659 | WRA8659 | A1 | SO on sewer network | SE1099021470 | 410995 | 421475 | GB104027062642 | Calder from Ryburn Confluence to River Colne | River | 3310 | Middle Calder | 3001 | Aire and Calder | CANKER DYKE | Not Applicable | Not Applicable | Not Applicable | 265:30 | 87 | 76.25 | 2021 | 99.68 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation completed, Operational investigation completed | No improvement action in reporting period | SOAF investigation completed - No work required | YWS01902
YWS01903 | Yorkshire Water | Live | HUDDERSFIELD ROAD/SOUTH LANE CSO | SOUTH LANE/CSO | WRA8660 | WRA8660 | 1 | SO on sewer network | SE1099121470 | 410995 | 421475 | GB104027062642 | Calder from Ryburn Confluence to River Colne | River | 3310 | Middle Calder | 3001 | Aire and Calder | CANKER DYKE | Not Applicable | Not Applicable | Not Applicable | 273:30 | 73 | 40.6 | 2020 | 99.73 |  |  | Performance - Infiltration | Performance - Infiltration | UWWTR investigation ongoing, Operational investigation ongoing | Operational improvement ongoing | SOAF investigation ongoing | YWS01903
YWS01904 | Yorkshire Water | Live | SUNNYBANK CSO | SUNNYBANK/CSO | WRA8661 | WRA8661 | A1 | SO on sewer network | SE0886120857 | 408861 | 420857 | GB104027062570 | Black Brook from Source to River Calder | River | 3310 | Middle Calder | 3001 | Aire and Calder | BLACK BROOK | Not Applicable | Not Applicable | Not Applicable | 1:30 | 6 | 6.4 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01904
YWS01905 | Yorkshire Water | Live | WISTONS LANE/ELLAND LINK CSO | WISTONS LANE/CSO | WRA8662 | WRA8662 | A1 | SO on sewer network | SE1101021420 | 410995 | 421475 | GB104027062642 | Calder from Ryburn Confluence to River Colne | River | 3310 | Middle Calder | 3001 | Aire and Calder | CANKER DYKE | Not Applicable | Not Applicable | Not Applicable | 206:30 | 47 | 46.6 | 2020 | 99.99 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS01905
YWS01906 | Yorkshire Water | Live | CROSS HILLS CSO | CROSS HILLS/CSO | WRA8667 | WRA8667 | A1 | SO on sewer network | SE0077644665 | 400776 | 444665 | GB104027062960 | Eastburn Beck from Lothersdale Beck to River Aire | River | 3484 | Upper Aire | 3001 | Aire and Calder | TRIBUTARY OF HOLME BECK | Not Applicable | Not Applicable | Not Applicable | 2:15 | 6 | 2.4 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01906
YWS01908 | Yorkshire Water | Live | MELTON STREET CSO | MELTON STREET/CSO | WRA8671 | WRA8671 | A1 | SO on sewer network | SE2397224645 | 423972 | 424645 | GB104027062670 | Batley Beck from Source to River Calder | River | 3268 | Lower Calder | 3001 | Aire and Calder | CARLINGHOW BECK | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0.4 | 2020 | 99.95 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01908
YWS01909 | Yorkshire Water | Revoked | SMITHIES MOOR LANE, BIRSTALL CSO | SMITHIES LANE NORTH/CSO | WRA8672 | WRA8672 | 1 | SO on sewer network | SE2251025740 | 422514 | 425743 | GB104027062670 | Batley Beck from Source to River Calder | River | 3268 | Lower Calder | 3001 | Aire and Calder | SMITHIES BECK | Not Applicable | Not Applicable | Not Applicable | [5 empty] | No longer operational as an overflow - permit revoked or to be revoked | Overflow no longer spilling to environment - from Jan | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01909
YWS01910 | Yorkshire Water | Live | BEAUMONT PARK CSO | BEAUMONT PARK/CSO | WRA8677 | WRA8677 | A1 | SO on sewer network | SE1264214116 | 412642 | 414116 | GB104027063301 | Holme from New Mill Dike to R Colne | River | 3097 | Colne and Holme | 3001 | Aire and Calder | TRIBUTARY OF RIVER HOLME | Not Applicable | Not Applicable | Not Applicable |  |  | 1.5 | 2020 | 0 | Sensor failure / issue | Scheduled | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01910
YWS01911 | Yorkshire Water | Live | HONLEY NEWTOWN NO 2 CSO | HONLEY NEWTOWN/NO 2 CSO | WRA8678 | WRA8678 | A1 | SO on sewer network | SE1400212134 | 414002 | 412134 | GB104027063301 | Holme from New Mill Dike to R Colne | River | 3097 | Colne and Holme | 3001 | Aire and Calder | RIVER HOLME | Not Applicable | Not Applicable | Not Applicable | 11:00 | 23 | 23 | 2020 | 99.98 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01911
YWS01912 | Yorkshire Water | Live | QUEENS MILL ROAD (OFF) | QUEENS MILL ROAD/CSO | WRA8679 | WRA8679 | A1 | SO on sewer network | SE1413115635 | 414131 | 415635 | GB104027063301 | Holme from New Mill Dike to R Colne | River | 3097 | Colne and Holme | 3001 | Aire and Calder | RIVER HOLME | Not Applicable | Not Applicable | Not Applicable | 0:15 | 1 | 4 | 2020 | 99.93 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01912
YWS01913 | Yorkshire Water | Live | WHITEHEAD LANE CSO | WHITEHEAD LANE/NO 2 CSO | WRA8680 | WRA8680 | 1 | SO on sewer network | SE1449015790 | 414502 | 415496 | GB104027062550 | Colne from River Holme to River Calder | River | 3097 | Colne and Holme | 3001 | Aire and Calder | RIVER COLNE | Not Applicable | Not Applicable | Not Applicable | 3:30 | 10 | 13.2 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01913
YWS01915 | Yorkshire Water | Live | DOG KENNEL BANK CSO | SOMERSET ROAD/CSO | WRA8681 | EPR/RB3793AQ | A1 | SO on sewer network | SE1512016250 | 415120 | 416250 | GB104027062550 | Colne from River Holme to River Calder | River | 3097 | Colne and Holme | 3001 | Aire and Calder | RIVER COLNE | Not Applicable | Not Applicable | Not Applicable | 8:00 | 12 | 18 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01915
YWS01916 | Yorkshire Water | Live | LONGLEY PARK CSO | LONGLEY PARK/CSO | WRA8682 | WRA8682 | A1 | SO on sewer network | SE1505216179 | 415052 | 416179 | GB104027062550 | Colne from River Holme to River Calder | River | 3097 | Colne and Holme | 3001 | Aire and Calder | RIVER COLNE | Not Applicable | Not Applicable | Not Applicable | 15:30 | 12 | 7 | 2020 | 99.93 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01916
YWS01917 | Yorkshire Water | Live | WHAMS ROAD CSO | WHAMS ROAD/NO 2 CSO | WRA8685 | WRA8685 | 1 | SO on sewer network | SE1916004120 | 419160 | 404120 | GB104027057500 | Don from Source to Scout Dyke | River | 3490 | Upper Don | 3029 | Don and Rother | SLEDBROOK DYKE | Not Applicable | Not Applicable | Not Applicable | 26:45 | 12 | 9.2 | 2020 | 88.38 | Sensor failure / issue | Resolved - Dec | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01917
YWS01918 | Yorkshire Water | Live | SILKSTONE CSO | SILKSTONE/CSO | WRA8686 | WRA8686 | A1 | SO on sewer network | SE2933506092 | 429335 | 406092 | GB104027057560 | Silkstone Beck from Source to Cawthorne Dyke | River | 3125 | Dearne | 3029 | Don and Rother | SILKSTONE BECK | Not Applicable | Not Applicable | Not Applicable | 35:00 | 13 | 16.4 | 2020 | 99.91 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01918
YWS01919 | Yorkshire Water | Live | BIRK ROAD, KENDRAY CSO | BIRK ROAD/CSO | WRA8687 | WRA8687 | 1 | SO on sewer network | SE3726106230 | 437269 | 406238 | GB104027063171 | Dearne from Cawthorne Dyke to Lundwood STW | River | 3125 | Dearne | 3029 | Don and Rother | TRIBUTARY OF THE RIVER DEARNE | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0.4 | 2020 | 99.91 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01919
YWS01920 | Yorkshire Water | Live | LAMBERT ROAD, KENDRAY CSO | LAMBERT ROAD/CSO | WRA8688 | WRA8688 | 1 | SO on sewer network | SE3726006320 | 437269 | 406328 | GB104027063171 | Dearne from Cawthorne Dyke to Lundwood STW | River | 3125 | Dearne | 3029 | Don and Rother | TRIBUTARY OF THE RIVER DEARNE | Not Applicable | Not Applicable | Not Applicable | 0:15 | 1 | 4.6 | 2020 | 98.96 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01920
YWS01921 | Yorkshire Water | Live | HILL TOP FARM CSO | HILL TOP FARM/CSO | WRA8691 | WRA8691 | 1 | SO on sewer network | SE3456008840 | 434523 | 408632 | GB104027063171 | Dearne from Cawthorne Dyke to Lundwood STW | River | 3125 | Dearne | 3029 | Don and Rother | DITCH TO THE RIVER DEARNE | Not Applicable | Not Applicable | Not Applicable | 2:15 | 3 | 1.8 | 2020 | 91.83 |  |  | High spill threshold not met | High spill threshold not met | Operational investigation completed | No improvement action in reporting period | No SOAF investigation required | YWS01921
YWS01922 | Yorkshire Water | Live | BURLEY ROAD CSO | BURLEY ROAD/CSO | WRA8693 | WRA8693 | A1 | SO on sewer network | SE2748134221 | 427481 | 434221 | GB104027063032 | Aire from Gill Beck (Baildon) to River Calder | River | 3265 | Lower Aire | 3001 | Aire and Calder | RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 4.2 | 2020 | 99.87 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01922
YWS01923 | Yorkshire Water | Live | HAWKSWORTH ROAD, HORSFORTH CSO | HAWKSWORTH ROAD/CSO | WRA8694 | WRA8694 | 1 | SO on sewer network | SE2472037190 | 424724 | 437190 | GB104027062920 | Carlton Beck from Source to River Aire | River | 3265 | Lower Aire | 3001 | Aire and Calder | COW BECK | Not Applicable | Not Applicable | Not Applicable | 6:15 | 13 | 16.8 | 2020 | 98.92 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01923
YWS01924 | Yorkshire Water | Live | VILLAGE PLACE NO 2CSO | VILLAGE PLACE/NO 2 CSO | WRA8696 | WRA8696 | A1 | SO on sewer network | SE2748134221 | 427481 | 434221 | GB104027063032 | Aire from Gill Beck (Baildon) to River Calder | River | 3265 | Lower Aire | 3001 | Aire and Calder | RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 85:00 | 57 | 46 | 2020 | 99.98 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation completed | No improvement action in reporting period | SOAF investigation completed - No work required | YWS01924
YWS01925 | Yorkshire Water | Live | SHEEPSCAR WAY CSO | SHEEPSCAR WAY/CSO | WRA8698 | WRA8698 | A1 | SO on sewer network | SE3055034991 | 430550 | 434991 | GB104027062900 | Meanwood Beck from Source to River Aire | River | 3265 | Lower Aire | 3001 | Aire and Calder | SHEEPSCAR BECK (CULVERTED) | Not Applicable | Not Applicable | Not Applicable | 21:15 | 24 | 28.2 | 2020 | 90.2 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01925
YWS01926 | Yorkshire Water | Live | ISLAND (RIVER AIRE) CSO | COMMERCIAL ROAD/CSO | WRA8699 | WRA8699 | 1 | SO on sewer network | SE2650035070 | 426501 | 435073 | GB104027063032 | Aire from Gill Beck (Baildon) to River Calder | River | 3265 | Lower Aire | 3001 | Aire and Calder | RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0 | 2023 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01926
YWS01927 | Yorkshire Water | Live | STOCKS HILL CSO | STOCKS HILL/CSO | WRA8702 | WRA8702 | 1 | SO on sewer network | SE2916032720 | 429143 | 432673 | GB104027062830 | Low/Wortley/Pudsey Bks | River | 3265 | Lower Aire | 3001 | Aire and Calder | HOL BECK | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0.6 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01927
YWS01928 | Yorkshire Water | Live | WYTHER LANE NO.2 CSO | WYTHER LANE/NO 2 CSO | WRA8705 | WRA8705 | A1 | SO on sewer network | SE2599435173 | 425994 | 435173 | GB104027063032 | Aire from Gill Beck (Baildon) to River Calder | River | 3265 | Lower Aire | 3001 | Aire and Calder | RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 29:16 | 39 | 37.6 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01928
YWS01929 | Yorkshire Water | Live | TOWN FARM 4 CSO | INNFOLD FARM 1/CSO | WRA8707 | WRA8707 | 1 | SO on sewer network | SE2896013604 | 428960 | 413604 | GB104027063260 | Dearne from Bentley Brook to Cawthorne Dyke | River | 3125 | Dearne | 3029 | Don and Rother | RIVER DEARNE | Not Applicable | Not Applicable | Not Applicable | 3:15 | 1 | 7.2 | 2020 | 99.71 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01929
YWS01930 | Yorkshire Water | Live | GODDARD HALL ROAD CSO | GODDARD HALL ROAD/CSO | WRA8708 | WRA8708 | 1 | SO on sewer network | SK3628090150 | 437284 | 390155 | GB104027057412 | Don from River Loxley confl to River Don Works | River | 3312 | Middle Don | 3029 | Don and Rother | TRIBUTARY OF BAGLEY DYKE | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0.4 | 2020 | 71.68 | Sensor failure / issue | Resolved - Nov | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01930
YWS01931 | Yorkshire Water | Live | FURNIVAL ROAD CSO | FURNIVAL ROAD/CSO | WRA8710 | WRA8710 | A1 | SO on sewer network | SK3629288094 | 436292 | 388094 | GB104027057412 | Don from River Loxley confl to River Don Works | River | 3312 | Middle Don | 3029 | Don and Rother | RIVER DON | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 1 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01931
YWS01932 | Yorkshire Water | Live | JOHN CALVERT LANE CSO | JOHN CALVERT ROAD/CSO | WRA8713 | WRA8713 | 1 | SO on sewer network | SK4298084880 | 442989 | 384888 | GB104027057772 | Rother, Doe Lea to Don | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | TRIBUTARY OF THE RIVER ROTHER | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0.8 | 2020 | 99.77 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01932
YWS01933 | Yorkshire Water | Live | LINCOLN STREET CSO | LINCOLN STREET/CSO | WRA8714 | WRA8714 | A1 | SO on sewer network | SK3852369623 | 438523 | 369623 | GB104027057630 | Rother from Redleadmill Brook to Spital Brook | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | RIVER ROTHER | Not Applicable | Not Applicable | Not Applicable | 15:15 | 16 | 7.8 | 2020 | 74.06 | Sensor failure / issue | Scheduled | High spill threshold not met | High spill threshold not met | Operational investigation ongoing | Operational improvement ongoing | No SOAF investigation required | YWS01933
YWS01934 | Yorkshire Water | Live | GRASSHILL FARM CSO | GRASSHILL FARM/CSO | WRA8716 | WRA8716 | A1 | SO on sewer network | SK4003067690 | 440030 | 367690 | GB104027057630 | Rother from Redleadmill Brook to Spital Brook | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | RIVER ROTHER | Not Applicable | Not Applicable | Not Applicable | 5:45 | 4 | 5 | 2020 | 95.52 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01934
YWS01935 | Yorkshire Water | Live | DUNMOW ROAD CSO | DUNMOW ROAD/CSO | WRA8723 | WRA8723 | 1 | SO on sewer network | SK3738090230 | 437389 | 390230 | GB104027057412 | Don from River Loxley confl to River Don Works | River | 3312 | Middle Don | 3029 | Don and Rother | BAGLEY DYKE | Not Applicable | Not Applicable | Not Applicable | 24:15 | 14 | 33.6 | 2020 | 99.91 |  |  | High spill threshold not met | High spill threshold not met | Operational investigation completed | Operational improvement completed | No SOAF investigation required | YWS01935
YWS01936 | Yorkshire Water | Live | POTTERY LANE WEST CSO | POTTERY LANE WEST/CSO | WRA8725 | WRA8725 | A1 | SO on sewer network | SK3866673093 | 438666 | 373093 | GB104027057771 | Rother, Spittal Brook to Doe Lea | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | RIVER ROTHER | Not Applicable | Not Applicable | Not Applicable | 15:15 | 18 | 21.2 | 2020 | 99.95 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01936
YWS01937 | Yorkshire Water | Live | SHEFFIELD ROAD FIRE STATION CSO | SHEFFIELD RD FIRE STN/CSO | WRA8726 | WRA8726 | 1 | SO on sewer network | SK3880073300 | 438800 | 373308 | GB104027057771 | Rother, Spittal Brook to Doe Lea | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | RIVER ROTHER | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0.4 | 2020 | 62.93 | Comms failure / issue | Resolved - Dec | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01937
YWS01938 | Yorkshire Water | Live | AUGHTON (TREETON LANE) SPS | AUGHTON/CSO | WRA8727 | WRA8727 | 1 | SO on sewer network | SK4495087110 | 444953 | 387114 | GB104027057740 | Ulley Brook from Source to River Rother | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | TRIBUTARY OF ULLEY BROOK | Not Applicable | Not Applicable | Not Applicable | 207:30 | 27 | 25.2 | 2020 | 99.9 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01938
YWS01939 | Yorkshire Water | Live | ASTON THE CHASE CSO | ASTON THE CHASE/CSO | WRA8728 | WRA8728 | A1 | SO on sewer network | SK4645084920 | 446450 | 384920 | GB104027057730 | Pigeon Bridge Brook from Source to River Rother | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | TRIBUTARY OF PIGEON BROOK | Not Applicable | Not Applicable | Not Applicable | 50:30 | 13 | 15 | 2020 | 99.23 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01939
YWS01940 | Yorkshire Water | Live | DELVES ROAD NO 2 CSO | DELVES ROAD/NO 2 CSO | WRA8729 | WRA8729 | A1 | SO on sewer network | SK4238883965 | 442388 | 383965 | GB104027057773 | Shire Brook | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | SHIRE BROOK | Not Applicable | Not Applicable | Not Applicable | 1:45 | 3 | 8.2 | 2020 | 99.98 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01940
YWS01941 | Yorkshire Water | Live | AVENUE FARM CSO | AVENUE FARM/CSO | WRA8731 | WRA8731 | A1 | SO on sewer network | SK3958567956 | 439585 | 367956 | GB104027057630 | Rother from Redleadmill Brook to Spital Brook | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | RIVER ROTHER | Not Applicable | Not Applicable | Not Applicable | 385:30 | 80 | 80.8 | 2020 | 99.98 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement ongoing | SOAF investigation ongoing | YWS01941
YWS01942 | Yorkshire Water | Live | A1/A645 SLIP ROAD SSO | KNOTTINGLEY A1/CSO | WRA8732 | WRA8732 | 1 | SO on sewer network | SE4834523515 | 448427 | 423544 | GB70410066 | Aire and Calder Navigation (Knottingley and Goole Canal) | Canal | 2018 | Don and Rother Canals | 2001 | Humber AWB | AIRE & CALDER NAVIGATION | Not Applicable | Not Applicable | Not Applicable | 74:00 | 29 | 33 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01942
YWS01943 | Yorkshire Water | Live | STONEGATE (CSO 174) CSO | BUSLINGTHORPE VALE/CSO | WRA8734 | WRA8734 | 1 | SO on sewer network | SE3021035490 | 430094 | 435597 | GB104027062900 | Meanwood Beck from Source to River Aire | River | 3265 | Lower Aire | 3001 | Aire and Calder | MEANWOOD BECK | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0 | 2020 | 6.13 | Sensor failure / issue | Resolved - Dec | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01943
YWS01944 | Yorkshire Water | Live | BURN AIRFIELD SPS | BURN AIRFIELD/CSO | WRA8735 | WRA8735 | A2 | SO on sewer network | SE6078627925 | 460700 | 427900 | GB104027064270 | Ouse from R Wharfe to Upper Humber | River | 3280 | Lower Ouse Yorkshire | 3115 | Wharfe and Lower Ouse | HAGG BUSH DIKE | Not Applicable | Not Applicable | Not Applicable | 42:45 | 19 | 33.8 | 2020 | 53.14 | Sensor failure / issue | Resolved - Jun | High spill threshold not met | High spill threshold not met | UWWTR investigation ongoing, Operational investigation completed | Operational improvement ongoing | SOAF investigation ongoing | YWS01944
YWS01945 | Yorkshire Water | Live | RAWCLIFFE PARK NO3 SPS | RAWCLIFFE PARK/NO 3 CSO | WRA8737 | WRA8737 | A1 | SO on sewer network | SE6884022603 | 468840 | 422603 | GB104027062760 | Aire from River Calder to River Ouse | River | 3265 | Lower Aire | 3001 | Aire and Calder | DOBELLER DRAIN | Not Applicable | Not Applicable | Not Applicable | 52:45 | 15 | 18 | 2020 | 71.39 | Comms failure / issue | Resolved - Sep | High spill threshold not met | High spill threshold not met | Operational investigation completed | Operational improvement completed | No SOAF investigation required | YWS01945
YWS01946 | Yorkshire Water | Live | CROFT MILLS CSO | CROFT MILLS/CSO | WRA8738 | WRA8738 | A1 | SO on sewer network | SD9743043540 | 397430 | 443540 | GB104027062930 | Glusburn beck from source to Lothersdale Beck | River | 3484 | Upper Aire | 3001 | Aire and Calder | ICKORNSHAW BECK | Not Applicable | Not Applicable | Not Applicable | 39:15 | 15 | 67 | 2020 | 18.54 | Comms failure / issue | Resolved - Dec | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01946
YWS01947 | Yorkshire Water | Live | SUTTON MAIN STREET CSO | SUTTON MAIN STREET/CSO | WRA8739 | WRA8739 | A1 | SO on sewer network | SE0144044570 | 401445 | 444579 | GB104027062960 | Eastburn Beck from Lothersdale Beck to River Aire | River | 3484 | Upper Aire | 3001 | Aire and Calder | HOLME/EASTBURN BECK | Not Applicable | Not Applicable | Not Applicable | 87:00 | 30 | 57.6 | 2020 | 98.16 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01947
YWS01948 | Yorkshire Water | Live | VALLEY FARM CSO | VALLEY FARM/CSO | WRA8741 | WRA8741 | A1 | SO on sewer network | SE2800038390 | 428002 | 438395 | GB104027062900 | Meanwood Beck from Source to River Aire | River | 3265 | Lower Aire | 3001 | Aire and Calder | ADEL BECK | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0 | 2020 | 99.89 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01948
YWS01949 | Yorkshire Water | Live | BLACKMOOR ROAD NO.2 CSO | BLACKMOOR ROAD/NO 2 CSO | WRA8742 | WRA8742 | A1 | SO on sewer network | SE2879139065 | 428791 | 439065 | GB104027062900 | Meanwood Beck from Source to River Aire | River | 3265 | Lower Aire | 3001 | Aire and Calder | ADEL BECK | Not Applicable | Not Applicable | Not Applicable | 28:15 | 23 | 29.2 | 2020 | 99.97 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01949
YWS01950 | Yorkshire Water | Live | BLEAKLEY LANE NO 2 CSO | BLEAKLEY LANE/NO 2 CSO | WRA8744 | WRA8744 | A1 | SO on sewer network | SE3577512318 | 435775 | 412318 | GB104027062530 | Owler Beck from Source to River Calder | River | 3268 | Lower Calder | 3001 | Aire and Calder | APPLEHAIGH BECK | Not Applicable | Not Applicable | Not Applicable | 51:00 | 24 | 29 | 2020 | 99.93 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01950
YWS01952 | Yorkshire Water | Live | CRAGG ROAD NO 2 CSO | CRAGG ROAD/NO 2 CSO | WRA8746 | WRA8746 | A1 | SO on sewer network | SE0113225780 | 401132 | 425780 | GB104027062610 | Cragg Brook from Source to River Calder | River | 3310 | Middle Calder | 3001 | Aire and Calder | CRAGG BROOK | Not Applicable | Not Applicable | Not Applicable | 310:30 | 44 | 52.4 | 2020 | 100 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01952
YWS01953 | Yorkshire Water | Live | BURNLEY ROAD CORNHOLME CSO | BURNLEY RD CORNHOLME/CSO | WRA8747 | WRA8747 | A1 | SO on sewer network | SD9135326087 | 391353 | 426087 | GB104027062660 | Calder from Source to Walsden Water | River | 3487 | Upper Calder | 3001 | Aire and Calder | RIVER CALDER | Not Applicable | Not Applicable | Not Applicable | 113:15 | 30 | 41 | 2020 | 99.96 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01953
YWS01954 | Yorkshire Water | Live | LONGFIELD ROAD | LONGFIELD ROAD/CSO | WRA8748 | WRA8748 | 1 | SO on sewer network | SD9361023960 | 393508 | 423938 | GB104027062600 | Walsden Water from Source to River Calder | River | 3487 | Upper Calder | 3001 | Aire and Calder | WALSDEN WATER | Not Applicable | Not Applicable | Not Applicable | 89:15 | 26 | 15.8 | 2020 | 96.82 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01954
YWS01955 | Yorkshire Water | Live | ARMSTEAD ROAD CSO | ARMSTEAD ROAD/NO 2 CSO | WRA8749 | WRA8749 | 1 | SO on sewer network | SK4399083120 | 443991 | 383124 | GB104027057772 | Rother, Doe Lea to Don | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | OCHRE DYKE | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0.5 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01955
YWS01956 | Yorkshire Water | Live | EASTWOOD INDUSTRIAL ESTATE CSO | EASTWOOD IND ESTATE/CSO | WRA8750 | WRA8750 | A1 | Inlet SO at WwTW | SK4445794214 | 444457 | 394214 | GB104027057452 | Don from River Rother to River Dearne | River | 3312 | Middle Don | 3029 | Don and Rother | RIVER DON | Not Applicable | Not Applicable | Not Applicable | 521:15 | 97 | 102.4 | 2020 | 99.96 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | Operational investigation ongoing | Operational improvement ongoing | SOAF investigation completed - No work required | YWS01956
YWS01957 | Yorkshire Water | Live | CHURCH LANE SPS | BAKEHOUSE LANE/CSO | WRA8752 | WRA8752 | 1 | Storm discharge at pumping station | TA0675064220 | 506540 | 464320 | GB104026067101 | Lowthorpe/Kelk/Foston Bks from Source to Frodingham Beck | River | 3492 | Upper Hull | 3039 | Hull and East Riding | LOWTHORPE BECK | Not Applicable | Not Applicable | Not Applicable | 729:45 | 67 | 21.2 | 2020 | 99.89 |  |  | Performance - GW inundation | High spill threshold not met | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS01957
YWS01958 | Yorkshire Water | Live | CARNABY SEWAGE PUMPING STATION | CARNABY EAST/CSO | C4279 | C4279(SS) | A1 | Storm discharge at pumping station | TA1459064150 | 514598 | 464150 | GB104026066650 | Auburn Beck from Source to North Sea | River | 3025 | Barmston Sea Drain | 3039 | Hull and East Riding | DEMMING DRAIN | Not Applicable | Wilsthorpe | Not Applicable | 6:15 | 1 | 1 | 2020 | 99.78 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01958
YWS01959 | Yorkshire Water | Live | CARNABY (VILLAGE) SPS | CARNABY MOOR LANE/CSO | WRA8753 | WRA8753 | A1 | Storm discharge at pumping station | TA1565364290 | 515653 | 464290 | GB104026066650 | Auburn Beck from Source to North Sea | River | 3025 | Barmston Sea Drain | 3039 | Hull and East Riding | AUBURN BECK | Not Applicable | Wilsthorpe | Not Applicable | 95:36 | 11 | 5.8 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01959
YWS01960 | Yorkshire Water | Live | NOTTON SPS | NOTTON/CSO | WRA8754 | WRA8754 | A2 | Storm discharge at pumping station | SE3524113141 | 435241 | 413141 | GB104027062530 | Owler Beck from Source to River Calder | River | 3268 | Lower Calder | 3001 | Aire and Calder | APPLEHAIGH BECK | Not Applicable | Not Applicable | Not Applicable | 455:30 | 77 | 63.8 | 2020 | 99.92 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement ongoing | SOAF investigation ongoing | YWS01960
YWS01961 | Yorkshire Water | Live | CRESCENT ROAD CSO | CRESCENT RD BIRKBY/2 CSO | WRA8759 | WRA8759 | 1 | SO on sewer network | SE1410018120 | 414043 | 418123 | GB104027062550 | Colne from River Holme to River Calder | River | 3097 | Colne and Holme | 3001 | Aire and Calder | TRIBUTARY OF GRIMSCAR DIKE | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0.2 | 2020 | 99.7 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01961
YWS01962 | Yorkshire Water | Live | GAS WORKS LANE | GAS WORKS LANE/CSO | WRA8762 | WRA8762 | 1 | SO on sewer network | SE1092021500 | 410922 | 421500 | GB104027062642 | Calder from Ryburn Confluence to River Colne | River | 3310 | Middle Calder | 3001 | Aire and Calder | RIVER CALDER | Not Applicable | Not Applicable | Not Applicable | 5:15 | 1 | 0.8 | 2020 | 99.91 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01962
YWS01963 | Yorkshire Water | Live | LOWER EDGE ROAD CSO | LOWER EDGE ROAD/CSO | WRA8764 | WRA8764 | 1 | SO on sewer network | SE1109021530 | 411094 | 421538 | GB104027062642 | Calder from Ryburn Confluence to River Colne | River | 3310 | Middle Calder | 3001 | Aire and Calder | RIVER CALDER | Not Applicable | Not Applicable | Not Applicable | 28:30 | 21 | 23.6 | 2020 | 93.18 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01963
YWS01964 | Yorkshire Water | Live | MILNS SHAW LANE NO 2 CSO | MILNS SHAW LANE/NO 2 CSO | WRA8765 | WRA8765 | A1 | SO on sewer network | SE1168215808 | 411682 | 415808 | GB104027063330 | Colne from Wessenden Brook to R Holme | River | 3097 | Colne and Holme | 3001 | Aire and Calder | TRIBUTARY OF THE RIVER COLNE | Not Applicable | Not Applicable | Not Applicable | 21:15 | 16 | 23.2 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01964
YWS01965 | Yorkshire Water | Live | MILNSBRIDGE (MARKET STREET) CSO | MILNSBRIDGE/CSO | WRA8766 | WRA8766 | A1 | SO on sewer network | SE1154816143 | 411548 | 416143 | GB104027063330 | Colne from Wessenden Brook to R Holme | River | 3097 | Colne and Holme | 3001 | Aire and Calder | LONGWOOD BROOK | Not Applicable | Not Applicable | Not Applicable | 130:30 | 69 | 60.2 | 2020 | 97.26 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | Operational investigation completed | No improvement action in reporting period | SOAF investigation completed - No work required | YWS01965
YWS01966 | Yorkshire Water | Live | PICKFORD STREET CSO | PICKFORD STREET/NO 2 CSO | WRA8768 | WRA8768 | 1 | SO on sewer network | SE1150015680 | 411515 | 415668 | GB104027063330 | Colne from Wessenden Brook to R Holme | River | 3097 | Colne and Holme | 3001 | Aire and Calder | TRIBUTARY OF THE RIVER COLNE | Not Applicable | Not Applicable | Not Applicable | 0:15 | 1 | 1 | 2020 | 84.35 | Comms failure / issue | Resolved - May | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01966
YWS01967 | Yorkshire Water | Live | STAINLAND ROAD CSO | HOLYWELL GREEN/CSO | WRA8770 | WRA8770 | 1 | SO on sewer network | SE0923019800 | 409238 | 419805 | GB104027062570 | Black Brook from Source to River Calder | River | 3310 | Middle Calder | 3001 | Aire and Calder | HOLYWELL BROOK | Not Applicable | Not Applicable | Not Applicable | 21:15 | 14 | 16.8 | 2020 | 99.93 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01967
YWS01968 | Yorkshire Water | Live | BROCCO BANK NO 2 CSO | BROCCO BANK/NO 2 CSO | WRA8773 | WRA8773 | A1 | SO on sewer network | SK3323985793 | 433239 | 385793 | GB104027057760 | Porter from Source to River Sheaf | River | 3312 | Middle Don | 3029 | Don and Rother | PORTER BROOK | Not Applicable | Not Applicable | Not Applicable | 24:30 | 21 | 18 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01968
YWS01969 | Yorkshire Water | Live | ENDCLIFFE VALE ROAD CSO | ENDCLIFFE VALE ROAD/2 CSO | WRA8774 | WRA8774 | 1 | SO on sewer network | SK3331085820 | 433311 | 385828 | GB104027057760 | Porter from Source to River Sheaf | River | 3312 | Middle Don | 3029 | Don and Rother | PORTER BROOK | Not Applicable | Not Applicable | Not Applicable | 3:00 | 5 | 1.67 | 2020 | 99.89 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01969
YWS01970 | Yorkshire Water | Live | KILDWICK SPS | KILDWICK/CSO | WRA8776 | WRA8776 | A1 | SO on sewer network | SE0134045770 | 401340 | 445732 | GB104027063033 | Aire (Eshton Beck to R Worth) | River | 3484 | Upper Aire | 3001 | Aire and Calder | RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 241:45 | 44 | 29.8 | 2020 | 99.69 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01970
YWS01971 | Yorkshire Water | Live | HOLME ROAD CSO | HOLME ROAD/CSO | WRA8779 | WRA8779 | A1 | SO on sewer network | SE8756041540 | 487560 | 441540 | GB104026066690 | Foulness from Black Beck to Market Weighton Canal | River | 3191 | Foulness | 3039 | Hull and East Riding | WEIGHTON BECK | Not Applicable | Not Applicable | Not Applicable | 1735:45 | 121 | 92.4 | 2020 | 99.97 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation ongoing | Operational improvement ongoing | SOAF investigation ongoing | YWS01971
YWS01972 | Yorkshire Water | Live | SCAR LANE CSO | SCAR LANE/CSO | WRA8780 | WRA8780 | A1 | SO on sewer network | SE1155715975 | 411557 | 415975 | GB104027063330 | Colne from Wessenden Brook to R Holme | River | 3097 | Colne and Holme | 3001 | Aire and Calder | RIVER COLNE | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 6.4 | 2020 | 64.48 | Sensor failure / issue | Resolved - May | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01972
YWS01973 | Yorkshire Water | Live | KNOTTINGLEY COMMON LANE SPS | KNOTTINGLEY COMMON LN/CSO | WRA8781 | WRA8781 | A2 | Storm discharge at pumping station | SE5091423767 | 450914 | 423767 | GB70410066 | Aire and Calder Navigation (Knottingley and Goole Canal) | Canal | 2018 | Don and Rother Canals | 2001 | Humber AWB | TOWN DYKE | Not Applicable | Not Applicable | Not Applicable | 92:45 | 35 | 38.6 | 2020 | 99.98 |  |  | High spill threshold not met | High spill threshold not met | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01973
YWS01974 | Yorkshire Water | Live | WANSFORD NO. 2 STW | WANSFORD/NO 2 STW | WRA8794 | WRA8794 | A2 | Inlet SO at WwTW | TA0651056690 | 506510 | 456690 | GB104026067090 | Nafferton Beck from Source to to Driffield Canal | River | 3492 | Upper Hull | 3039 | Hull and East Riding | TRIBUTARY OF NAFFERTON BECK | Not Applicable | Not Applicable | Not Applicable | 811:00 | 112 | 80.6 | 2020 | 99.95 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS01974
YWS01975 | Yorkshire Water | Live | OLD ELLERBY STW | OLD ELLERBY/STW | WRA8796 | WRA8796 | 2 | Inlet SO at WwTW | TA1663037450 | 516630 | 437450 | GB104026066860 | Lambwath Stream from Source to Foredyke Stream | River | 3274 | Lower Hull | 3039 | Hull and East Riding | TRIBUTARY OF KELWELL DRAIN | Not Applicable | Not Applicable | Not Applicable | 845:30 | 67 | 52.2 | 2020 | 100 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement completed | SOAF investigation ongoing | YWS01975
YWS01976 | Yorkshire Water | Live | LELLEY SEWAGE TREATMENT WORKS | LELLEY/STW | WRA8797 | WRA8797 | 2 | Inlet SO at WwTW | TA2100032750 | 521000 | 432750 | GB104026066600 | Oldfleet/Wyton/Sproatley Drain from Source to Humber | River | 3057 | Burstwick and Eastern Drains | 3039 | Hull and East Riding | TRIBUTARY OF NORTHFIELD DRAIN | Not Applicable | Not Applicable | Not Applicable | 1523:45 | 93 | 32.6 | 2020 | 100 |  |  | Performance - Partial / no capacity due to blockage or restriction (e.g. roots / grid) - maintenance issue | High spill threshold not met | UWWTR investigation ongoing, Operational investigation completed | Operational improvement completed | SOAF investigation ongoing | YWS01976
YWS01977 | Yorkshire Water | Live | BATLEY MOUNT STREET CSO | BATLEY MOUNT STREET/CSO | WRA8819 | WRA8819 | A1 | SO on sewer network | SE2469023188 | 424690 | 423188 | GB104027062670 | Batley Beck from Source to River Calder | River | 3268 | Lower Calder | 3001 | Aire and Calder | BATLEY BECK | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 14.6 | 2020 | 3.88 | Comms failure / issue | Scheduled | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01977
YWS01978 | Yorkshire Water | Live | BAYSWATER ROAD CSO | BAYSWATER ROAD/CSO | WRA8820 | WRA8820 | A1 | SO on sewer network | SE3140035026 | 431400 | 435026 | GB104027062900 | Meanwood Beck from Source to River Aire | River | 3265 | Lower Aire | 3001 | Aire and Calder | GIPTON BECK | Not Applicable | Not Applicable | Not Applicable | 2:15 | 7 | 7.2 | 2020 | 99.76 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01978
YWS01979 | Yorkshire Water | Live | HAWTHORNE STREET SPS | HAWTHORNE STREET/CSO | WRA8822 | WRA8822 | 1 | Storm discharge at pumping station | SK3861070050 | 438610 | 370050 | GB104027057630 | Rother from Redleadmill Brook to Spital Brook | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | RIVER ROTHER | Not Applicable | Not Applicable | Not Applicable | 0:15 | 1 | 0.8 | 2020 | 66.19 | Capital / maintenance works affect EDM operation | Resolved - May | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01979
YWS01980 | Yorkshire Water | Live | UNSTONE SPS | UNSTONE/CSO | WRA8827 | WRA8827 | A2 | SO on sewer network | SK3754076220 | 437545 | 376219 | GB104027057710 | Drone/Whitting from Source to River Rother | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | RIVER DRONE | Not Applicable | Not Applicable | Not Applicable | 249:15 | 32 | 34.2 | 2020 | 99.57 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01980
YWS01981 | Yorkshire Water | Live | FOSTON-ON-THE-WOLDS STW | FOSTON ON THE WOLDS/STW | WRA8838 | WRA8838 | A2 | Inlet SO at WwTW | TA0935054680 | 509350 | 454680 | GB104026067101 | Lowthorpe/Kelk/Foston Bks from Source to Frodingham Beck | River | 3492 | Upper Hull | 3039 | Hull and East Riding | FOSTON BECK | Not Applicable | Not Applicable | Not Applicable | 24:00 | 5 | 1.6 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01981
YWS01982 | Yorkshire Water | Live | BURTON FLEMING STW | BURTON FLEMING/STW | WRA8858 | WRA8858 | A2 | Inlet SO at WwTW | TA0866071967 | 508660 | 471967 | GB104026072790 | Gypsey Race from Source to North Sea | River | 3214 | Gypsey Race | 3039 | Hull and East Riding | GYPSY RACE | Not Applicable | Not Applicable | Not Applicable | 19:00 | 12 | 7 | 2020 | 71.58 | Sensor failure / issue | Resolved - May | High spill threshold not met | High spill threshold not met | Operational investigation completed | Operational improvement completed | No SOAF investigation required | YWS01982
YWS01983 | Yorkshire Water | Live | GRIMSTON SEWAGE TREATMENT WORKS | GRIMSTON/CSO | WRA8859 | WRA8859 | 2 | SO on sewer network | TA2787035270 | 527880 | 435270 | GB104026066590 | Burton Pidsea Drain Lower Catchment | River | 3057 | Burstwick and Eastern Drains | 3039 | Hull and East Riding | FOSTON BECK | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0 | 2020 | 99.91 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01983
YWS01984 | Yorkshire Water | Live | NEW ELLERBY SEWAGE PUMPING STATION | NEW ELLERBY/CSO | WRA8861 | WRA8861 | 1 | SO on sewer network | TA1673039180 | 516737 | 439184 | GB104026066860 | Lambwath Stream from Source to Foredyke Stream | River | 3274 | Lower Hull | 3039 | Hull and East Riding | A TRIBUTARY OF KELWELL DRAIN | Not Applicable | Not Applicable | Not Applicable | 610:15 | 72 | 69.8 | 2020 | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement ongoing | SOAF investigation ongoing | YWS01984
YWS01985 | Yorkshire Water | Live | NEW ELLERBY STW | NEW ELLERBY/STW | WRA8862 | WRA8862 | 2 | Inlet SO at WwTW | TA1667040300 | 516670 | 440300 | GB104026066860 | Lambwath Stream from Source to Foredyke Stream | River | 3274 | Lower Hull | 3039 | Hull and East Riding | LAMBWATH STREAM | Not Applicable | Not Applicable | Not Applicable | 1563:45 | 149 | 32.4 | 2020 | 99.98 |  |  | Performance - Pump failure / issue | High spill threshold not met | UWWTR investigation ongoing, Operational investigation completed | Operational improvement completed | SOAF investigation ongoing | YWS01985
YWS01986 | Yorkshire Water | Live | SALTAIRE ROAD NO 2 CSO | SALTAIRE ROAD/NO 2 CSO | WRA8895 | WRA8895 | A1 | SO on sewer network | SE1281740140 | 412817 | 440140 | GB104027063034 | Aire (R Worth to Gill Beck) | River | 3307 | Middle Aire | 3001 | Aire and Calder | LOADPIT BECK | Not Applicable | Not Applicable | Not Applicable | 11:45 | 15 | 20.8 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01986
YWS01987 | Yorkshire Water | Live | LEEDS WEST PARK CSO | LEEDS WEST PARK/NO 2 CSO | WRA8896 | WRA8896 | 1 | SO on sewer network | SE2593038110 | 425933 | 438111 | GB104027062920 | Carlton Beck from Source to River Aire | River | 3265 | Lower Aire | 3001 | Aire and Calder | CULVERTED TRIB OF OIL MILL BCK | Not Applicable | Not Applicable | Not Applicable | 3:30 | 5 | 19 | 2020 | 99.89 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01987
YWS01988 | Yorkshire Water | Live | ROYAL OAK RAWCLIFFE SPS | ROYAL OAK RAWCLIFFE/CSO | WRA8920 | WRA8920 | A2 | Storm discharge at pumping station | SE6821623206 | 468216 | 423206 | GB104027062760 | Aire from River Calder to River Ouse | River | 3265 | Lower Aire | 3001 | Aire and Calder | RIVER AIRE (TIDAL) | Not Applicable | Not Applicable | Not Applicable | 27:00 | 32 | 74.2 | 2020 | 99.99 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement ongoing | SOAF investigation ongoing | YWS01988
YWS01989 | Yorkshire Water | Live | RAWCLIFFE BANKSIDE STW | RAWCLIFFE BANKSIDE/STW | WRA8921 | WRA8921 | 2 | Inlet SO at WwTW | SE6860023410 | 468600 | 423410 | GB104027062760 | Aire from River Calder to River Ouse | River | 3265 | Lower Aire | 3001 | Aire and Calder | RIVER AIRE (TIDAL) | Not Applicable | Not Applicable | Not Applicable | 319:45 | 81 | 109 | 2020 | 99.89 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement completed | SOAF investigation ongoing | YWS01989
YWS01990 | Yorkshire Water | Live | WISEWOOD ROAD CSO | WISEWOOD ROAD/CSO | WRA9024 | WRA9024 | A1 | SO on sewer network | SK3240589402 | 432405 | 389402 | GB104027057370 | Loxley from Strines Dyke to River Don | River | 3490 | Upper Don | 3029 | Don and Rother | RIVER LOXLEY | Not Applicable | Not Applicable | Not Applicable | 64:00 | 39 | 32.8 | 2020 | 98.73 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01990
YWS01991 | Yorkshire Water | Live | STAITHES ROAD NO.2 SPS | STAITHES RD PRESTON/CSO | WRA9026 | WRA9026 | 1 | SO on sewer network | TA1816030260 | 518233 | 430278 | GB104026067200 | Burstwick Drain from Source to Humber | River | 3057 | Burstwick and Eastern Drains | 3039 | Hull and East Riding | UNNAMED TRIB OF REDMERE SEWER | Not Applicable | Not Applicable | Not Applicable | 0:45 | 1 | 0.4 | 2020 | 99.87 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01991
YWS01992 | Yorkshire Water | Live | NEWLANDS NO 2 CSO | NEWLANDS/NO 2 CSO | WRA9032 | WRA9032 | A1 | SO on sewer network | SE0061353356 | 400613 | 453356 | GB104027063060 | Haw Beck from Source to Eller beck | River | 3484 | Upper Aire | 3001 | Aire and Calder | EMBSAY BECK | Not Applicable | Not Applicable | Not Applicable | 13:15 | 12 | 12.6 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01992
YWS01993 | Yorkshire Water | Live | ROTHERSIDE ROAD CSO | ROTHERSIDE ROAD/CSO | WRA9068 | WRA9068 | A1 | SO on sewer network | SK4353179794 | 443531 | 379794 | GB104027057720 | The Moss from Source to River Rother | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | RIVER MOSS | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01993
YWS01994 | Yorkshire Water | Live | DENE PLACE NO 2 CSO | DENE PLACE/NO 2 CSO | WRA9083 | WRA9083 | A1 | SO on sewer network | SE0912225732 | 409122 | 425732 | GB104027062780 | Hebble Brook from Source to River Calder | River | 3310 | Middle Calder | 3001 | Aire and Calder | HEBBLE BROOK | Not Applicable | Not Applicable | Not Applicable | 35:45 | 18 | 35 | 2020 | 99.87 |  |  | High spill threshold not met | High spill threshold not met | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS01994
YWS01995 | Yorkshire Water | Live | LEDGARD WAY CSO | LEDGARD WAY/CSO | WRA9084 | WRA9084 | A1 | SO on sewer network | SE2774134099 | 427741 | 434099 | GB104027063032 | Aire from Gill Beck (Baildon) to River Calder | River | 3265 | Lower Aire | 3001 | Aire and Calder | RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 9:15 | 5 | 28.8 | 2020 | 8.44 | Sensor failure / issue | Resolved - January after reporting year | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01995
YWS01996 | Yorkshire Water | Live | BRIMINGTON ROAD NORTH CSO | BRIMINGTON ROAD NTH/CSO | WRA9088 | WRA9088 | A1 | SO on sewer network | SK3893073717 | 438930 | 373717 | GB104027057710 | Drone/Whitting from Source to River Rother | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | RIVER WHITTING | Not Applicable | Not Applicable | Not Applicable | 482:15 | 80 | 81.6 | 2020 | 99.41 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS01996
YWS01997 | Yorkshire Water | Live | HASLAND BY-PASS CSO | HASLAND BY-PASS/CSO | WRA9089 | WRA9089 | A1 | SO on sewer network | SK3930670262 | 439306 | 370262 | GB104027057640 | Spital/Calow/Muster Brook | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | SPITTAL BROOK | Not Applicable | Not Applicable | Not Applicable | 151:00 | 37 | 60.4 | 2020 | 99.65 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation ongoing | Operational improvement ongoing | SOAF investigation ongoing | YWS01997
YWS01998 | Yorkshire Water | Live | DERBY ROAD NORTH CSO | DERBY ROAD NORTH/CSO | WRA9090 | WRA9090 | A1 | SO on sewer network | SK3855470172 | 438554 | 370172 | GB104027057630 | Rother from Redleadmill Brook to Spital Brook | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | RIVER ROTHER | Not Applicable | Not Applicable | Not Applicable | 70:15 | 11 | 22.6 | 2020 | 96.92 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01998
YWS01999 | Yorkshire Water | Live | DERBY ROAD GARAGE CSO | DERBY ROAD GARAGE/CSO | WRA9091 | WRA9091 | 1 | SO on sewer network | SK3842069870 | 438427 | 369871 | GB104027057630 | Rother from Redleadmill Brook to Spital Brook | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | RIVER ROTHER | Not Applicable | Not Applicable | Not Applicable | 70:30 | 14 | 14.2 | 2020 | 99.39 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS01999
YWS02000 | Yorkshire Water | Live | DERBY ROAD 242 CSO | DERBY ROAD 242/CSO | WRA9092 | WRA9092 | A1 | SO on sewer network | SK3848369695 | 438483 | 369695 | GB104027057630 | Rother from Redleadmill Brook to Spital Brook | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | RIVER ROTHER VIA SWS | Not Applicable | Not Applicable | Not Applicable | 7:15 | 8 | 7.2 | 2020 | 99.96 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02000
YWS02001 | Yorkshire Water | Live | OLD ROAD CHESTERFIELD CSO | OLD ROAD CHESTERFIELD/CSO | WRA9093 | WRA9093 | A1 | SO on sewer network | SK3683970773 | 436839 | 370773 | GB104027057660 | Hipper from Source to River Rother | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | RIVER HIPPER | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 1 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02001
YWS02002 | Yorkshire Water | Live | CHURCH VIEW CSO | CHURCH VIEW/CSO | WRA9094 | WRA9094 | 1 | SO on sewer network | SK3700070870 | 437001 | 370878 | GB104027057660 | Hipper from Source to River Rother | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | RIVER HIPPER | Not Applicable | Not Applicable | Not Applicable | 3:45 | 2 | 3.8 | 2020 | 99.8 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02002
YWS02003 | Yorkshire Water | Live | CHATSWORTH ROAD CSO | CHATSWORTH ROAD/CSO | WRA9095 | WRA9095 | A1 | SO on sewer network | SK3720670887 | 437206 | 370887 | GB104027057660 | Hipper from Source to River Rother | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | RIVER HIPPER | Not Applicable | Not Applicable | Not Applicable | 16:15 | 18 | 14.8 | 2020 | 99.76 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02003
YWS02004 | Yorkshire Water | Live | DOCK WALK CSO | DOCK WALK/CSO | WRA9097 | WRA9097 | 1 | SO on sewer network | SK3764070920 | 437641 | 370922 | GB104027057660 | Hipper from Source to River Rother | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | RIVER HIPPER | Not Applicable | Not Applicable | Not Applicable | 48:45 | 15 | 11.4 | 2020 | 83.58 | Sensor failure / issue | Resolved - Nov | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02004
YWS02005 | Yorkshire Water | Live | NORTH BRIMINGTON WORKS CSO | NORTH BRIMINGTON WKS/CSO | WRA9098 | WRA9098 | 1 | SO on sewer network | SK3868073820 | 438687 | 373826 | GB104027057710 | Drone/Whitting from Source to River Rother | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | RIVER WHITTING | Not Applicable | Not Applicable | Not Applicable | 1:45 | 1 | 2 | 2020 | 99.93 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02005
YWS02006 | Yorkshire Water | Live | FIELDEN TERRACE CSO | FIELDEN TERRACE/CSO | WRA9099 | WRA9099 | A1 | SO on sewer network | SD9374924768 | 393749 | 424768 | GB104027062660 | Calder from Source to Walsden Water | River | 3487 | Upper Calder | 3001 | Aire and Calder | OAK HILL CLOUGH | Not Applicable | Not Applicable | Not Applicable | 303:00 | 100 | 28.4 | 2020 | 99.82 |  |  | Performance - Infiltration | High spill threshold not met | UWWTR investigation ongoing, Operational investigation ongoing | Operational improvement ongoing | SOAF investigation ongoing | YWS02006
YWS02007 | Yorkshire Water | Live | FERNHILL CSO | FERN HILL/CSO | WRA9100 | WRA9100 | 1 | SO on sewer network | SD9198025660 | 391981 | 425669 | GB104027062660 | Calder from Source to Walsden Water | River | 3487 | Upper Calder | 3001 | Aire and Calder | RIVER CALDER | Not Applicable | Not Applicable | Not Applicable | 13:45 | 11 | 2.75 | 2020 | 95.24 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02007
YWS02008 | Yorkshire Water | Live | MITCHELL STREET CSO | MITCHELL STREET/CSO | WRA9101 | WRA9101 | A1 | SO on sewer network | SD9233725503 | 392337 | 425503 | GB104027062660 | Calder from Source to Walsden Water | River | 3487 | Upper Calder | 3001 | Aire and Calder | RIVER CALDER | Not Applicable | Not Applicable | Not Applicable | 14:00 | 7 | 3.33 | 2020 | 78.93 | Comms failure / issue | Resolved - Oct | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02008
YWS02009 | Yorkshire Water | Live | GLEN LEE LANE CSO | GLEN LEE LANE/CSO | WRA9102 | WRA9102 | 1 | SO on sewer network | SE0680040270 | 406805 | 440277 | GB104027062891 | Worth from Bridgehouse Beck to R Aire | River | 3307 | Middle Aire | 3001 | Aire and Calder | HOG HOLES BECK | Not Applicable | Not Applicable | Not Applicable | 1:15 | 4 | 7.6 | 2020 | 99.42 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02009
YWS02010 | Yorkshire Water | Live | WORTH WAY SUN STREET CSO | WORTH WAY SUN STREET/CSO | WRA9103 | WRA9103 | A1 | SO on sewer network | SE0618440632 | 406184 | 440632 | GB104027062891 | Worth from Bridgehouse Beck to R Aire | River | 3307 | Middle Aire | 3001 | Aire and Calder | RIVER WORTH | Not Applicable | Not Applicable | Not Applicable | 25:30 | 25 | 36.6 | 2020 | 85.83 | Comms failure / issue | Resolved - Oct | High spill threshold not met | High spill threshold not met | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS02010
YWS02011 | Yorkshire Water | Live | WOODHOUSE ROAD 36 CSO | WOODHOUSE ROAD 36/CSO | WRA9104 | WRA9104 | A1 | SO on sewer network | SE0601540208 | 406015 | 440208 | GB104027062891 | Worth from Bridgehouse Beck to R Aire | River | 3307 | Middle Aire | 3001 | Aire and Calder | RIVER WORTH | Not Applicable | Not Applicable | Not Applicable | 0:45 | 3 | 8.4 | 2020 | 99.98 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02011
YWS02012 | Yorkshire Water | Live | WOODHOUSE ROAD 38 CSO | WOODHOUSE RD 38/CSO | WRA9105 | WRA9105 | A1 | SO on sewer network | SE0588640188 | 405886 | 440188 | GB104027062891 | Worth from Bridgehouse Beck to R Aire | River | 3307 | Middle Aire | 3001 | Aire and Calder | RIVER WORTH | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0 | 2023 | 97.73 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02012
YWS02013 | Yorkshire Water | Live | BRIDGE INN KEIGHLEY CSO | BRIDGE INN KEIGHLEY/CSO | WRA9107 | WRA9107 | 1 | SO on sewer network | SE0742042220 | 407427 | 442220 | GB104027063033 | Aire (Eshton Beck to R Worth) | River | 3484 | Upper Aire | 3001 | Aire and Calder | RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0.4 | 2020 | 99.67 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02013
YWS02014 | Yorkshire Water | Live | DEAN BECK CSO | DEAN BECK/CSO | WRA9108 | WRA9108 | A1 | SO on sewer network | SE2542530001 | 425425 | 430001 | GB104027062830 | Low/Wortley/Pudsey Bks | River | 3265 | Lower Aire | 3001 | Aire and Calder | FARNLEY WOOD BECK | Not Applicable | Not Applicable | Not Applicable | 152:45 | 61 | 71 | 2020 | 83.13 | Sensor failure / issue | Resolved - Jul | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement ongoing | SOAF investigation ongoing | YWS02014
YWS02015 | Yorkshire Water | Live | CHURWELL HILL CSO | CHURWELL HILL/CSO | WRA9109 | WRA9109 | A1 | SO on sewer network | SE2765129885 | 427651 | 429885 | GB104027062750 | Milshaw Beck from Source to Low/Wortley/Pudsey Bks | River | 3265 | Lower Aire | 3001 | Aire and Calder | FARNLEY WOOD BECK | Not Applicable | Not Applicable | Not Applicable | 2:45 | 6 | 4.2 | 2020 | 99.86 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02015
YWS02016 | Yorkshire Water | Live | BAPTISTS LANE CSO | BAPTIST LANE/CSO | WRA9111 | WRA9111 | A1 | SO on sewer network | SE2963219839 | 429632 | 419839 | GB104027062631 | Calder from River Colne to River Chald | River | 3268 | Lower Calder | 3001 | Aire and Calder | SPRING MILL BECK | Not Applicable | Not Applicable | Not Applicable | 63:15 | 41 | 41.4 | 2020 | 98.27 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS02016
YWS02017 | Yorkshire Water | Live | BROOMGROVE ROAD CSO | BROOMGROVE ROAD/CSO | WRA9112 | WRA9112 | A1 | SO on sewer network | SK3401085930 | 434010 | 385930 | GB104027057760 | Porter from Source to River Sheaf | River | 3312 | Middle Don | 3029 | Don and Rother | PORTER BROOK | Not Applicable | Not Applicable | Not Applicable | 3:30 | 9 | 18.4 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02017
YWS02018 | Yorkshire Water | Live | FRASER ROAD CSO | FRASER ROAD/CSO | WRA9113 | WRA9113 | A1 | SO on sewer network | SK3425183281 | 434251 | 383281 | GB104027057750 | Sheaf from Source to River Don | River | 3312 | Middle Don | 3029 | Don and Rother | RIVER SHEAF | Not Applicable | Not Applicable | Not Applicable | 0:15 | 1 | 4 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02018
YWS02019 | Yorkshire Water | Live | SNAITHING PARK ROAD CSO | SNAITHING PARK ROAD/CSO | WRA9115 | WRA9115 | 1 | SO on sewer network | SK3116086220 | 431161 | 386222 | GB104027057760 | Porter from Source to River Sheaf | River | 3312 | Middle Don | 3029 | Don and Rother | TRIBUTARY OF PORTER BROOK | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0.8 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02019
YWS02020 | Yorkshire Water | Live | SNAITHING LANE CSO | SNAITHING LANE/CSO | WRA9116 | WRA9116 | 1 | SO on sewer network | SK3133086170 | 431332 | 386171 | GB104027057760 | Porter from Source to River Sheaf | River | 3312 | Middle Don | 3029 | Don and Rother | TRIBUTARY OF PORTER BROOK | Not Applicable | Not Applicable | Not Applicable | 2:15 | 3 | 2.6 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02020
YWS02021 | Yorkshire Water | Live | STUMPERLOWE ROAD CSO | STUMPERLOWE CRES ROAD/CSO | WRA9117 | WRA9117 | A1 | SO on sewer network | SK3145485845 | 431454 | 385845 | GB104027057760 | Porter from Source to River Sheaf | River | 3312 | Middle Don | 3029 | Don and Rother | PORTER BROOK | Not Applicable | Not Applicable | Not Applicable | 14:00 | 18 | 21.6 | 2020 | 98.03 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02021
YWS02022 | Yorkshire Water | Live | GLOBE ROAD CSO | GLOBE ROAD/CSO | WRA9118 | WRA9118 | 1 | SO on sewer network | SE2966032930 | 429662 | 432932 | GB104027062830 | Low/Wortley/Pudsey Bks | River | 3265 | Lower Aire | 3001 | Aire and Calder | HOL BECK | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02022
YWS02023 | Yorkshire Water | Live | CRICKET INN CRESCENT CSO | CRICKET INN CRESCENT/CSO | WRA9122 | WRA9122 | A1 | SO on sewer network | SK3727187549 | 437145 | 388112 | GB104027057412 | Don from River Loxley confl to River Don Works | River | 3312 | Middle Don | 3029 | Don and Rother | RIVER DON | Not Applicable | Not Applicable | Not Applicable | 71:00 | 41 | 46 | 2020 | 100 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement ongoing | SOAF investigation ongoing | YWS02023
YWS02024 | Yorkshire Water | Live | ATTERCLIFFE COMMON CSO | ATTERCLIFFE COMMON/CSO | WRA9123 | WRA9123 | 1 | SO on sewer network | SK3802089390 | 438144 | 389097 | GB104027057412 | Don from River Loxley confl to River Don Works | River | 3312 | Middle Don | 3029 | Don and Rother | RIVER DON | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0.4 | 2020 | 99.8 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02024
YWS02025 | Yorkshire Water | Live | ATTERCLIFFE HILL CSO | ATTERCLIFFE HILL/CSO | WRA9124 | WRA9124 | A1 | SO on sewer network | SK3814489097 | 438144 | 389097 | GB104027057412 | Don from River Loxley confl to River Don Works | River | 3312 | Middle Don | 3029 | Don and Rother | KIRK BRIDGE DIKE | Not Applicable | Not Applicable | Not Applicable | 0:15 | 1 | 3 | 2020 | 99.77 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02025
YWS02026 | Yorkshire Water | Live | NEWMAN DRIVE CSO | NEWMAN DRIVE/CSO | WRA9127 | WRA9127 | A1 | SO on sewer network | SK3802691537 | 438026 | 391537 | GB104027057440 | Blackburn Brook from Source to River Don | River | 3312 | Middle Don | 3029 | Don and Rother | TRIBUTARY OF BLACKBURN BROOK | Not Applicable | Not Applicable | Not Applicable | 5:15 | 9 | 2.4 | 2020 | 96.08 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02026
YWS02027 | Yorkshire Water | Live | MEADOWHALL WAY NO.2 CSO | MEADOWHALL WAY/NO 2 CSO | WRA9128 | WRA9128 | 1 | SO on sewer network | SK3827090200 | 438275 | 390200 | GB104027057412 | Don from River Loxley confl to River Don Works | River | 3312 | Middle Don | 3029 | Don and Rother | RIVER DON | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0.2 | 2020 | 99.86 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02027
YWS02029 | Yorkshire Water | Live | WAINGATE CSO | WAINGATE/CSO | WRA9130 | WRA9130 | A1 | SO on sewer network | SK3572487758 | 435724 | 387758 | GB104027057412 | Don from River Loxley confl to River Don Works | River | 3312 | Middle Don | 3029 | Don and Rother | RIVER DON | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02029
YWS02030 | Yorkshire Water | Live | HILL BRIDGE CSO | HILL BRIDGE/CSO | WRA9131 | WRA9131 | A1 | SO on sewer network | SK3327689572 | 433276 | 389572 | GB104027057370 | Loxley from Strines Dyke to River Don | River | 3490 | Upper Don | 3029 | Don and Rother | RIVER LOXLEY | Not Applicable | Not Applicable | Not Applicable | 61:00 | 49 | 46.6 | 2020 | 88.47 | Comms failure / issue | Resolved - Dec | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS02030
YWS02031 | Yorkshire Water | Live | RUDYARD ROAD CSO | RUDYARD ROAD/CSO | WRA9134 | WRA9134 | A1 | SO on sewer network | SK3331089618 | 433310 | 389618 | GB104027057370 | Loxley from Strines Dyke to River Don | River | 3490 | Upper Don | 3029 | Don and Rother | RIVER LOXLEY | Not Applicable | Not Applicable | Not Applicable | 0:30 | 2 | 2.8 | 2020 | 99.98 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02031
YWS02032 | Yorkshire Water | Live | ST MARY'S ROAD CSO | ST MARYS ROAD/CSO | WRA9135 | WRA9135 | A1 | SO on sewer network | SK3584386563 | 435843 | 386563 | GB104027057750 | Sheaf from Source to River Don | River | 3312 | Middle Don | 3029 | Don and Rother | RIVER SHEAF | Not Applicable | Not Applicable | Not Applicable | 15:45 | 11 | 13.2 | 2020 | 99.75 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02032
YWS02033 | Yorkshire Water | Live | VULCAN ROAD CSO | VULCAN ROAD/CSO | WRA9136 | WRA9136 | 1 | SO on sewer network | SK3956090610 | 439569 | 390615 | GB104027057413 | Don from River Don Works to River Rother | River | 3312 | Middle Don | 3029 | Don and Rother | TRIBUTARY OF THE RIVER DON | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0.4 | 2020 | 99.54 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02033
YWS02034 | Yorkshire Water | Live | EFFINGHAM STREET CSO | EFFINGHAM STREET/CSO | WRA9137 | WRA9137 | 1 | SO on sewer network | SK3635088100 | 436353 | 388105 | GB104027057412 | Don from River Loxley confl to River Don Works | River | 3312 | Middle Don | 3029 | Don and Rother | RIVER DON | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0.4 | 2020 | 99.13 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02034
YWS02035 | Yorkshire Water | Live | HORSEWOOD ROAD CSO | HORSEWOOD ROAD/CSO | WRA9138 | WRA9138 | 1 | SO on sewer network | SK4279085530 | 442799 | 385532 | GB104027057772 | Rother, Doe Lea to Don | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | SHIRTCLIFF BROOK | Not Applicable | Not Applicable | Not Applicable | 17:00 | 4 | 13.8 | 2020 | 99.67 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02035
YWS02037 | Yorkshire Water | Live | ASLING ROAD CSO | ALSING ROAD/CSO | WRA9141 | WRA9141 | 1 | SO on sewer network | SK3928091340 | 439288 | 391340 | GB104027057440 | Blackburn Brook from Source to River Don | River | 3312 | Middle Don | 3029 | Don and Rother | BLACKBURN BROOK | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0 | 2020 | 99.76 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02037
YWS02038 | Yorkshire Water | Live | SOUTH PARKWAY CSO | SOUTH PARKWAY/CSO | WRA9142 | WRA9142 | A1 | SO on sewer network | SE3426935278 | 434269 | 435278 | GB104027062880 | Wyke Beck from Source to River Aire | River | 3265 | Lower Aire | 3001 | Aire and Calder | WYKE BECK | Not Applicable | Not Applicable | Not Applicable | 59:45 | 49 | 19 | 2020 | 99.92 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02038
YWS02039 | Yorkshire Water | Live | FOUNDRY MILL CSO | FOUNDRY MILL STREET/CSO | WRA9143 | WRA9143 | 1 | SO on sewer network | SE3422035220 | 434225 | 435228 | GB104027062880 | Wyke Beck from Source to River Aire | River | 3265 | Lower Aire | 3001 | Aire and Calder | WYKE BECK | Not Applicable | Not Applicable | Not Applicable | 2:00 | 4 | 2.2 | 2020 | 99.89 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02039
YWS02040 | Yorkshire Water | Live | STOCKS RISE CSO | STOCKS RISE/CSO | WRA9144 | WRA9144 | A1 | SO on sewer network | SE3589835598 | 435898 | 435598 | GB104027062880 | Wyke Beck from Source to River Aire | River | 3265 | Lower Aire | 3001 | Aire and Calder | WYKE BECK | Not Applicable | Not Applicable | Not Applicable | 110:45 | 39 | 40.6 | 2020 | 99.82 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS02040
YWS02041 | Yorkshire Water | Live | SPEN LANE 185 CSO | SPEN LANE 185/CSO | WRA9145 | WRA9145 | A1 | SO on sewer network | SE2610736731 | 426107 | 436731 | GB104027063032 | Aire from Gill Beck (Baildon) to River Calder | River | 3265 | Lower Aire | 3001 | Aire and Calder | CULVERTED TRIB OF RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 25.33 | 2020 | 5.57 | Sensor failure / issue | Resolved - Dec | High spill threshold not met | High spill threshold not met | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS02041
YWS02042 | Yorkshire Water | Live | MILFORD PLACE CSO | MILFORD PLACE/CSO | WRA9146 | WRA9146 | 1 | SO on sewer network | SE2775034120 | 427757 | 434128 | GB104027063032 | Aire from Gill Beck (Baildon) to River Calder | River | 3265 | Lower Aire | 3001 | Aire and Calder | RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 153:15 | 57 | 46.2 | 2020 | 98.76 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS02042
YWS02043 | Yorkshire Water | Live | PARKWAY CLOSE CSO | PARKWAY CLOSE/CSO | WRA9147 | WRA9147 | A1 | SO on sewer network | SE3426135323 | 434261 | 435323 | GB104027062880 | Wyke Beck from Source to River Aire | River | 3265 | Lower Aire | 3001 | Aire and Calder | WYKE BECK | Not Applicable | Not Applicable | Not Applicable | 17:15 | 19 | 9 | 2020 | 99.87 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02043
YWS02044 | Yorkshire Water | Live | GLEADLESS ROAD CSO | GLEADLESS ROAD/CSO | WRA9148 | WRA9148 | A1 | SO on sewer network | SK3652584554 | 436525 | 384554 | GB104027057750 | Sheaf from Source to River Don | River | 3312 | Middle Don | 3029 | Don and Rother | TRIBUTARY OF MEERS BROOK | Not Applicable | Not Applicable | Not Applicable | 44:15 | 28 | 37.4 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02044
YWS02045 | Yorkshire Water | Live | HOLLIN DRIVE CSO | HOLLIN DRIVE/CSO | WRA9149 | WRA9149 | A1 | SO on sewer network | SE2814537212 | 428145 | 437212 | GB104027062900 | Meanwood Beck from Source to River Aire | River | 3265 | Lower Aire | 3001 | Aire and Calder | MEANWOOD BECK | Not Applicable | Not Applicable | Not Applicable | 117:45 | 57 | 28.8 | 2020 | 96.1 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02045
YWS02046 | Yorkshire Water | Live | CARR MANOR ROAD CSO | CARR MANOR ROAD/CSO | WRA9150 | WRA9150 | 1 | SO on sewer network | SE2955037600 | 429552 | 437606 | GB104027062900 | Meanwood Beck from Source to River Aire | River | 3265 | Lower Aire | 3001 | Aire and Calder | TRIBUTARY OF STAIN BECK | Not Applicable | Not Applicable | Not Applicable | 0:45 | 1 | 1.8 | 2020 | 24.12 | Sensor failure / issue | Resolved - Dec | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02046
YWS02047 | Yorkshire Water | Live | MEANWOOD PARK CSO | MEANWOOD PARK/CSO | WRA9151 | WRA9151 | A1 | SO on sewer network | SE2790738053 | 427907 | 438053 | GB104027062900 | Meanwood Beck from Source to River Aire | River | 3265 | Lower Aire | 3001 | Aire and Calder | MEANWOOD BECK | Not Applicable | Not Applicable | Not Applicable | 14:45 | 21 | 36 | 2020 | 99.76 |  |  | High spill threshold not met | High spill threshold not met | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS02047
YWS02048 | Yorkshire Water | Live | STAIRFOOT LANE CSO | STAIRFOOT LANE/CSO | WRA9152 | WRA9152 | A1 | SO on sewer network | SE2788540269 | 427885 | 440269 | GB104027062900 | Meanwood Beck from Source to River Aire | River | 3265 | Lower Aire | 3001 | Aire and Calder | ADEL BECK | Not Applicable | Not Applicable | Not Applicable | 4:15 | 6 | 6.8 | 2020 | 59.96 | Comms failure / issue | Resolved - Sep | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02048
YWS02049 | Yorkshire Water | Live | OAKFIELD WOOD LANE CSO | OAKFIELD WOOD LANE/CSO | WRA9153 | WRA9153 | 1 | SO on sewer network | SE2860036350 | 428609 | 436357 | GB104027062900 | Meanwood Beck from Source to River Aire | River | 3265 | Lower Aire | 3001 | Aire and Calder | MEANWOOD BECK | Not Applicable | Not Applicable | Not Applicable | 0:15 | 1 | 1 | 2020 | 79.56 | Comms failure / issue | Resolved - February after reporting year | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02049
YWS02050 | Yorkshire Water | Live | THORNTON ROAD 201 CSO | THORNTON ROAD 201/CSO | WRA9155 | WRA9155 | 1 | SO on sewer network | SE0907032800 | 409065 | 432742 | GB104027062861 | Clayton Beck (Source to Bradford Bk) | River | 3307 | Middle Aire | 3001 | Aire and Calder | PINCH BECK | Not Applicable | Not Applicable | Not Applicable | 0:15 | 1 | 0.2 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02050
YWS02051 | Yorkshire Water | Live | DAWSONS HILL CSO | DAWSONS HILL/CSO | WRA9156 | WRA9156 | 1 | SO on sewer network | SE1015032370 | 410150 | 432370 | GB104027062861 | Clayton Beck (Source to Bradford Bk) | River | 3307 | Middle Aire | 3001 | Aire and Calder | PINCH BECK | Not Applicable | Not Applicable | Not Applicable | 71:45 | 5 | 1.2 | 2020 | 97.19 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02051
YWS02052 | Yorkshire Water | Live | SPENCER ROAD CSO | SPENCER ROAD/CSO | WRA9158 | WRA9158 | A1 | SO on sewer network | SE1457332413 | 414573 | 432413 | GB104027062862 | Bradford Beck (Clayton Bk to R Aire) | River | 3307 | Middle Aire | 3001 | Aire and Calder | HORTON BECK (WEST BROOK) | Not Applicable | Not Applicable | Not Applicable | 9:15 | 15 | 12.8 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02052
YWS02053 | Yorkshire Water | Live | ROSLYN PLACE CSO | ROSLYN PLACE/CSO | WRA9159 | WRA9159 | 1 | SO on sewer network | SE1492032590 | 414925 | 432590 | GB104027062862 | Bradford Beck (Clayton Bk to R Aire) | River | 3307 | Middle Aire | 3001 | Aire and Calder | HORTON BECK | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 2.4 | 2020 | 95.23 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02053
YWS02054 | Yorkshire Water | Live | BIRCH LANE CSO | BIRCH LANE/CSO | WRA9160 | WRA9160 | A1 | SO on sewer network | SE1662031050 | 416620 | 431050 | GB104027062862 | Bradford Beck (Clayton Bk to R Aire) | River | 3307 | Middle Aire | 3001 | Aire and Calder | TRIBUTARY OF BOWLING BECK | Not Applicable | Not Applicable | Not Applicable | 3:15 | 6 | 5.6 | 2020 | 98.13 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02054
YWS02055 | Yorkshire Water | Live | QUEENS ROAD BRADFORD CSO | QUEENS ROAD BRADFORD/CSO | WRA9161 | WRA9161 | 1 | SO on sewer network | SE1643034890 | 416436 | 434890 | GB104027062862 | Bradford Beck (Clayton Bk to R Aire) | River | 3307 | Middle Aire | 3001 | Aire and Calder | BOLTON BECK | Not Applicable | Not Applicable | Not Applicable | 4:15 | 8 | 15.2 | 2020 | 99.94 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02055
YWS02056 | Yorkshire Water | Live | ASHBOURNE ROAD CSO | ASHBOURNE ROAD/CSO | WRA9162 | WRA9162 | A1 | SO on sewer network | SE1676235120 | 416762 | 435120 | GB104027062862 | Bradford Beck (Clayton Bk to R Aire) | River | 3307 | Middle Aire | 3001 | Aire and Calder | BOLTON BECK | Not Applicable | Not Applicable | Not Applicable | 40:15 | 37 | 39 | 2020 | 96.75 |  |  | High spill threshold not met | High spill threshold not met | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS02056
YWS02057 | Yorkshire Water | Live | UPPER PARK HOUSE CSO | UPPER PARK HOUSE/CSO | WRA9163 | WRA9163 | 1 | SO on sewer network | SE1644029120 | 416440 | 429123 | GB104027062710 | Spen Beck from Source to River Calder | River | 3268 | Lower Calder | 3001 | Aire and Calder | LOW MOOR BECK | Not Applicable | Not Applicable | Not Applicable | 1:00 | 2 | 1.4 | 2020 | 99.89 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02057
YWS02058 | Yorkshire Water | Live | CLECKHEATON ROAD CSO | CLECKHEATON ROAD/CSO | WRA9164 | WRA9164 | 1 | SO on sewer network | SE1594029160 | 415931 | 429155 | GB104027062710 | Spen Beck from Source to River Calder | River | 3268 | Lower Calder | 3001 | Aire and Calder | TRIBUTARY OF LOW MOOR BECK | Not Applicable | Not Applicable | Not Applicable | 8:45 | 17 | 8.5 | 2023 | 98.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02058
YWS02059 | Yorkshire Water | Live | ROOLEY AVENUE CSO | ROOLEY AVENUE/CSO | WRA9165 | WRA9165 | A1 | SO on sewer network | SE1598829987 | 415988 | 429987 | GB104027062710 | Spen Beck from Source to River Calder | River | 3268 | Lower Calder | 3001 | Aire and Calder | DEAN BECK | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0 | 2020 | 99.95 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02059
YWS02060 | Yorkshire Water | Live | COMMON ROAD CSO | COMMON ROAD/CSO | WRA9166 | WRA9166 | A1 | SO on sewer network | SE1563328782 | 415633 | 428782 | GB104027062710 | Spen Beck from Source to River Calder | River | 3268 | Lower Calder | 3001 | Aire and Calder | TRIBUTARY OF LOW MOOR BECK | Not Applicable | Not Applicable | Not Applicable | 0:30 | 1 | 0.4 | 2020 | 97.4 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02060
YWS02061 | Yorkshire Water | Live | SMITH AVENUE CSO | SMITH AVENUE/CSO | WRA9167 | WRA9167 | A1 | SO on sewer network | SE1531329890 | 415313 | 429890 | GB104027062710 | Spen Beck from Source to River Calder | River | 3268 | Lower Calder | 3001 | Aire and Calder | TRIBUTARY OF LOW MOOR BECK | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0.4 | 2020 | 52.91 | Sensor failure / issue | Resolved - Oct | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02061
YWS02062 | Yorkshire Water | Live | CALDER BANK ROAD CSO | CALDER BANK ROAD/CSO | WRA9168 | WRA9168 | A1 | SO on sewer network | SE2401021055 | 424010 | 421055 | GB104027062631 | Calder from River Colne to River Chald | River | 3268 | Lower Calder | 3001 | Aire and Calder | RIVER CALDER | Not Applicable | Not Applicable | Not Applicable | 10:00 | 2 | 2.5 | 2020 | 76.3 | Sensor failure / issue | Resolved - Dec | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02062
YWS02063 | Yorkshire Water | Live | THORNHILL SYPHON CSO | THORNHILL DEWSBURY/2 CSO | WRA9169 | WRA9169 | 1 | SO on sewer network | SE2549020190 | 425494 | 420193 | GB104027062631 | Calder from River Colne to River Chald | River | 3268 | Lower Calder | 3001 | Aire and Calder | RIVER CALDER | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 11.5 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02063
YWS02064 | Yorkshire Water | Live | NEWSOME ROAD CSO | NEWSOME ROAD/CSO | WRA9170 | WRA9170 | A1 | SO on sewer network | SE1470615810 | 414706 | 415810 | GB104027062550 | Colne from River Holme to River Calder | River | 3097 | Colne and Holme | 3001 | Aire and Calder | RIVER COLNE | Not Applicable | Not Applicable | Not Applicable | 77:30 | 46 | 42.4 | 2020 | 99.93 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS02064
YWS02065 | Yorkshire Water | Live | DAISY STREET CSO | DAISY STREET/CSO | WRA9171 | WRA9171 | A1 | SO on sewer network | SE1516316663 | 415163 | 416663 | GB104027062550 | Colne from River Holme to River Calder | River | 3097 | Colne and Holme | 3001 | Aire and Calder | RIVER COLNE | Not Applicable | Not Applicable | Not Applicable | 79:30 | 39 | 59 | 2020 | 66.32 | Comms failure / issue | Resolved - Aug | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS02065
YWS02066 | Yorkshire Water | Live | ANCHOR STREET CSO | ANCHOR STREET/CSO | WRA9172 | WRA9172 | A1 | SO on sewer network | SE1520817129 | 415208 | 417129 | GB104027062550 | Colne from River Holme to River Calder | River | 3097 | Colne and Holme | 3001 | Aire and Calder | RIVER COLNE | Not Applicable | Not Applicable | Not Applicable | 66:30 | 47 | 46.4 | 2020 | 99.22 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS02066
YWS02067 | Yorkshire Water | Live | ASPLEY WAKEFIELD ROAD CSO | ASPLEY WAKEFIELD RD/CSO | WRA9173 | WRA9173 | 1 | SO on sewer network | SE1538016280 | 415382 | 416286 | GB104027062550 | Colne from River Holme to River Calder | River | 3097 | Colne and Holme | 3001 | Aire and Calder | PENNY DIKE | Not Applicable | Not Applicable | Not Applicable | 40:00 | 27 | 35.4 | 2020 | 77.35 | Sensor failure / issue | Resolved - Oct | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02067
YWS02069 | Yorkshire Water | Live | BROOK MOTORS CSO | BROOK MOTORS/CSO | WRA9175 | WRA9175 | 1 | SO on sewer network | SE1384016120 | 413842 | 416120 | GB104027063330 | Colne from Wessenden Brook to R Holme | River | 3097 | Colne and Holme | 3001 | Aire and Calder | RIVER COLNE | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0.4 | 2020 | 99.72 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02069
YWS02070 | Yorkshire Water | Live | SPRINGDALE MILLS CSO | SPRINGDALE MILLS/CSO | WRA9176 | WRA9176 | 1 | SO on sewer network | SE1384016130 | 413842 | 416136 | GB104027063330 | Colne from Wessenden Brook to R Holme | River | 3097 | Colne and Holme | 3001 | Aire and Calder | RIVER COLNE | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0.8 | 2020 | 99.93 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02070
YWS02071 | Yorkshire Water | Live | ST THOMAS ROAD CSO | ST THOMAS ROAD/CSO | WRA9177 | WRA9177 | A1 | SO on sewer network | SE1360216085 | 413602 | 416085 | GB104027063330 | Colne from Wessenden Brook to R Holme | River | 3097 | Colne and Holme | 3001 | Aire and Calder | RIVER COLNE | Not Applicable | Not Applicable | Not Applicable | 40:45 | 27 | 18.8 | 2020 | 99.98 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02071
YWS02072 | Yorkshire Water | Live | GASWORKS STREET CSO | GASWORKS STREET/CSO | WRA9178 | WRA9178 | A1 | SO on sewer network | SE1515417340 | 415154 | 417340 | GB104027062550 | Colne from River Holme to River Calder | River | 3097 | Colne and Holme | 3001 | Aire and Calder | RIVER COLNE | Not Applicable | Not Applicable | Not Applicable | 65:45 | 41 | 23.6 | 2020 | 99.58 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02072
YWS02073 | Yorkshire Water | Live | CHARLIE BROWNS CSO | CHARLIE BROWNS/CSO | WRA9179 | WRA9179 | 1 | SO on sewer network | SE1353016090 | 413539 | 416091 | GB104027063330 | Colne from Wessenden Brook to R Holme | River | 3097 | Colne and Holme | 3001 | Aire and Calder | RIVER COLNE | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0.6 | 2020 | 89.13 | Sensor failure / issue | Scheduled | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02073
YWS02074 | Yorkshire Water | Live | FACTORY LANE CSO | FACTORY LANE/CSO | WRA9180 | WRA9180 | A1 | SO on sewer network | SE1202815862 | 412028 | 415862 | GB104027063330 | Colne from Wessenden Brook to R Holme | River | 3097 | Colne and Holme | 3001 | Aire and Calder | TRIBUTARY OF THE RIVER COLNE | Not Applicable | Not Applicable | Not Applicable | 62:00 | 32 | 48 | 2020 | 99.85 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | No investigation activity in reporting period | No improvement action in reporting period | SOAF investigation completed - No work required | YWS02074
YWS02075 | Yorkshire Water | Live | LOWER HIRST CSO | LOWER HIRST/CSO | WRA9181 | WRA9181 | A1 | SO on sewer network | SE0953817655 | 409538 | 417655 | GB104027063330 | Colne from Wessenden Brook to R Holme | River | 3097 | Colne and Holme | 3001 | Aire and Calder | LONGWOOD BROOK | Not Applicable | Not Applicable | Not Applicable | 13:30 | 18 | 21.2 | 2020 | 59.92 | Comms failure / issue | Scheduled | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02075
YWS02076 | Yorkshire Water | Live | LOCKWOOD SCAR CSO | LOCKWOOD SCAR/CSO | WRA9182 | WRA9182 | 1 | SO on sewer network | SE1369015110 | 413690 | 415117 | GB104027063301 | Holme from New Mill Dike to R Colne | River | 3097 | Colne and Holme | 3001 | Aire and Calder | RIVER HOLME | Not Applicable | Not Applicable | Not Applicable | 8:15 | 10 | 11.8 | 2020 | 99.89 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02076
YWS02077 | Yorkshire Water | Live | VESPER LANE CSO | VESPER LANE/CSO | WRA9183 | WRA9183 | A1 | SO on sewer network | SE2559536244 | 425595 | 436244 | GB104027063032 | Aire from Gill Beck (Baildon) to River Calder | River | 3265 | Lower Aire | 3001 | Aire and Calder | RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 2:32 | 18 | 21.6 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02077
YWS02078 | Yorkshire Water | Live | STANNINGLEY ROAD CSO | STANNINGLEY ROAD/CSO | WRA9184 | WRA9184 | 1 | SO on sewer network | SE2631034070 | 426311 | 434074 | GB104027063032 | Aire from Gill Beck (Baildon) to River Calder | River | 3265 | Lower Aire | 3001 | Aire and Calder | TRIBUTARY OF THE RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 79:45 | 50 | 28.6 | 2020 | 99.88 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02078
YWS02079 | Yorkshire Water | Live | CLAREMONT STREET CSO | CLAREMONT ST ROTHERHM/CSO | WRA9185 | WRA9185 | 1 | SO on sewer network | SK4082092580 | 440829 | 392589 | GB70410276 | Sheffield and South Yorkshire Navigation (Holmes Cut) | Canal | 2018 | Don and Rother Canals | 2001 | Humber AWB | TRIBUTARY OF HOLMES TAIL GOIT | Not Applicable | Not Applicable | Not Applicable | 0:30 | 1 | 0.2 | 2020 | 54.3 | Sensor failure / issue | Resolved - Jul | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02079
YWS02081 | Yorkshire Water | Live | WATER LANE ROTHERHAM CSO | WATER LANE ROTHERHAM/CSO | WRA9187 | WRA9187 | A1 | SO on sewer network | SK4262292482 | 442622 | 392482 | GB104027057452 | Don from River Rother to River Dearne | River | 3312 | Middle Don | 3029 | Don and Rother | RIVER DON | Not Applicable | Not Applicable | Not Applicable | 183:15 | 32 | 20 | 2020 | 96.66 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02081
YWS02082 | Yorkshire Water | Live | CLIFTON LORD STREET CSO | CLIFTON LORD STREET/CSO | WRA9188 | WRA9188 | A1 | SO on sewer network | SK4496494269 | 444964 | 394269 | GB104027057452 | Don from River Rother to River Dearne | River | 3312 | Middle Don | 3029 | Don and Rother | HERRINGTHORPE BECK | Not Applicable | Not Applicable | Not Applicable | 28:45 | 22 | 25.8 | 2020 | 99.91 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02082
YWS02083 | Yorkshire Water | Live | CANKLOW CSO | CANKLOW/CSO | WRA9189 | WRA9189 | 1 | SO on sewer network | SK4261491886 | 442614 | 391886 | GB104027057772 | Rother, Doe Lea to Don | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | RIVER ROTHER | Not Applicable | Not Applicable | Not Applicable | 12:15 | 10 | 10.4 | 2020 | 99.92 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02083
YWS02084 | Yorkshire Water | Live | HARTLEY BROOK ROAD CSO | HARTLEY BROOK ROAD/CSO | WRA9190 | WRA9190 | A1 | SO on sewer network | SK3624092747 | 436240 | 392747 | GB104027057440 | Blackburn Brook from Source to River Don | River | 3312 | Middle Don | 3029 | Don and Rother | SHEFFIELD LANE DIKE | Not Applicable | Not Applicable | Not Applicable | 21:30 | 17 | 19.4 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02084
YWS02085 | Yorkshire Water | Live | GODRIC ROAD CSO | GODRIC ROAD/CSO | WRA9191 | WRA9191 | A1 | SO on sewer network | SK3627093230 | 436270 | 393230 | GB104027057440 | Blackburn Brook from Source to River Don | River | 3312 | Middle Don | 3029 | Don and Rother | HARTLEY BROOK DIKE | Not Applicable | Not Applicable | Not Applicable | 51:30 | 21 | 26.6 | 2020 | 99.94 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02085
YWS02086 | Yorkshire Water | Live | WOODSEATS ROAD 1 CSO | WOODSEATS ROAD 1/CSO | WRA9192 | WRA9192 | 1 | SO on sewer network | SK3437083910 | 434373 | 383910 | GB104027057750 | Sheaf from Source to River Don | River | 3312 | Middle Don | 3029 | Don and Rother | RIVER SHEAF | Not Applicable | Not Applicable | Not Applicable | 1:45 | 2 | 3.25 | 2020 | 30.43 | Comms failure / issue | Resolved - Dec | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02086
YWS02087 | Yorkshire Water | Live | HARTLEY BROOK AVENUE CSO | HARTLEY BROOK AVENUE/CSO | WRA9193 | WRA9193 | A1 | SO on sewer network | SK3627092830 | 436270 | 392832 | GB104027057440 | Blackburn Brook from Source to River Don | River | 3312 | Middle Don | 3029 | Don and Rother | HARTLEY BROOK DIKE | Not Applicable | Not Applicable | Not Applicable | 0:15 | 1 | 1 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02087
YWS02088 | Yorkshire Water | Live | FIFE STREET CSO | FIFE STREET/CSO | WRA9194 | WRA9194 | A1 | SO on sewer network | SK3886492035 | 438864 | 392035 | GB104027057440 | Blackburn Brook from Source to River Don | River | 3312 | Middle Don | 3029 | Don and Rother | BLACKBURN BROOK | Not Applicable | Not Applicable | Not Applicable | 31:30 | 17 | 19.4 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02088
YWS02089 | Yorkshire Water | Live | PARKSIDE ROAD CSO | PARKSIDE ROAD/CSO | WRA9195 | WRA9195 | A1 | SO on sewer network | SK3326490517 | 433264 | 390517 | GB104027057411 | Don from Little Don to River Loxley confluence | River | 3490 | Upper Don | 3029 | Don and Rother | RIVER DON | Not Applicable | Not Applicable | Not Applicable | 0:15 | 1 | 2.2 | 2020 | 94.16 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02089
YWS02090 | Yorkshire Water | Live | SMITHY WOOD CRESCENT CSO | SMITHY WOOD CRESCENT/CSO | WRA9196 | WRA9196 | A1 | SO on sewer network | SK3450883739 | 434508 | 383739 | GB104027057750 | Sheaf from Source to River Don | River | 3312 | Middle Don | 3029 | Don and Rother | RIVER SHEAF | Not Applicable | Not Applicable | Not Applicable | 0:15 | 1 | 1.5 | 2020 | 98.93 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02090
YWS02091 | Yorkshire Water | Live | WOODSEATS ROAD 2 CSO | WOODSEATS ROAD 2/CSO | WRA9197 | WRA9197 | A1 | SO on sewer network | SK3437083902 | 434370 | 383902 | GB104027057750 | Sheaf from Source to River Don | River | 3312 | Middle Don | 3029 | Don and Rother | RIVER SHEAF | Not Applicable | Not Applicable | Not Applicable | 16:30 | 15 | 15.2 | 2020 | 97.01 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02091
YWS02092 | Yorkshire Water | Live | LITTLE LONDON ROAD CSO | LITTLE LONDON ROAD/CSO | WRA9198 | WRA9198 | 1 | SO on sewer network | SK3446084010 | 434460 | 384014 | GB104027057750 | Sheaf from Source to River Don | River | 3312 | Middle Don | 3029 | Don and Rother | RIVER SHEAF | Not Applicable | Not Applicable | Not Applicable | 38:30 | 30 | 24.2 | 2020 | 78.03 | Comms failure / issue | Resolved - Jul | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02092
YWS02093 | Yorkshire Water | Live | NEWMILLERDAM CSO | NEWMILLERDAM/CSO | WRA9199 | WRA9199 | A1 | SO on sewer network | SE3312515777 | 433125 | 415777 | GB104027062530 | Owler Beck from Source to River Calder | River | 3268 | Lower Calder | 3001 | Aire and Calder | OWLER BECK/NEWMILLERDAM | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 1.2 | 2020 | 99.97 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02093
YWS02095 | Yorkshire Water | Live | THORNES ROAD JUNCTION CSO | THORNES ROAD JUNCT/CSO | WRA9201 | WRA9201 | 1 | SO on sewer network | SE3202019510 | 432020 | 419510 | GB104027062631 | Calder from River Colne to River Chald | River | 3268 | Lower Calder | 3001 | Aire and Calder | GILL SYKE | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02095
YWS02096 | Yorkshire Water | Live | WATERTON ROAD CSO | WATERTON ROAD/CSO | WRA9202 | WRA9202 | A1 | SO on sewer network | SE3155019857 | 431550 | 419857 | GB104027062620 | Chald from Source to River Calder | River | 3268 | Lower Calder | 3001 | Aire and Calder | GILL SYKE | Not Applicable | Not Applicable | Not Applicable | 60:30 | 31 | 14.6 | 2020 | 99.87 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02096
YWS02097 | Yorkshire Water | Live | FLANSHAW LANE CSO | FLANSHAW LANE/CSO | WRA9203 | WRA9203 | 1 | SO on sewer network | SE3100021350 | 431007 | 421359 | GB104027062620 | Chald from Source to River Calder | River | 3268 | Lower Calder | 3001 | Aire and Calder | ALVERTHORPE BECK | Not Applicable | Not Applicable | Not Applicable | 4:15 | 8 | 7.2 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02097
YWS02098 | Yorkshire Water | Live | NEW SCARBOROUGH CSO | NEW SCARBOROUGH/CSO | WRA9204 | WRA9204 | 1 | SO on sewer network | SE3192020870 | 431922 | 420871 | GB104027062620 | Chald from Source to River Calder | River | 3268 | Lower Calder | 3001 | Aire and Calder | ALVERTHORPE BECK | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0 | 2020 | 96.28 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02098
YWS02099 | Yorkshire Water | Live | WHINNEY MOOR PUB HOUSE CSO | WHINNEY MOOR PUB HSE/CSO | WRA9205 | WRA9205 | Α1 | SO on sewer network | SE3170719679 | 431707 | 419679 | GB104027062620 | Chald from Source to River Calder | River | 3268 | Lower Calder | 3001 | Aire and Calder | TRIBUTARY OF THE RIVER CALDER | Not Applicable | Not Applicable | Not Applicable | 5:30 | 3 | 1 | 2020 | 96.48 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02099
YWS02100 | Yorkshire Water | Live | OLD MILL LANE CSO | OLD MILL LANE/CSO | WRA9206 | WRA9206 | Α1 | SO on sewer network | SE3505407236 | 435054 | 407236 | GB104027063171 | Dearne from Cawthorne Dyke to Lundwood STW | River | 3125 | Dearne | 3029 | Don and Rother | RIVER DEARNE | Not Applicable | Not Applicable | Not Applicable | 17:00 | 13 | 13.4 | 2020 | 89.11 | Sensor failure / issue | Resolved - May | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02100
YWS02101 | Yorkshire Water | Live | WRENTHORPE LANE CSO | WRENTHORPE LANE/CSO | WRA9207 | WRA9207 | 1 | SO on sewer network | SE3138022510 | 431385 | 422515 | GB104027062620 | Chald from Source to River Calder | River | 3268 | Lower Calder | 3001 | Aire and Calder | BALNE BECK | Not Applicable | Not Applicable | Not Applicable | 6:45 | 18 | 3.8 | 2020 | 99.71 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02101
YWS02102 | Yorkshire Water | Live | QUEENS ROAD BEIGHTON CSO | QUEENS ROAD BEIGHTON/CSO | WRA9208 | WRA9208 | 1 | SO on sewer network | SK4431083830 | 444315 | 383835 | GB104027057772 | Rother, Doe Lea to Don | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | OCHRE BECK | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 2.2 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02102
YWS02103 | Yorkshire Water | Live | RAINBOW AVENUE SPS | RAINBOW AVENUE/CSO | WRA9209 | WRA9209 | A1 | Storm discharge at pumping station | SK4270783820 | 442707 | 383820 | GB104027057773 | Shire Brook | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | TRIBUTARY OF SHIRE BROOK | Not Applicable | Not Applicable | Not Applicable | 69:00 | 12 | 74.2 | 2020 | 99.99 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS02103
YWS02104 | Yorkshire Water | Live | RIDGEWAY WELL CSO | RIDGEWAY WELL/CSO | WRA9210 | WRA9210 | A1 | SO on sewer network | SK4042381657 | 440423 | 381657 | GB104027057720 | The Moss from Source to River Rother | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | TRIBUTARY OF THE MOSS | Not Applicable | Not Applicable | Not Applicable | 1:00 | 2 | 2.8 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02104
YWS02105 | Yorkshire Water | Live | BRIDGE INN FORD CSO | BRIDGE INN FORD/CSO | WRA9211 | WRA9211 | Α1 | SO on sewer network | SK4020680368 | 440206 | 380368 | GB104027057720 | The Moss from Source to River Rother | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | THE MOSS | Not Applicable | Not Applicable | Not Applicable | 81:30 | 37 | 71 | 2020 | 99.84 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS02105
YWS02106 | Yorkshire Water | Live | CROW LANE FIELD CSO | CROW LANE FIELD/CSO | WRA9212 | WRA9212 | 1 | SO on sewer network | SK3792077870 | 437927 | 377877 | GB104027057710 | Drone/Whitting from Source to River Rother | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | TRIBUTARY OF THE RIVER DRONE | Not Applicable | Not Applicable | Not Applicable | 0:15 | 1 | 3 | 2020 | 99.27 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02106
YWS02107 | Yorkshire Water | Live | CROW LANE MEMORIAL CSO | CROW LANE MEMORIAL/CSO | WRA9213 | WRA9213 | A1 | SO on sewer network | SK3743877262 | 437438 | 377262 | GB104027057710 | Drone/Whitting from Source to River Rother | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | RIVER DRONE | Not Applicable | Not Applicable | Not Applicable | 3:15 | 4 | 26.4 | 2020 | 96.8 |  |  | High spill threshold not met | High spill threshold not met | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS02107
YWS02108 | Yorkshire Water | Live | SISCAR COTTAGE CSO | SISCAR COTTAGE/CSO | WRA9214 | WRA9214 | A1 | SO on sewer network | SK3759077184 | 437590 | 377184 | GB104027057710 | Drone/Whitting from Source to River Rother | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | RIVER DRONE | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 1 | 2020 | 99.93 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02108
YWS02109 | Yorkshire Water | Live | HARDHURST ROAD CSO | HARDHURST ROAD/CSO | WRA9215 | WRA9215 | A1 | SO on sewer network | SK3756376424 | 437563 | 376424 | GB104027057710 | Drone/Whitting from Source to River Rother | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | RIVER DRONE | Not Applicable | Not Applicable | Not Applicable | 2:30 | 1 | 40.8 | 2020 | 99.88 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS02109
YWS02110 | Yorkshire Water | Live | HIPPER HALL CSO | HIPPER HALL/CSO | WRA9216 | WRA9216 | 1 | SO on sewer network | SK3415069490 | 434155 | 369495 | GB104027057660 | Hipper from Source to River Rother | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | TRIBUTARY OF THE RIVER HIPPER | Not Applicable | Not Applicable | Not Applicable | 109:00 | 42 | 29.6 | 2020 | 99.92 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02110
YWS02111 | Yorkshire Water | Live | BULLS HEAD CSO | BULLS HEAD/CSO | WRA9218 | WRA9218 | 1 | SO on sewer network | SK3399069290 | 433997 | 369290 | GB104027057660 | Hipper from Source to River Rother | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | RIVER HIPPER | Not Applicable | Not Applicable | Not Applicable | 21:45 | 18 | 30.8 | 2020 | 97.94 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02111
YWS02112 | Yorkshire Water | Live | DYKE VALE ROAD 1 CSO | DYKE VALE ROAD 1/CSO | WRA9219 | WRA9219 | A1 | SO on sewer network | SK4082384413 | 440823 | 384413 | GB104027057773 | Shire Brook | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | SHIRE BROOK | Not Applicable | Not Applicable | Not Applicable | 59:00 | 37 | 36 | 2020 | 90.98 |  |  | High spill threshold not met | High spill threshold not met | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS02112
YWS02113 | Yorkshire Water | Live | NORMANTON SPRING CSO | NORMANTON SPRING/CSO | WRA9220 | WRA9220 | Α1 | SO on sewer network | SK4045084374 | 440450 | 384390 | GB104027057773 | Shire Brook | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | SHIRE BROOK | Not Applicable | Not Applicable | Not Applicable | 46:30 | 39 | 43.4 | 2020 | 86.94 | Comms failure / issue | Resolved - May | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS02113
YWS02114 | Yorkshire Water | Live | ALPORT ROAD CSO | ALPORT ROAD/CSO | WRA9221 | WRA9221 | Α1 | SO on sewer network | SK4034284331 | 440342 | 384331 | GB104027057773 | Shire Brook | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | TRIBUTARY OF SHIRE BROOK | Not Applicable | Not Applicable | Not Applicable | 123:30 | 71 | 125.2 | 2020 | 99.78 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement ongoing | SOAF investigation ongoing | YWS02114
YWS02115 | Yorkshire Water | Live | COWLING CSO | COWLING/CSO | WRA9222 | WRA9222 | A1 | SO on sewer network | SD9681743002 | 396817 | 443002 | GB104027062930 | Glusburn beck from source to Lothersdale Beck | River | 3484 | Upper Aire | 3001 | Aire and Calder | ICKORNSHAW BECK | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 2.5 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02115
YWS02116 | Yorkshire Water | Live | EASTBURN OLD STW CSO | EASTBURN WKS/CSO | WRA9223 | WRA9223 | 1 | SO on sewer network | SE0191044960 | 401825 | 444965 | GB104027062960 | Eastburn Beck from Lothersdale Beck to River Aire | River | 3484 | Upper Aire | 3001 | Aire and Calder | MILL STREAM | Not Applicable | Not Applicable | Not Applicable | 288:30 | 75 | 47.2 | 2020 | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS02116
YWS02117 | Yorkshire Water | Live | HESLEY LANE CSO | HESLEY LANE/CSO | WRA9225 | WRA9225 | A1 | SO on sewer network | SK3744896086 | 437448 | 396086 | GB104027057420 | Greasbrough Dike from Source to River Don | River | 3312 | Middle Don | 3029 | Don and Rother | THORPE DYKE | Not Applicable | Not Applicable | Not Applicable | 20:00 | 9 | 6 | 2020 | 99.91 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02117
YWS02118 | Yorkshire Water | Live | WARREN LANE SHEFFIELD CSO | WARREN LN SHEFFIELD/CSO | WRA9226 | WRA9226 | 1 | SO on sewer network | SK3605097410 | 436055 | 397416 | GB104027057440 | Blackburn Brook from Source to River Don | River | 3312 | Middle Don | 3029 | Don and Rother | TRIBUTARY OF BLACKBURN BROOK | Not Applicable | Not Applicable | Not Applicable | 58:45 | 30 | 17.6 | 2020 | 99.96 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02118
YWS02119 | Yorkshire Water | Live | BACK WHARF STREET CSO | BACK WHARF STREET/CSO | WRA9230 | WRA9230 | A1 | SO on sewer network | SE0622523620 | 406225 | 423620 | GB104027062642 | Calder from Ryburn Confluence to River Colne | River | 3310 | Middle Calder | 3001 | Aire and Calder | RIVER CALDER | Not Applicable | Not Applicable | Not Applicable | 7:42 | 28 | 33.6 | 2020 | 61.45 | Sensor failure / issue | Resolved - Aug | High spill threshold not met | High spill threshold not met | UWWTR investigation ongoing, Operational investigation ongoing | Operational improvement ongoing | SOAF investigation ongoing | YWS02119
YWS02120 | Yorkshire Water | Live | TOWN HALL STREET CSO | TOWN HALL STREET/CSO | WRA9231 | WRA9231 | A1 | SO on sewer network | SE0590023530 | 405902 | 423534 | GB104027062641 | Calder from Colden Water to Ryburn Confluence | River | 3310 | Middle Calder | 3001 | Aire and Calder | RIVER CALDER | Not Applicable | Not Applicable | Not Applicable | 2:58 | 17 | 18.6 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02120
YWS02121 | Yorkshire Water | Live | PEAR TREE HOLLINS CSO | PEAR TREE HOLLINS/CSO | WRA9232 | WRA9232 | A1 | SO on sewer network | SE0547323854 | 405473 | 423854 | GB104027062641 | Calder from Colden Water to Ryburn Confluence | River | 3310 | Middle Calder | 3001 | Aire and Calder | RIVER CALDER | Not Applicable | Not Applicable | Not Applicable | 18:44 | 37 | 8 | 2020 | 91.49 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02121
YWS02122 | Yorkshire Water | Live | WEST STREET COMBINED SEWER OVERFLOW | WEST STREET/CSO | WRA9233 | WRA9233 | A1 | SO on sewer network | SE0582823292 | 405828 | 423292 | GB104027062580 | Ryburn from Booth Dean Clough to R Calder | River | 3310 | Middle Calder | 3001 | Aire and Calder | RIVER RYBURN | Not Applicable | Not Applicable | Not Applicable | 548:02 | 137 | 113.2 | 2020 | 100 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | Operational investigation completed | No improvement action in reporting period | SOAF investigation completed - No work required | YWS02122
YWS02123 | Yorkshire Water | Live | STANSFIELD MILL CSO | STANSFIELD MILL/CSO | WRA9234 | WRA9234 | A1 | SO on sewer network | SE0434222159 | 404342 | 422159 | GB104027062580 | Ryburn from Booth Dean Clough to R Calder | River | 3310 | Middle Calder | 3001 | Aire and Calder | NETHER ENDS BECK | Not Applicable | Not Applicable | Not Applicable | 43:45 | 16 | 15 | 2020 | 30.1 | Comms failure / issue | Scheduled | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02123
YWS02124 | Yorkshire Water | Live | BRIDGE ROAD CSO | BRIDGE ROAD/CSO | WRA9235 | WRA9235 | 1 | SO on sewer network | SE2784017820 | 427848 | 417824 | GB104027062510 | Smithy Brook from Source to River Calder | River | 3268 | Lower Calder | 3001 | Aire and Calder | SMITHY BROOK | Not Applicable | Not Applicable | Not Applicable | 735:45 | 110 | 91.2 | 2020 | 92.7 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement ongoing | SOAF investigation ongoing | YWS02124
YWS02125 | Yorkshire Water | Live | SPRINGFIELD LANE CSO | MANOR ROAD/CSO | WRA9236 | WRA9236 | A1 | SO on sewer network | SE1719012793 | 417190 | 412793 | GB104027063301 | Holme from New Mill Dike to R Colne | River | 3097 | Colne and Holme | 3001 | Aire and Calder | TRIBUTARY OF RANGE DIKE | Not Applicable | Not Applicable | Not Applicable | 24:00 | 2 | 6.2 | 2020 | 99.95 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02125
YWS02126 | Yorkshire Water | Live | DOGLEY CSO | DOGLEY/CSO | WRA9237 | WRA9237 | A1 | SO on sewer network | SE1869113780 | 418691 | 413780 | GB104027063340 | Fenay beck from Source to River Colne | River | 3097 | Colne and Holme | 3001 | Aire and Calder | WOODSOME BECK | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 15.2 | 2020 | 94.07 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02126
YWS02127 | Yorkshire Water | Live | WEST STREET WORSBROUGH CSO | WEST ST WORSBROUGH/CSO | WRA9239 | WRA9239 | A1 | SO on sewer network | SE3611303521 | 436113 | 403521 | GB104027057510 | Dove from Source to River Dearne | River | 3125 | Dearne | 3029 | Don and Rother | RIVER DOVE | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 4.6 | 2020 | 99.96 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02127
YWS02128 | Yorkshire Water | Live | BANK END AVENUE CSO | BANK END AVENUE/CSO | WRA9240 | WRA9240 | A1 | SO on sewer network | SE3619004600 | 436190 | 404600 | GB104027057510 | Dove from Source to River Dearne | River | 3125 | Dearne | 3029 | Don and Rother | DOB SIKE | Not Applicable | Not Applicable | Not Applicable | 2:45 | 7 | 6.8 | 2020 | 99.86 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02128
YWS02129 | Yorkshire Water | Live | CLOG BRIDGE CSO | CLOG BRIDGE/CSO | WRA9241 | WRA9241 | A1 | SO on sewer network | SE0422046200 | 404220 | 446200 | GB104027062990 | Silsden Beck from Source to River Aire | River | 3484 | Upper Aire | 3001 | Aire and Calder | SILSDEN BECK | Not Applicable | Not Applicable | Not Applicable | 33:45 | 25 | 17.8 | 2020 | 98.48 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02129
YWS02130 | Yorkshire Water | Live | NEWGATE CSO | NEWGATE/CSO | WRA9242 | WRA9242 | 1 | SO on sewer network | SE2012019550 | 420124 | 419557 | GB104027062631 | Calder from River Colne to River Chald | River | 3268 | Lower Calder | 3001 | Aire and Calder | RIVER CALDER | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 2.2 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02130
YWS02131 | Yorkshire Water | Live | KIPPAX 80 CSO | KIPPAX 80/CSO | WRA9243 | WRA9243 | A1 | SO on sewer network | SE4112229937 | 441122 | 429937 | GB104027062810 | Lin Dike from Source to River Aire | River | 3265 | Lower Aire | 3001 | Aire and Calder | HOLLINS BECK | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 18.4 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS02131
YWS02132 | Yorkshire Water | Live | FOREST HILL ROAD CSO | FOREST HILL ROAD/CSO | WRA9244 | WRA9244 | 1 | SO on sewer network | SE0793018210 | 407937 | 418213 | GB104027062570 | Black Brook from Source to River Calder | River | 3310 | Middle Calder | 3001 | Aire and Calder | TRIBUTARY OF HOLYWELL BROOK | Not Applicable | Not Applicable | Not Applicable | 10:00 | 13 | 18 | 2020 | 96.08 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02132
YWS02133 | Yorkshire Water | Live | GREEN LANE 125 CSO | GREEN LANE 125/CSO | WRA9245 | WRA9245 | A1 | SO on sewer network | SE1446138146 | 414461 | 438146 | GB104027063034 | Aire (R Worth to Gill Beck) | River | 3307 | Middle Aire | 3001 | Aire and Calder | RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 226:30 | 69 | 71.6 | 2020 | 99.87 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement ongoing | SOAF investigation ongoing | YWS02133
YWS02134 | Yorkshire Water | Live | RIDGEWAY CSO | RIDGEWAY/CSO | WRA9246 | WRA9246 | A1 | SO on sewer network | SE1651036420 | 416510 | 436420 | GB104027062862 | Bradford Beck (Clayton Bk to R Aire) | River | 3307 | Middle Aire | 3001 | Aire and Calder | TRAP SIKE | Not Applicable | Not Applicable | Not Applicable | 2:30 | 9 | 20.8 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02134
YWS02135 | Yorkshire Water | Revoked | BRIGHTON CSO | BRIGHTON STREET/CSO | WRA9247 | WRA9247 | 1 | SO on sewer network | SE1496038030 | 414960 | 438030 | GB104027063034 | Aire (R Worth to Gill Beck) | River | 3307 | Middle Aire | 3001 | Aire and Calder | RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | [5 empty] | No longer operational as an overflow - permit revoked or to be revoked | Overflow no longer spilling to environment - from Jan | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02135
YWS02136 | Yorkshire Water | Live | LIME GROVE CSO | LIME GROVE/CSO | WRA9249 | WRA9249 | A1 | SO on sewer network | SK4638198985 | 446381 | 398985 | GB70410274 | Sheffield and South Yorkshire Navigations (Mexborough Cut) | Canal | 2018 | Don and Rother Canals | 2001 | Humber AWB | CLVRT TRIB OF KILNHURST CUT | Not Applicable | Not Applicable | Not Applicable | 264:15 | 59 | 48.4 | 2020 | 100 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS02136
YWS02137 | Yorkshire Water | Live | DRONFIELD LEA ROAD CSO | DRONFIELD LEA ROAD/CSO | WRA9250 | WRA9250 | 1 | SO on sewer network | SK3542078380 | 435425 | 378386 | GB104027057710 | Drone/Whitting from Source to River Rother | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | RIVER DRONE | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 2 | 2020 | 99.93 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02137
YWS02138 | Yorkshire Water | Live | DRONFIELD YARD CSO | DRONFIELD YARD/CSO | WRA9251 | WRA9251 | A1 | SO on sewer network | SK3512278686 | 435122 | 378686 | GB104027057710 | Drone/Whitting from Source to River Rother | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | RIVER DRONE | Not Applicable | Not Applicable | Not Applicable | 16:15 | 23 | 20.2 | 2020 | 99.89 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02138
YWS02139 | Yorkshire Water | Live | DRONFIELD MILL LANE CSO | DRONFIELD MILL LANE/CSO | WRA9252 | WRA9252 | 1 | SO on sewer network | SK3587078120 | 435871 | 378127 | GB104027057710 | Drone/Whitting from Source to River Rother | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | RIVER DRONE | Not Applicable | Not Applicable | Not Applicable | 39:15 | 30 | 32 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02139
YWS02140 | Yorkshire Water | Live | DRONFIELD TIP CSO | DRONFIELD TIP/CSO | WRA9253 | WRA9253 | A1 | SO on sewer network | SK3629978045 | 436299 | 378045 | GB104027057710 | Drone/Whitting from Source to River Rother | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | RIVER DRONE | Not Applicable | Not Applicable | Not Applicable | 37:00 | 28 | 20.4 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02140
YWS02141 | Yorkshire Water | Live | RIVERSIDE CLOSE DARFIELD CSO | RIVERSIDE CL DARFIELD/CSO | WRA9255 | WRA9255 | A1 | SO on sewer network | SE4207804550 | 442078 | 404550 | GB104027063172 | Dearne from Lundwood to River Dove | River | 3125 | Dearne | 3029 | Don and Rother | RIVER DEARNE | Not Applicable | Not Applicable | Not Applicable | 40:45 | 21 | 20.6 | 2020 | 89.15 | Comms failure / issue | Resolved - Feb | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | SOAF investigation completed - operational solution completed | YWS02141
YWS02142 | Yorkshire Water | Live | DARFIELD DONCASTER ROAD CSO | DARFIELD DONCASTER RD/CSO | WRA9256 | WRA9256 | A1 | SO on sewer network | SE4230804575 | 442308 | 404575 | GB104027063172 | Dearne from Lundwood to River Dove | River | 3125 | Dearne | 3029 | Don and Rother | RIVER DEARNE | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0 | 2020 | 99.55 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02142
YWS02143 | Yorkshire Water | Live | GREYS BRIDGE CSO | GREYS BRIDGE/CSO | WRA9258 | WRA9258 | 1 | SO on sewer network | SK4914099890 | 449162 | 399902 | GB104027057452 | Don from River Rother to River Dearne | River | 3312 | Middle Don | 3029 | Don and Rother | RIVER DON | Not Applicable | Not Applicable | Not Applicable | 3:00 | 3 | 1.4 | 2020 | 96.64 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02143
YWS02145 | Yorkshire Water | Live | MEXBOROUGH EAST CSO | MEXBOROUGH EAST/CSO | WRA9260 | WRA9260 | 1 | SO on sewer network | SE4571002170 | 445715 | 402175 | GB104027063173 | Dearne Darfield STW to River Don | River | 3125 | Dearne | 3029 | Don and Rother | RIVER DEARNE | Not Applicable | Not Applicable | Not Applicable | 0:30 | 1 | 1.8 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02145
YWS02147 | Yorkshire Water | Live | LANE HACKINGS GREEN CSO | LANE HACKINGS GREEN/CSO | WRA9263 | WRA9263 | 1 | SO on sewer network | SE2261009540 | 422616 | 409547 | GB104027063220 | Dearne from Source to Bentley Brook | River | 3125 | Dearne | 3029 | Don and Rother | THORPE DIKE | Not Applicable | Not Applicable | Not Applicable | 20:30 | 17 | 10.6 | 2020 | 96 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02147
YWS02148 | Yorkshire Water | Live | BACK LANE CSO | BACK LANE/CSO | WRA9265 | WRA9265 | A1 | SO on sewer network | SE2616611492 | 426166 | 411492 | GB104027063220 | Dearne from Source to Bentley Brook | River | 3125 | Dearne | 3029 | Don and Rother | CLVRT TRIB OF TOAD HOLE DIKE | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 4.6 | 2020 | 99.91 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02148
YWS02149 | Yorkshire Water | Live | BROW BRIDGE CSO | BROW BRIDGE/CSO | WRA9266 | WRA9266 | A1 | SO on sewer network | SE0964421280 | 409644 | 421280 | GB104027062570 | Black Brook from Source to River Calder | River | 3310 | Middle Calder | 3001 | Aire and Calder | BLACK BROOK | Not Applicable | Not Applicable | Not Applicable | 18:00 | 21 | 20 | 2020 | 99.75 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02149
YWS02150 | Yorkshire Water | Live | STAINLAND ROAD CSO | STAINLAND ROAD/CSO | WRA9267 | WRA9267 | 1 | SO on sewer network | SE0909020670 | 409095 | 420670 | GB104027062570 | Black Brook from Source to River Calder | River | 3310 | Middle Calder | 3001 | Aire and Calder | HOLYWELL BROOK | Not Applicable | Not Applicable | Not Applicable | 2:15 | 8 | 6.8 | 2020 | 92.72 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02150
YWS02151 | Yorkshire Water | Live | BREARLEY MAIN SEWER CSO | BREARLEY MAIN SEWER/CSO | WRA9268 | WRA9268 | A1 | SO on sewer network | SE0282425897 | 402824 | 425897 | GB104027062641 | Calder from Colden Water to Ryburn Confluence | River | 3310 | Middle Calder | 3001 | Aire and Calder | RIVER CALDER | Not Applicable | Not Applicable | Not Applicable | 689:45 | 92 | 106.8 | 2020 | 97.93 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation ongoing | Operational improvement ongoing | SOAF investigation ongoing | YWS02151
YWS02152 | Yorkshire Water | Live | HANGINGROYD ROAD CSO | HANGINGROYD ROAD/CSO | WRA9269 | WRA9269 | 1 | SO on sewer network | SD9887027180 | 398865 | 427184 | GB104027062641 | Calder from Colden Water to Ryburn Confluence | River | 3310 | Middle Calder | 3001 | Aire and Calder | RIVER CALDER | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 2.4 | 2020 | 98.61 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02152
YWS02153 | Yorkshire Water | Live | HOLMFIRTH BRIDGE LANE CSO | HOLMFIRTH BRIDGE LN/CSO | WRA9270 | WRA9270 | A1 | SO on sewer network | SE1440108475 | 414401 | 408475 | GB104027057600 | Holme from Source to New Mill Dike | River | 3097 | Colne and Holme | 3001 | Aire and Calder | RIVER HOLME | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0.4 | 2020 | 96.82 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02153
YWS02154 | Yorkshire Water | Live | HEPWORTH ROAD CSO | HEPWORTH ROAD/CSO | WRA9272 | WRA9272 | A1 | SO on sewer network | SE1651407104 | 416514 | 407104 | GB104027057610 | New Mill Dike from Source to River Holme | River | 3097 | Colne and Holme | 3001 | Aire and Calder | RAKES DYKE | Not Applicable | Not Applicable | Not Applicable | 6:45 | 9 | 11 | 2020 | 99.95 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02154
YWS02155 | Yorkshire Water | Live | BUTT LANE CSO | BUTT LANE/CSO | WRA9273 | WRA9273 | A1 | SO on sewer network | SE1652407072 | 416524 | 407072 | GB104027057610 | New Mill Dike from Source to River Holme | River | 3097 | Colne and Holme | 3001 | Aire and Calder | RAKES DYKE | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0.2 | 2020 | 99.58 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02155
YWS02156 | Yorkshire Water | Live | KIRKBRIDGE LANE CSO | KIRKBRIDGE LANE/CSO | WRA9274 | WRA9274 | 1 | SO on sewer network | SE1598009220 | 415986 | 409226 | GB104027057610 | New Mill Dike from Source to River Holme | River | 3097 | Colne and Holme | 3001 | Aire and Calder | NEW MILL DIKE | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 2 | 2020 | 48.91 | Comms failure / issue | Resolved - Nov | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02156
YWS02157 | Yorkshire Water | Live | HOLME BOTTOM CSO | HOLME BOTTOM/CSO | WRA9275 | WRA9275 | 1 | SO on sewer network | SE1618009080 | 416189 | 409084 | GB104027057610 | New Mill Dike from Source to River Holme | River | 3097 | Colne and Holme | 3001 | Aire and Calder | NEW MILL DIKE | Not Applicable | Not Applicable | Not Applicable | 53:45 | 29 | 84.2 | 2020 | 99.88 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS02157
YWS02158 | Yorkshire Water | Live | SPRING WOOD CSO | SPRING WOOD/CSO | WRA9276 | WRA9276 | A1 | SO on sewer network | SE1623108149 | 416231 | 408149 | GB104027057610 | New Mill Dike from Source to River Holme | River | 3097 | Colne and Holme | 3001 | Aire and Calder | JACKSON BRIDGE DIKE | Not Applicable | Not Applicable | Not Applicable | 102:45 | 43 | 45.75 | 2020 | 90.39 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | Operational investigation ongoing | Operational improvement ongoing | SOAF investigation completed - No work required | YWS02158
YWS02160 | Yorkshire Water | Live | HIGHBURY MOUNT CSO | HIGHBURY MOUNT/CSO | WRA9292 | WRA9292 | 1 | SO on sewer network | SE2844036830 | 428440 | 436838 | GB104027062900 | Meanwood Beck from Source to River Aire | River | 3265 | Lower Aire | 3001 | Aire and Calder | MEANWOOD BECK | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0 | 2020 | 99.88 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02160
YWS02161 | Yorkshire Water | Live | CANAL STREET CSO | CANAL STREET ARMLEY/CSO | WRA9293 | WRA9293 | A1 | SO on sewer network | SE2883533475 | 428835 | 433475 | GB104027063032 | Aire from Gill Beck (Baildon) to River Calder | River | 3265 | Lower Aire | 3001 | Aire and Calder | RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02161
YWS02162 | Yorkshire Water | Live | ARMLEY ROAD CSO | ARMLEY ROAD/CSO | WRA9294 | WRA9294 | 1 | SO on sewer network | SE2883033471 | 428835 | 433475 | GB104027063032 | Aire from Gill Beck (Baildon) to River Calder | River | 3265 | Lower Aire | 3001 | Aire and Calder | RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 0:30 | 2 | 1.6 | 2020 | 99.31 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02162
YWS02163 | Yorkshire Water | Live | DRIVER TERRACE CSO | DRIVER TERRACE/CSO | WRA9295 | WRA9295 | A1 | SO on sewer network | SE2883533475 | 428835 | 433475 | GB104027063032 | Aire from Gill Beck (Baildon) to River Calder | River | 3265 | Lower Aire | 3001 | Aire and Calder | RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 326:30 | 90 | 89.75 | 2020 | 83.93 | Sensor failure / issue | Resolved - Mar | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation completed | No improvement action in reporting period | SOAF investigation completed - No work required | YWS02163
YWS02164 | Yorkshire Water | Live | WOLSELEY ROAD CSO | WOLSELEY ROAD/CSO | WRA9296 | WRA9296 | 1 | SO on sewer network | SE2775034121 | 427758 | 434126 | GB104027063032 | Aire from Gill Beck (Baildon) to River Calder | River | 3265 | Lower Aire | 3001 | Aire and Calder | RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 1:30 | 2 | 4.2 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02164
YWS02165 | Yorkshire Water | Live | CARDIGAN LANE CSO | CARDIGAN LANE/CSO | WRA9297 | WRA9297 | 1 | SO on sewer network | SE2775034122 | 427758 | 434126 | GB104027063032 | Aire from Gill Beck (Baildon) to River Calder | River | 3265 | Lower Aire | 3001 | Aire and Calder | RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 0:15 | 1 | 3.8 | 2020 | 97.65 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02165
YWS02166 | Yorkshire Water | Live | GREAT HORTON ROAD CSO | GREAT HORTON ROAD/CSO | WRA9298 | WRA9298 | A1 | SO on sewer network | SE1448332337 | 414483 | 432337 | GB104027062862 | Bradford Beck (Clayton Bk to R Aire) | River | 3307 | Middle Aire | 3001 | Aire and Calder | HORTON BECK WEST BROOK CLVRTD | Not Applicable | Not Applicable | Not Applicable | 50:45 | 41 | 101 | 2020 | 99.78 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS02166
YWS02167 | Yorkshire Water | Live | FARNHAM ROAD CSO | FARNHAM ROAD/CSO | WRA9299 | WRA9299 | A1 | SO on sewer network | SE1448332338 | 414483 | 432338 | GB104027062862 | Bradford Beck (Clayton Bk to R Aire) | River | 3307 | Middle Aire | 3001 | Aire and Calder | HORTON BECK (WEST BROOK) | Not Applicable | Not Applicable | Not Applicable | 14:45 | 22 | 19.2 | 2020 | 99.74 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02167
YWS02168 | Yorkshire Water | Live | LONGROYD MANCH ROAD CSO | SPRINGDALE AVENUE/CSO | WRA9301 | WRA9301 | A1 | SO on sewer network | SE1356716072 | 413567 | 416072 | GB104027063330 | Colne from Wessenden Brook to R Holme | River | 3097 | Colne and Holme | 3001 | Aire and Calder | RIVER COLNE | Not Applicable | Not Applicable | Not Applicable | 3:15 | 10 | 51 | 2020 | 99.78 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS02168
YWS02169 | Yorkshire Water | Live | LONGROYD MANCH ROAD CSO | LONGROYD MANCH ROAD/CSO | WRA9302 | WRA9302 | A1 | SO on sewer network | SE1356616073 | 413566 | 416073 | GB104027063330 | Colne from Wessenden Brook to R Holme | River | 3097 | Colne and Holme | 3001 | Aire and Calder | RIVER COLNE | Not Applicable | Not Applicable | Not Applicable | 4:00 | 11 | 4.4 | 2020 | 91.47 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | SOAF investigation completed - No work required | YWS02169
YWS02170 | Yorkshire Water | Live | WILLOW LANE BECK CSO | WILLOW LANE BECK/CSO | WRA9304 | WRA9304 | A1 | SO on sewer network | SE1520017527 | 415200 | 417527 | GB104027062550 | Colne from River Holme to River Calder | River | 3097 | Colne and Holme | 3001 | Aire and Calder | RIVER COLNE(VIA BIRKBY RELIEF) | Not Applicable | Not Applicable | Not Applicable | 42:45 | 38 | 69.8 | 2020 | 99.93 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement ongoing | SOAF investigation ongoing | YWS02170
YWS02171 | Yorkshire Water | Live | STAIRFOOT GRANGE CSO | STAIRFOOT GRANGE/CSO | WRA9305 | WRA9305 | A1 | SO on sewer network | SE3726206236 | 437262 | 406236 | GB104027063171 | Dearne from Cawthorne Dyke to Lundwood STW | River | 3125 | Dearne | 3029 | Don and Rother | CLVRT TRIB RIVER DEARNE | Not Applicable | Not Applicable | Not Applicable | 162:45 | 58 | 52.2 | 2020 | 100 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS02171
YWS02173 | Yorkshire Water | Revoked | FARTOWN GREEN ROAD CSO | FARTOWN GREEN ROAD/CSO | WRA9311 | WRA9311 | 1 | SO on sewer network | SE1497818642 | 414970 | 418640 | GB104027062550 | Colne from River Holme to River Calder | River | 3097 | Colne and Holme | 3001 | Aire and Calder | BLACKHOUSE DIKE | Not Applicable | Not Applicable | Not Applicable | [5 empty] | No longer operational as an overflow - permit revoked or to be revoked | Overflow no longer spilling to environment - from Jan | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02173
YWS02174 | Yorkshire Water | Live | QUEENS SQUARE CSO | QUEENS SQUARE/CSO | WRA9312 | WRA9312 | A1 | SO on sewer network | SE1413012692 | 414130 | 412692 | GB104027063301 | Holme from New Mill Dike to R Colne | River | 3097 | Colne and Holme | 3001 | Aire and Calder | RIVER HOLME | Not Applicable | Not Applicable | Not Applicable | 323:45 | 67 | 66.2 | 2020 | 92.94 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | Operational investigation completed | No improvement action in reporting period | SOAF investigation completed - No work required | YWS02174
YWS02175 | Yorkshire Water | Live | EMBSAY CSO | EMBSAY/CSO | WRA9313 | WRA9313 | A1 | SO on sewer network | SE0057553332 | 400575 | 453332 | GB104027063060 | Haw Beck from Source to Eller beck | River | 3484 | Upper Aire | 3001 | Aire and Calder | EMBSAY BECK | Not Applicable | Not Applicable | Not Applicable | 250:30 | 66 | 49 | 2020 | 99.59 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS02175
YWS02176 | Yorkshire Water | Live | BARROWFIELD ROAD CSO | BARROWFIELD ROAD/CSO | WRA9314 | WRA9314 | A1 | SO on sewer network | SK3827098592 | 438245 | 398621 | GB104027057470 | Knoll Beck from Source to River Dearne | River | 3125 | Dearne | 3029 | Don and Rother | TRIB OF HARLEY DIKE | Not Applicable | Not Applicable | Not Applicable | 32:00 | 16 | 35 | 2020 | 91.1 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | SOAF investigation completed - No work required | YWS02176
YWS02177 | Yorkshire Water | Live | OLD GEORGE CSO | OLD GEORGE/CSO | WRA9315 | WRA9315 | A1 | SO on sewer network | SE3934332424 | 439343 | 432424 | GB104027062810 | Lin Dike from Source to River Aire | River | 3265 | Lower Aire | 3001 | Aire and Calder | THE BECK | Not Applicable | Not Applicable | Not Applicable | 6:45 | 7 | 2.6 | 2020 | 97.28 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02177
YWS02178 | Yorkshire Water | Live | LUMB CLOUGH CSO | LUMB CLOUGH/CSO | WRA9316 | WRA9316 | A1 | SO on sewer network | SE0445021285 | 404450 | 421285 | GB104027062580 | Ryburn from Booth Dean Clough to R Calder | River | 3310 | Middle Calder | 3001 | Aire and Calder | RIVER RYBURN | Not Applicable | Not Applicable | Not Applicable | 16:30 | 10 | 16.2 | 2020 | 89.78 | Comms failure / issue | Resolved - Jun | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | SOAF investigation completed - operational solution completed | YWS02178
YWS02179 | Yorkshire Water | Live | NEWLAY LANE CSO | NEWLAY LANE/CSO | WRA9317 | WRA9317 | 1 | SO on sewer network | SE2386036941 | 423866 | 436949 | GB104027063032 | Aire from Gill Beck (Baildon) to River Calder | River | 3265 | Lower Aire | 3001 | Aire and Calder | RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 0:15 | 1 | 0.6 | 2020 | 99.93 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02179
YWS02180 | Yorkshire Water | Live | NORTH CLIFF ROAD CSO | NORTH CLIFF ROAD/CSO | WRA9318 | WRA9318 | 1 | SO on sewer network | SK5130099340 | 451303 | 399345 | GB104027064242 | Don from River Dearne to Mill Dyke | River | 3312 | Middle Don | 3029 | Don and Rother | RIVER DON | Not Applicable | Not Applicable | Not Applicable | 26:00 | 2 | 0.6 | 2020 | 94.8 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02180
YWS02181 | Yorkshire Water | Live | SPRING GROVE CSO | SPRING GROVE/CSO | WRA9319 | WRA9319 | 1 | SO on sewer network | SE2534010700 | 425341 | 410701 | GB104027063220 | Dearne from Source to Bentley Brook | River | 3125 | Dearne | 3029 | Don and Rother | TRIB OF RIVER DEARNE | Not Applicable | Not Applicable | Not Applicable | 0:15 | 1 | 1.2 | 2020 | 98.27 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02181
YWS02182 | Yorkshire Water | Live | OAK ROAD CSO | OAK ROAD/CSO | WRA9320 | WRA9320 | A1 | SO on sewer network | SE1717820400 | 417178 | 420400 | GB70410176 | Huddersfield Broad Canal | Canal | 2007 | Calder Canals | 2001 | Humber AWB | TRIB OF HUDDERSFIELD BROAD CAN | Not Applicable | Not Applicable | Not Applicable | 206:15 | 57 | 94.8 | 2020 | 95.14 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement ongoing | SOAF investigation ongoing | YWS02182
YWS02183 | Yorkshire Water | Live | WAKEFIELD ROAD 90 CSO | WAKEFIELD ROAD 90/CSO | WRA9321 | WRA9321 | A1 | SO on sewer network | SE0747723586 | 407477 | 423586 | GB70410243 | Rochdale Canal, eastern section | Canal | 2007 | Calder Canals | 2001 | Humber AWB | CALDER+HEBBLE NAVIGATION CANAL | Not Applicable | Not Applicable | Not Applicable | 107:30 | 64 | 60.4 | 2020 | 99.74 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS02183
YWS02184 | Yorkshire Water | Live | AIRMYN (THE CROSSINGS) SPS | AIRMYN CROSSING/CSO | YWUCD1/1 | YWUCD1/1 | 1 | Storm discharge at pumping station | SE7243725144 | 472437 | 425144 | GB104027062760 | Aire from River Calder to River Ouse | River | 3265 | Lower Aire | 3001 | Aire and Calder | RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 48.8 | 2020 | 99.99 |  |  | High spill threshold not met | N/A - Ongoing investigation | UWWTR investigation ongoing, Operational investigation completed | Operational improvement completed | SOAF investigation ongoing | YWS02184
YWS02185 | Yorkshire Water | Live | WHARNCLIFFE SIDE SPS | WHARNCLIFFE WEST/CSO | YWUCD1/107 | YWUCD1/107 | 1 | SO on sewer network | SK2989494525 | 429891 | 394513 | GB104027057411 | Don from Little Don to River Loxley confluence | River | 3490 | Upper Don | 3029 | Don and Rother | RIVER DON | Not Applicable | Not Applicable | Not Applicable | 112:30 | 29 | 6 | 2020 | 99.97 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02185
YWS02186 | Yorkshire Water | Live | WHITWOOD (WHITWOOD LANE) SPS | WHITWOOD/CSO | YWUCD1/109 | YWUCD1/109 | 1 | Storm discharge at pumping station | SE4017924649 | 440179 | 424649 | GB104027062632 | Calder from River Chald to River Aire | River | 3268 | Lower Calder | 3001 | Aire and Calder | WILLOWBRIDGE BECK | Not Applicable | Not Applicable | Not Applicable | 4:15 | 2 | 1.6 | 2020 | 99.95 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02186
YWS02188 | Yorkshire Water | Live | CARCROFT (NEW STREET) SPS | CARCROFT NEW STREET/SPS | YWUCD1/18 | YWUCD1/18 | 1 | Storm discharge at pumping station | SE5460410025 | 454604 | 410025 | GB104027057591 | Ea Beck from the Skell to River Don | River | 3272 | Lower Don | 3029 | Don and Rother | WELLSYKE DRAIN | Not Applicable | Not Applicable | Not Applicable | 172:45 | 19 | 18.4 | 2020 | 87.69 | Sensor failure / issue | Resolved - Nov | High spill threshold not met | High spill threshold not met | Operational investigation completed | Operational improvement completed | No SOAF investigation required | YWS02188
YWS02189 | Yorkshire Water | Live | CARCROFT (SKELLOW - INGS LANE) SPS | DONCASTER INGS LN/CSO | YWUCD1/19 | YWUCD1/19 | 1 | Storm discharge at pumping station | SE5313509736 | 453171 | 409739 | GB104027057591 | Ea Beck from the Skell to River Don | River | 3272 | Lower Don | 3029 | Don and Rother | TRIBUTARY OF THE SKELL | Not Applicable | Not Applicable | Not Applicable | 5:15 | 1 | 3.5 | 2023 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02189
YWS02190 | Yorkshire Water | Live | CARCROFT (SKELLOW) [1] SPS | BENTLEY MOOR LANE/CSO | YWUCD1/20 | YWUCD1/20 | 1 | Storm discharge at pumping station | SE5540009400 | 455400 | 409400 | GB104027057591 | Ea Beck from the Skell to River Don | River | 3272 | Lower Don | 3029 | Don and Rother | WELL SIKE | Not Applicable | Not Applicable | Not Applicable | 38:00 | 19 | 86.2 | 2020 | 99.91 |  |  | High spill threshold not met | N/A - Ongoing investigation | UWWTR investigation ongoing, Operational investigation completed | Operational improvement ongoing | SOAF investigation ongoing | YWS02190
YWS02191 | Yorkshire Water | Live | EAST COTTINGWITH SPS | EAST COTTINGWITH/CSO | YWUCD1/32 | EPR/ZB3395WB | A1 | Storm discharge at pumping station | SE7024542575 | 470245 | 442575 | GB104027068311 | Derwent from Elvington Beck to River Ouse | River | 3271 | Lower Derwent Yorkshire | 3027 | Derwent Humber | DITCH TO BECK | Not Applicable | Not Applicable | Not Applicable | 21:30 | 7 | 4.5 | 2020 | 99.88 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02191
YWS02192 | Yorkshire Water | Live | SPRING GARDENS SEWAGE PUMPING STA. | SPRING GARDENS BEAL/CSO | YWUCD1/53 | YWUCD1/53 | 1 | Storm discharge at pumping station | SE5287224342 | 452872 | 424342 | GB104027062760 | Aire from River Calder to River Ouse | River | 3265 | Lower Aire | 3001 | Aire and Calder | TRIBUTARY OF RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 2:15 | 6 | 29.8 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02192
YWS02194 | Yorkshire Water | Live | RAWCLIFFE SPS | CLIFTON HOSPITAL/CSO | YWUCD1/78 | YWUCD1/78 | 1 | Storm discharge at pumping station | SE5821453350 | 458214 | 453350 | GB104027069593 | Ouse from River Nidd to Stillingfleet Beck | River | 3499 | Upper Ouse Yorkshire | 3088 | Swale, Ure, Nidd and Upper Ouse | TRIB OF RIVER OUSE | Not Applicable | Not Applicable | Not Applicable | 0:48 | 1 | 1.2 | 2020 | 99.98 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02194
YWS02195 | Yorkshire Water | Live | RAWCLIFFE BRIDGE SPS | RAWCLIFFE BRIDGE/CSO | YWUCD1/81 | YWUCD1/81 | 1 | Storm discharge at pumping station | SE6977821126 | 469778 | 421126 | GB104027064243 | Don from Mill Dyke to River Ouse | River | 3272 | Lower Don | 3029 | Don and Rother | LANGHAM DRAIN | Not Applicable | Not Applicable | Not Applicable | 373:45 | 66 | 33.6 | 2020 | 99.97 |  |  | Not asset maintenance - Hydraulic capacity | High spill threshold not met | UWWTR investigation ongoing, Operational investigation completed | Operational improvement completed | SOAF investigation ongoing | YWS02195
YWS02196 | Yorkshire Water | Live | BARLBY ROAD SPS | BARLBY ROAD/CSO | YWUCD1/89 | YWUCD1/89 | 1 | Storm discharge at pumping station | SE6281032940 | 462810 | 432940 | GB104027064270 | Ouse from R Wharfe to Upper Humber | River | 3280 | Lower Ouse Yorkshire | 3115 | Wharfe and Lower Ouse | RIVER OUSE | Not Applicable | Not Applicable | Not Applicable | 64:00 | 35 | 66.2 | 2020 | 100 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS02196
YWS02197 | Yorkshire Water | Live | CARLETON ROAD CSO | CARLETON RD SKIPTON/CSO | YWUCD2/103 | YWUCD2/103 | 1 | SO on sewer network | SD9844450748 | 398444 | 450748 | GB104027063020 | Eller Beck from Haw Beck to River Aire | River | 3484 | Upper Aire | 3001 | Aire and Calder | ELLER BECK | Not Applicable | Not Applicable | Not Applicable | 670:15 | 136 | 131 | 2020 | 95.86 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | Operational investigation completed | No improvement action in reporting period | SOAF investigation completed - No work required | YWS02197
YWS02198 | Yorkshire Water | Live | MAIN STREET CSO | DALTON MAIN STREET/CSO | YWUCD2/105 | YWUCD2/105 | 1 | SO on sewer network | SE9684044986 | 496840 | 444986 | GB104026066901 | Scorborough Beck | River | 3274 | Lower Hull | 3039 | Hull and East Riding | BECKS DRAIN | Not Applicable | Not Applicable | Not Applicable |  |  | 0.75 | 2020 | 0 | Sensor failure / issue | Scheduled | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02198
YWS02199 | Yorkshire Water | Live | COD & LOBSTER SSO | SLIPWAY/CSO | YWUCD2/108 | YWUCD2/108 | 1 | SO on sewer network | NZ7836518869 | 478365 | 518869 | GB650401500004 | Yorkshire North | Coastal Water | 3179 | Esk TraC | 3040 | Humber TraC | NORTH SEA | Not Applicable | Not Applicable | Not Applicable | 6:30 | 5 | 7.4 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02199
YWS02200 | Yorkshire Water | Live | MILL GREEN CSO | MILL GREEN/CSO | YWUCD2/110 | YWUCD2/110 | 1 | SO on sewer network | SK4290074700 | 442919 | 374719 | GB104027057771 | Rother, Spittal Brook to Doe Lea | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | RIVER ROTHER | Not Applicable | Not Applicable | Not Applicable | 307:45 | 50 | 10 | 2020 | 96.71 |  |  | High spill threshold not met | High spill threshold not met | UWWTR investigation ongoing, Operational investigation ongoing | Operational improvement ongoing | SOAF investigation ongoing | YWS02200
YWS02202 | Yorkshire Water | Live | PONTEFRACT ROAD CSO | PONTEFRACT RD BRAMPTN/CSO | YWUCD2/117 | YWUCD2/117 | 1 | SO on sewer network | SE4195102137 | 441951 | 402137 | GB104027057470 | Knoll Beck from Source to River Dearne | River | 3125 | Dearne | 3029 | Don and Rother | KNOLL BECK | Not Applicable | Not Applicable | Not Applicable | 21:00 | 15 | 15.4 | 2020 | 99.92 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02202
YWS02203 | Yorkshire Water | Live | BROTHERTON CSO | BROTHERTON CHURCH RD/CSO | YWUCD2/12 | YWUCD2/12 | 1 | SO on sewer network | SE4824425309 | 448244 | 425309 | GB104027062760 | Aire from River Calder to River Ouse | River | 3265 | Lower Aire | 3001 | Aire and Calder | RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 0:15 | 1 | 0.2 | 2020 | 99.91 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02203
YWS02204 | Yorkshire Water | Live | TOWN FARM 2 CSO | XXXFOLD FARM 2/CSO | YWUCD2/120 | YWUCD2/120 | 1 | SO on sewer network | SE2898513653 | 428985 | 413653 | GB104027063260 | Dearne from Bentley Brook to Cawthorne Dyke | River | 3125 | Dearne | 3029 | Don and Rother | BRETTON BROOK | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0.2 | 2020 | 99.97 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02204
YWS02205 | Yorkshire Water | Live | TOWN FARM 4 SSO | XXXFOLD FARM 4/CSO | YWUCD2/122 | YWUCD2/122 | 1 | SO on sewer network | SE2894013677 | 428940 | 413677 | GB104027063260 | Dearne from Bentley Brook to Cawthorne Dyke | River | 3125 | Dearne | 3029 | Don and Rother | TRIBUTARY OF BRETTON BROOK | Not Applicable | Not Applicable | Not Applicable | 3:15 | 2 | 5.4 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02205
YWS02206 | Yorkshire Water | Live | GOLF COURSE CSO | BROUGH GOLF COURSE/CSO | YWUCD2/13 | YWUCD2/13 | 1 | SO on sewer network | SE9398427402 | 493984 | 427402 | Not part of a WFD catchment | Not part of a WFD catchment | River | N/A | N/A | N/A | N/A | GOLF LINKS BECK | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 19 | 2020 | 96.44 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02206
YWS02207 | Yorkshire Water | Live | ALDBOROUGH SSO | DUNSFORTH RD ALDBORO/CSO | YWUCD2/2 | YWUCD2/2 | 1 | SO on sewer network | SE4158466000 | 441584 | 466000 | GB104027064162 | Ure from River Tutt to River Swale | River | 3309 | Middle and Lower Ure | 3088 | Swale, Ure, Nidd and Upper Ouse | LOW COMMONDRAIN | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0.8 | 2020 | 99.77 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02207
YWS02210 | Yorkshire Water | Live | RAILWAY STREET (B TO D) CSO | RAILWAY ST DEWSBURY/CSO | YWUCD2/28 | YWUCD2/28 | 1 | SO on sewer network | SE2475021324 | 424750 | 421324 | GB104027062631 | Calder from River Colne to River Chald | River | 3268 | Lower Calder | 3001 | Aire and Calder | RIVER CALDER | Not Applicable | Not Applicable | Not Applicable | 176:00 | 33 | 66.8 | 2020 | 100 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS02210
YWS02211 | Yorkshire Water | Live | HULL ROAD CSO | HULL ROAD ANLABY/CSO | YWUCD2/3 | YWUCD2/3 | 1 | SO on sewer network | TA0398228758 | 503982 | 428758 | GB104026066750 | Fleet Drain | River | 3274 | Lower Hull | 3039 | Hull and East Riding | SAND DIKE | Not Applicable | Not Applicable | Not Applicable | 16:15 | 14 | 21.2 | 2020 | 99.95 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02211
YWS02212 | Yorkshire Water | Live | THORNHILL PARK AVENUE CSO | LOCK STREET/CSO | YWUCD2/30 | YWUCD2/30 | 1 | SO on sewer network | SE2508719787 | 426433 | 419453 | GB104027062631 | Calder from River Colne to River Chald | River | 3268 | Lower Calder | 3001 | Aire and Calder | RIVER CALDER | Not Applicable | Not Applicable | Not Applicable | 3:30 | 2 | 1.33 | 2020 | 78.14 | Sensor failure / issue | Resolved - Jul | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02212
YWS02213 | Yorkshire Water | Live | PRIMARY SCHOOL CSO | RIDGEWAY MAIN ROAD/CSO | YWUCD2/34 | YWUCD2/34 | 1 | SO on sewer network | SK4035581803 | 440355 | 381803 | GB104027057720 | The Moss from Source to River Rother | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | TRIB OF THE MOSS | Not Applicable | Not Applicable | Not Applicable | 0:30 | 2 | 1.4 | 2020 | 96.38 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02213
YWS02214 | Yorkshire Water | Live | SWAN INN CSO | SWAN INN RIDGEWAY/CSO | YWUCD2/35 | YWUCD2/35 | 1 | SO on sewer network | SK4041581664 | 440415 | 381664 | GB104027057720 | The Moss from Source to River Rother | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | TRIB OF THE MOSS | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0.4 | 2020 | 97.8 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02214
YWS02215 | Yorkshire Water | Live | ELLERTON CSO | ELLERTON/CSO | YWUCD2/36 | EPR/VB3797WT | A1 | SO on sewer network | SE7030239805 | 470302 | 439805 | GB104027068311 | Derwent from Elvington Beck to River Ouse | River | 3271 | Lower Derwent Yorkshire | 3027 | Derwent Humber | DRAIN TO RIVER DERWENT | Not Applicable | Not Applicable | Not Applicable | 689:00 | 84 | 95 | 2020 | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | Operational improvement completed | SOAF investigation ongoing | YWS02215
YWS02216 | Yorkshire Water | Live | STOCKBRIDGE ROAD CSO | ELLOUGHTON/CSO | YWUCD2/37 | YWUCD2/37 | 1 | SO on sewer network | SE9383328132 | 493833 | 428132 | Not part of a WFD catchment | Not part of a WFD catchment | River | N/A | N/A | N/A | N/A | GOLF LINKS BECK | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 1.6 | 2020 | 99.72 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02216
YWS02217 | Yorkshire Water | Live | REGENT STREET | REGENT ST BARNSLEY/CSO | YWUCD2/4 | YWUCD2/4 | 1 | SO on sewer network | SE3483206906 | 434832 | 406906 | GB104027063171 | Dearne from Cawthorne Dyke to Lundwood STW | River | 3125 | Dearne | 3029 | Don and Rother | TRIB OF RIVER DEARNE | Not Applicable | Not Applicable | Not Applicable | 0:15 | 1 | 2 | 2020 | 98.49 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02217
YWS02220 | Yorkshire Water | Live | KIRBY MISPERTON LANE SSO | MISPERTON LANE/CSO | YWUCD2/47 | YWUCD2/47 | 1 | SO on sewer network | SE7582076190 | 475805 | 476160 | GB104027068320 | Rye from River Seven to River Derwent | River | 3387 | Rye | 3027 | Derwent Humber | HABTON INGS DRAIN | Not Applicable | Not Applicable | Not Applicable | 1:00 | 1 | 0.5 | 2020 | 72.46 | Comms failure / issue | Resolved - Apr | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02220
YWS02222 | Yorkshire Water | Live | FERRY ROAD CSO | FERRY ROAD/CSO | YWUCD2/53 | YWUCD2/53 | 1 | SO on sewer network | TA0345426002 | 503454 | 426002 | GB104026066750 | Fleet Drain | River | 3274 | Lower Hull | 3039 | Hull and East Riding | FLEET DRAIN | Not Applicable | Not Applicable | Not Applicable | 86:00 | 42 | 66.2 | 2020 | 98.27 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS02222
YWS02223 | Yorkshire Water | Live | WOODHEAD ROAD CSO | HOLMBRIDGE MILL/CSO | YWUCD2/55 | YWUCD2/55 | 1 | SO on sewer network | SE1206106706 | 412061 | 406706 | GB104027057600 | Holme from Source to New Mill Dike | River | 3097 | Colne and Holme | 3001 | Aire and Calder | DIGLEY BROOK | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0 | 2020 | 75.47 | Comms failure / issue | Scheduled | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02223
YWS02226 | Yorkshire Water | Live | LONGROYD BRIDGE CSO | LONGROYD BRIDGE/CSO | YWUCD2/60 | YWUCD2/60 | 1 | SO on sewer network | SE1354616069 | 413546 | 416073 | GB104027063330 | Colne from Wessenden Brook to R Holme | River | 3097 | Colne and Holme | 3001 | Aire and Calder | RIVER COLNE | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0 | 2020 | 99.92 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02226
YWS02227 | Yorkshire Water | Live | KIRK HAMMERTON SSO | CHAPEL STREET YORK/CSO | YWUCD2/61 | YWUCD2/61 | 1 | SO on sewer network | SE4680055300 | 446800 | 455300 | GB104027068292 | Nidd from Crimple Beck to River Ouse | River | 3308 | Middle and Lower Nidd | 3088 | Swale, Ure, Nidd and Upper Ouse | KIRK HAMMERTON BECK | Not Applicable | Not Applicable | Not Applicable | 40:30 | 13 | 4.2 | 2020 | 93.52 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02227
YWS02230 | Yorkshire Water | Live | FEARNVILLE PLACE CSO | FEARNVILLE PL/NO 1 CSO | YWUCD2/66 | YWUCD2/66 | 1 | SO on sewer network | SE3427235614 | 434272 | 435614 | GB104027062880 | Wyke Beck from Source to River Aire | River | 3265 | Lower Aire | 3001 | Aire and Calder | WYKE BECK | Not Applicable | Not Applicable | Not Applicable | 1:00 | 3 | 14.4 | 2020 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02230
YWS02231 | Yorkshire Water | Revoked | FEARNVILLE PLACE CSO | FEARNVILLE PL/NO 2 CSO | YWUCD2/66 | YWUCD2/66 | 2 | SO on sewer network | SE3427235614 | 434272 | 435614 | GB104027062880 | Wyke Beck from Source to River Aire | River | 3265 | Lower Aire | 3001 | Aire and Calder | WYKE BECK | Not Applicable | Not Applicable | Not Applicable | [5 empty] | No longer operational as an overflow - permit revoked or to be revoked | Overflow no longer spilling to environment - from Jan | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02231
YWS02232 | Yorkshire Water | Live | NORTHSIDE CSO | NORTHSIDE BUSN PARK/CSO | YWUCD2/68 | YWUCD2/68 | 1 | SO on sewer network | SE3062734782 | 430627 | 434782 | GB104027062900 | Meanwood Beck from Source to River Aire | River | 3265 | Lower Aire | 3001 | Aire and Calder | SHEEPSCAR BECK | Not Applicable | Not Applicable | Not Applicable | 12:00 | 3 | 23.2 | 2020 | 99.92 |  |  | High spill threshold not met | High spill threshold not met | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS02232
YWS02233 | Yorkshire Water | Live | LONGBOTTOM BRIDGE CSO | LONGBOTTOM BRIDGE/CSO | YWUCD2/69 | YWUCD2/69 | 1 | SO on sewer network | SE0404024010 | 404040 | 424127 | GB104027062641 | Calder from Colden Water to Ryburn Confluence | River | 3310 | Middle Calder | 3001 | Aire and Calder | RIVER CALDER | Not Applicable | Not Applicable | Not Applicable | 88:15 | 16 | 8 | 2023 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02233
YWS02234 | Yorkshire Water | Live | THE DRIVE/CALDENE AVENUE CSO | THE DRIVE/CSO | YWUCD2/71 | YWUCD2/71 | 1 | SO on sewer network | SE0112526086 | 401125 | 426086 | GB104027062641 | Calder from Colden Water to Ryburn Confluence | River | 3310 | Middle Calder | 3001 | Aire and Calder | RIVER CALDER | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 2 | 2020 | 98.66 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02234
YWS02236 | Yorkshire Water | Live | RICHMOND SSO | LOMBARDS WYND/2 CSO | YWUCD2/82 | YWUCD2/82 | 1 | SO on sewer network | NZ1759501008 | 417617 | 501028 | GB104027069122 | Swale from Clapgate Beck to Bedale Beck | River | 3317 | Middle Swale | 3088 | Swale, Ure, Nidd and Upper Ouse | RIVER SWALE | Not Applicable | Not Applicable | Not Applicable | 317:45 | 91 | 91.4 | 2020 | 97.97 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS02236
YWS02238 | Yorkshire Water | Live | DALTON LANE CSO | DALTON PARVA/CSO | YWUCD2/88 | YWUCD2/88 | 1 | SO on sewer network | SK4619793673 | 446201 | 393671 | GB104027057452 | Don from River Rother to River Dearne | River | 3312 | Middle Don | 3029 | Don and Rother | DALTON BROOK | Not Applicable | Not Applicable | Not Applicable | 16:15 | 5 | 1.2 | 2020 | 99.43 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02238
YWS02240 | Yorkshire Water | Live | BARNSLEY ROAD CSO | BARNSLEY ROAD 248/CSO | YWUCD2/97 | YWUCD2/97 | 1 | SO on sewer network | SK3612392668 | 436123 | 392668 | GB104027057440 | Blackburn Brook from Source to River Don | River | 3312 | Middle Don | 3029 | Don and Rother | SHEFFIELD LANE DIKE | Not Applicable | Not Applicable | Not Applicable | 2:00 | 5 | 7.8 | 2020 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02240
YWS02241 | Yorkshire Water | Live | SHERBURN SSO | ST HILDAS STREET/CSO | YWUCD2/98 | YWUCD2/98 | 1 | SO on sewer network | SE9588277556 | 495882 | 477556 | GB104027067800 | Sherburn Beck catchment (trib of Derwent) | River | 3489 | Upper Derwent Yorkshire | 3027 | Derwent Humber | EAST BECK | Not Applicable | Not Applicable | Not Applicable | 3:15 | 6 | 8.6 | 2020 | 99.82 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02241
YWS02242 | Yorkshire Water | Live | ROYAL HOTEL CSO | ROYAL HOTEL/CSO | EPRBB3996EY | EPR/BB3996EY | A1 | SO on sewer network | NZ8986011368 | 489860 | 511368 | GB510402703400 | ESK (E) | Transitional Water | 3179 | Esk TraC | 3040 | Humber TraC | RIVER ESK | Not Applicable | Whitby | Not Applicable | 6:00 | 4 | 3 | 2020 | 91.53 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02242
YWS02243 | Yorkshire Water | Permit Application Submitted | TBC When Permit Issued | SCARBOROUGH/STW/STORM TREATMENT | Permit applied for | 27/27/0053 | TBC | Storm tank at WwTW - with treatment | TA0470191640 | 504704 | 491645 | GB650401500004 | Yorkshire North | Coastal Water | 3179 | Esk TraC | 3040 | Humber TraC | NORTH SEA | Not Applicable | Scarborough South Bay | UV (Ultraviolet) | 513:16 | 65 | 57.33 | 2022 | 99.82 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS02243
YWS02244 | Yorkshire Water | Live | MILLHOUSES PARK CSO | MILLHOUSES PARK/CSO/RETENTION/NO 1 COMPARTMENT | WRA7562 | WRA7562 | A1 | SO on sewer network | SK3365683262 | 433656 | 383258 | GB104027057750 | Sheaf from Source to River Don | River | 3312 | Middle Don | 3029 | Don and Rother | RIVER SHEAF | Not Applicable | Not Applicable | Not Applicable | 213:15 | 43 | 69 | 2022 | 99.99 |  |  | High spill threshold not met | Not asset maintenance - Hydraulic capacity | No investigation activity in reporting period | No improvement action in reporting period | SOAF investigation completed - No work required | YWS02244
YWS02245 | Yorkshire Water | Live | MILLHOUSES PARK CSO | MILLHOUSES PARK/CSO/RETENTION/NO 2 COMPARTMENT | WRA7562 | WRA7562 | A2 | SO on sewer network | SK3365683262 | 433656 | 383258 | GB104027057750 | Sheaf from Source to River Don | River | 3312 | Middle Don | 3029 | Don and Rother | RIVER SHEAF | Not Applicable | Not Applicable | Not Applicable | 392:00 | 55 | 19 | 2022 | 99.87 |  |  | High spill threshold not met | High spill threshold not met | Operational investigation completed | No improvement action in reporting period | No SOAF investigation required | YWS02245
YWS02246 | Yorkshire Water | Live | CHAPEL LAND KILHAM CSO | CHAPEL LANE KILHAM/CSO | EPRUP3127XA | EPR/UP3127XA | A1 | SO on sewer network | TA0599264313 | 505995 | 464306 | GB104026067101 | Lowthorpe/Kelk/Foston Bks from Source to Frodingham Beck | River | 3492 | Upper Hull | 3039 | Hull and East Riding | TRIB OF LOWTHORPE BECK | Not Applicable | Not Applicable | Not Applicable | 2217:45 | 100 | 48.67 | 2022 | 100 |  |  | Performance - GW inundation | Performance - GW inundation | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS02246
YWS02247 | Yorkshire Water | Live | ACOMB CSO | ACOMB/CSO | EPRJB3498RC | EPR/JB3498RC | A1 | SO on sewer network | SE5784251171 | 457843 | 451170 | GB104027064001 | Holgate Beck to Ouse | River | 3499 | Upper Ouse Yorkshire | 3088 | Swale, Ure, Nidd and Upper Ouse | Not matched in EA Consents Database | Not Applicable | Not Applicable | Not Applicable | 4:45 | 10 | 21.5 | 2022 | 47.17 | Sensor failure / issue | Resolved - Dec | High spill threshold not met | High spill threshold not met | UWWTR investigation ongoing, Operational investigation ongoing | Operational improvement ongoing | SOAF investigation ongoing | YWS02247
YWS02248 | Yorkshire Water | Revoked | TBC When Permit Issued | APPERLEY ROAD/CSO | Permit applied for | TBC | A1 | SO on sewer network | SE1927738175 | 419277 | 438175 | GB104027063032 | Aire from Gill Beck (Baildon) to River Calder | River | 3265 | Lower Aire | 3001 | Aire and Calder | TBC When Permit Issued | Not Applicable | Not Applicable | Not Applicable | [5 empty] | No longer operational as an overflow - permit revoked or to be revoked | Overflow no longer spilling to environment - from Jan | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02248
YWS02249 | Yorkshire Water | Permit Application Submitted | TBC When Permit Issued | BAGLEY LANE 105/CSO | Permit applied for | TBC | TBC | SO on sewer network | SE2229936309 | 422299 | 436309 | GB104027063032 | Aire from Gill Beck (Baildon) to River Calder | River | 3265 | Lower Aire | 3001 | Aire and Calder | TBC When Permit Issued | Not Applicable | Not Applicable | Not Applicable | 0:45 | 2 | 1 | 2023 | 93.46 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02249
YWS02251 | Yorkshire Water | Permit Application Submitted | TBC When Permit Issued | BRACKENDALE/SPS | Permit applied for | TBC | TBC | SO on sewer network | SE1690738874 | 416907 | 438874 | GB70410231 | Leeds and Liverpool Canal, summit to Leeds | Canal | 2031 | Leeds and Liverpool Canal | 2001 | Humber AWB | TBC When Permit Issued | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0 | 2023 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02251
YWS02252 | Yorkshire Water | Permit Application Submitted | TBC When Permit Issued | EVERINGHAM HALL/SPS | Permit applied for | TBC | TBC | SO on sewer network | SE8038842190 | 480388 | 442190 | GB104026066690 | Foulness from Black Beck to Market Weighton Canal | River | 3191 | Foulness | 3039 | Hull and East Riding | TBC When Permit Issued | Not Applicable | Not Applicable | Not Applicable | 132:30 | 13 | 11.5 | 2023 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02252
YWS02253 | Yorkshire Water | Permit Application Submitted | TBC When Permit Issued | FISHERGATE 20/CSO | Permit applied for | TBC | TBC | SO on sewer network | SE6058251097, SE6058351087 | 460582 | 451097 | GB104027063520 | Foss from the Syke to the River Ouse | River | 3190 | Foss | 3088 | Swale, Ure, Nidd and Upper Ouse | TBC When Permit Issued | Not Applicable | Not Applicable | Not Applicable | 1248:15 | 66 | 54 | 2023 | 99.96 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS02253
YWS02254 | Yorkshire Water | Permit Application Submitted | TBC When Permit Issued | GARFORTH TANKS/CSO | Permit applied for | TBC | TBC | SO on sewer network | SE39803206 | 439800 | 432060 | GB104027062810 | Lin Dike from Source to River Aire | River | 3265 | Lower Aire | 3001 | Aire and Calder | TBC When Permit Issued | Not Applicable | Not Applicable | Not Applicable | 21:30 | 14 | 8 | 2023 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02254
YWS02255 | Yorkshire Water | Permit Application Submitted | TBC When Permit Issued | HOLYWELL MANCH ROAD/CSO | Permit applied for | TBC | TBC | SO on sewer network | SE0955914336 | 409559 | 414336 | GB104027063330 | Colne from Wessenden Brook to R Holme | River | 3097 | Colne and Holme | 3001 | Aire and Calder | TBC When Permit Issued | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0 | 2023 | 82.91 | Comms failure / issue | Resolved - Dec | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02255
YWS02256 | Yorkshire Water | Permit Application Submitted | TBC When Permit Issued | KILNERS BRIDGE DENABY/CSO | Permit applied for | TBC | TBC | SO on sewer network | SK5039599886 | 450395 | 399886 | GB104027064242 | Don from River Dearne to Mill Dyke | River | 3312 | Middle Don | 3029 | Don and Rother | TBC When Permit Issued | Not Applicable | Not Applicable | Not Applicable | 252:30 | 32 | 38.5 | 2023 | 99.93 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02256
YWS02257 | Yorkshire Water | Permit Application Submitted | TBC When Permit Issued | LEEMING WATER LANE/CSO | Permit applied for | TBC | TBC | SO on sewer network | SE2929289569 | 429292 | 489569 | GB104027068910 | Bedale/Newton/Burton Bk from Rand Bk to R Swale | River | 3317 | Middle Swale | 3088 | Swale, Ure, Nidd and Upper Ouse | TBC When Permit Issued | Not Applicable | Not Applicable | Not Applicable | 244:15 | 41 | 32.5 | 2023 | 97.79 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02257
YWS02259 | Yorkshire Water | Permit Application Submitted | TBC When Permit Issued | MIDDLE LANE SOUTH/CSO | Permit applied for | TBC | TBC | SO on sewer network | SK4310193705 | 443101 | 393705 | GB104027057452 | Don from River Rother to River Dearne | River | 3312 | Middle Don | 3029 | Don and Rother | TBC When Permit Issued | Not Applicable | Not Applicable | Not Applicable | 266:30 | 86 | 91 | 2023 | 99.31 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing, Operational investigation completed | No improvement action in reporting period | SOAF investigation ongoing | YWS02259
YWS02260 | Yorkshire Water | Permit Application Submitted | TBC When Permit Issued | PEASHOLME GREEN/CSO | Permit applied for | TBC | TBC | SO on sewer network | SE6084452079 | 460844 | 452079 | GB104027063520 | Foss from the Syke to the River Ouse | River | 3190 | Foss | 3088 | Swale, Ure, Nidd and Upper Ouse | TBC When Permit Issued | Not Applicable | Not Applicable | Not Applicable | 0:30 | 1 | 0.5 | 2023 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02260
YWS02262 | Yorkshire Water | Permit Application Submitted | TBC When Permit Issued | RAWMARSH HILL/CSO | Permit applied for | TBC | TBC | SO on sewer network | SK4351894984 | 443518 | 394984 | GB104027057452 | Don from River Rother to River Dearne | River | 3312 | Middle Don | 3029 | Don and Rother | TBC When Permit Issued | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0.5 | 2023 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02262
YWS02264 | Yorkshire Water | Permit Application Submitted | TBC When Permit Issued | MILTON ROAD/CSO | Permit applied for | TBC | TBC | SO on sewer network | SE2139723034 | 421397 | 423034 | GB104027062710 | Spen Beck from Source to River Calder | River | 3268 | Lower Calder | 3001 | Aire and Calder | TBC When Permit Issued | Not Applicable | Not Applicable | Not Applicable | 101:45 | 33 | 28 | 2023 | 99.93 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02264
YWS02267 | Yorkshire Water | Permit Application Submitted | TBC When Permit Issued | BATH ROAD/CSO | Permit applied for | TBC | TBC | SO on sewer network | SE2176923570 | #N/A | #N/A | GB104027062710 | Spen Beck from Source to River Calder | #N/A | #N/A | #N/A | #N/A | #N/A | TBC When Permit Issued | Not Applicable | Not Applicable | Not Applicable | 5:30 | 10 | 10 | 2024 | 95.74 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02267
YWS02269 | Yorkshire Water | Permit Application Submitted | TBC When Permit Issued | WESTBURY GROVE/CSO | Permit applied for | TBC | TBC | SO on sewer network | SE3216131221 | 432161 | 431221 | GB104027063032 | Aire from Gill Beck (Baildon) to River Calder | River | 3265 | Lower Aire | 3001 | Aire and Calder | TBC When Permit Issued | Not Applicable | Not Applicable | Not Applicable | 0:15 | 1 | 0.5 | 2023 | 99.87 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02269
YWS02270 | Yorkshire Water | Permit Application Submitted | TBC When Permit Issued | SELBY ROAD WISTOW/CSO | Permit applied for | TBC | TBC | SO on sewer network | SE5950135128 | 459501 | 435128 | GB104027063650 | Holmes Dike catchment (trib of Ouse) | River | 3280 | Lower Ouse Yorkshire | 3115 | Wharfe and Lower Ouse | TBC When Permit Issued | Not Applicable | Not Applicable | Not Applicable | 1437:15 | 97 | 79.5 | 2023 | 96.5 |  |  | Not asset maintenance - Hydraulic capacity | Not asset maintenance - Hydraulic capacity | UWWTR investigation ongoing | No improvement action in reporting period | SOAF investigation ongoing | YWS02270
YWS02271 | Yorkshire Water | Permit Application Submitted | TBC When Permit Issued | SENIOR ROAD/CSO | Permit applied for | TBC | TBC | SO on sewer network | SK3944587846 | 439445 | 387846 | GB104027057360 | Car Brook from Source to River Don | River | 3312 | Middle Don | 3029 | Don and Rother | TBC When Permit Issued | Not Applicable | Not Applicable | Not Applicable | 0:30 | 2 | 2 | 2023 | 99.76 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02271
YWS02273 | Yorkshire Water | Permit Application Submitted | TBC When Permit Issued | DEMA WORKS/CSO | Permit applied for | TBC | TBC | SO on sewer network | SK3866773093 | 438667 | 373093 | GB104027057771 | Rother, Spittal Brook to Doe Lea | River | 3385 | Rother and Doe Lea | 3029 | Don and Rother | TBC When Permit Issued | Not Applicable | Not Applicable | Not Applicable | 58:30 | 21 | 13.5 | 2023 | 99.47 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02273
YWS02275 | Yorkshire Water | Permit Application Submitted | TBC When Permit Issued | SOUTH END BEDALE/CSO | Permit applied for | TBC | TBC | SO on sewer network | SE2700088059 | 427000 | 488059 | GB104027068910 | Bedale/Newton/Burton Bk from Rand Bk to R Swale | River | 3317 | Middle Swale | 3088 | Swale, Ure, Nidd and Upper Ouse | TBC When Permit Issued | Not Applicable | Not Applicable | Not Applicable | 34:45 | 22 | 26 | 2023 | 99.48 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02275
YWS02276 | Yorkshire Water | Live | SWINTON CHURCH STREET/CSO | SWINTON CHURCH STREET/CSO | EPR/JB3499WR | EPR/JB3499WR | A1 | SO on sewer network | SK4538299153 | 445382 | 399153 | GB104027057452 | Don from River Rother to River Dearne | River | 3312 | Middle Don | 3029 | Don and Rother | A tributary of the River Don | Not Applicable | Not Applicable | Not Applicable | 5:15 | 5 | 2.5 | 2023 | 94.17 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02276
YWS02278 | Yorkshire Water | Live | Not matched in EA Consents Database | UPPER MILLGATE/CSO | EPR/JB3590WL | EPR/JB3590WL | A1 | SO on sewer network | SK4273393067 | 442733 | 393067 | GB104027057452 | Don from River Rother to River Dearne | River | 3312 | Middle Don | 3029 | Don and Rother | Not matched in EA Consents Database | Not Applicable | Not Applicable | Not Applicable | 21:00 | 19 | 15.5 | 2023 | 99.64 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02278
YWS02279 | Yorkshire Water | Permit Application Submitted | TBC When Permit Issued | VALE MILL LANE/SPS | Permit applied for | EPR/JB3591EF | TBC | SO on sewer network | SE0383938219 | 403839 | 438219 | GB104027062891 | Worth from Bridgehouse Beck to R Aire | River | 3307 | Middle Aire | 3001 | Aire and Calder | TBC When Permit Issued | Not Applicable | Not Applicable | Not Applicable | 0:00 | 0 | 0.5 | 2023 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02279
YWS02281 | Yorkshire Water | Live | Not matched in EA Consents Database | WILMINGTON STREET/CSO | EPR/JB3594WF | EPR/JB3594WF | A1 | SO on sewer network | SE3054634994 | 430546 | 434994 | GB104027062900 | Meanwood Beck from Source to River Aire | River | 3265 | Lower Aire | 3001 | Aire and Calder | Not matched in EA Consents Database | Not Applicable | Not Applicable | Not Applicable | 0:45 | 1 | 0.5 | 2023 | 99.91 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02281
YWS02284 | Yorkshire Water | Permit Application Submitted | TBC When Permit Issued | KERESFORTH ROAD 24/CSO | Permit applied for | TBC | TBC | SO on sewer network | SE3202504832 | 432025 | 404832 | GB104027057520 | Dodworth Dyke from Source to River Dove | River | 3125 | Dearne | 3029 | Don and Rother | TBC When Permit Issued | Not Applicable | Not Applicable | Not Applicable | 2:30 | 2 | 1.5 | 2023 | 57.92 | Sensor failure / issue | Resolved - Dec | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02284
YWS02285 | Yorkshire Water | Permit Application Submitted | TBC When Permit Issued | THORNE WEST STREET/CSO | Permit applied for | TBC | TBC | SO on sewer network | SE6877712564 | 468777 | 412564 | GB104028064350 | North Soak Drain Catchment (trib of Torne/Three Rivers) | River | 3234 | Isle of Axholme | 3041 | Idle and Torne | TBC When Permit Issued | Not Applicable | Not Applicable | Not Applicable | 32:15 | 23 | 33.5 | 2023 | 99.5 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02285
YWS02287 | Yorkshire Water | Permit Application Submitted | TBC When Permit Issued | RAWDON AVENUE/CSO | Permit applied for | YWUCD2 129 | TBC | SO on sewer network | SE6166351669 | 461663 | 451669 | GB104027063500 | Tang Hall Bk/Old Foss Bk catch, trib of River Foss | River | 3190 | Foss | 3088 | Swale, Ure, Nidd and Upper Ouse | TBC When Permit Issued | Not Applicable | Not Applicable | Not Applicable | 145:45 | 25 | 28 | 2023 | 54.92 | Sensor failure / issue | Scheduled | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02287
YWS02289 | Yorkshire Water | Live | BELLEVUE SPS | BELLE VUE/CSO | T/83/45412/O | T/83/45412/O | A2 | SO on sewer network | SE5894002200 | 458945 | 402209 | GB104028058440 | Mother Drain from Source to Torne | River | 3234 | Isle of Axholme | 3041 | Idle and Torne | THE LADY BANK DRAIN | Not Applicable | Not Applicable | Not Applicable | 30:00 | 10 | 8.67 | 2022 | 99.99 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02289
YWS02290 | Yorkshire Water | Live | HAIGH STW | HAIGH/STW | 201 | 201 | A2 | Inlet SO at WwTW | SE2990012300 | 429926 | 412375 | GB104027063260 | Dearne from Bentley Brook to Cawthorne Dyke | River | 3125 | Dearne | 3029 | Don and Rother | TRIB OF RIVER DEARNE | Not Applicable | Not Applicable | Not Applicable | 69:45 | 20 | 28.67 | 2022 | 99.71 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02290
YWS02291 | Yorkshire Water | Permit Application Submitted | TBC When Permit Issued | NEWSHAM/STW | Permit applied for | E807(SS) | TBC | Inlet SO at WwTW | NZ1123209943 | 411232 | 509943 | GB104027069180 | Skeeby/Holme/Dalton Bk from Source to River Swale | River | 3317 | Middle Swale | 3088 | Swale, Ure, Nidd and Upper Ouse | TBC When Permit Issued | Not Applicable | Not Applicable | Not Applicable | 110:15 | 22 | 32.67 | 2022 | 79.25 | Sensor failure / issue | Resolved - Dec | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02291
YWS02293 | Yorkshire Water | Live | ALLERTON BYWATER CSO | ALLERTON BYWATER/SPS | WRA7536 | WRA7536 | A2 | Storm discharge at pumping station | SE4226227568 | 442213 | 427568 | GB104027063032 | Aire from Gill Beck (Baildon) to River Calder | River | 3265 | Lower Aire | 3001 | Aire and Calder | TRIB OF RIVER AIRE | Not Applicable | Not Applicable | Not Applicable | 66:30 | 12 | 9.5 | 2023 | 94.79 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02293
YWS02294 | Yorkshire Water | Permit Application Submitted | TBC When Permit Issued | LINKFIELD/NO 2 SPS | Permit applied for | 27/27/0096 | TBC | Storm discharge at pumping station | TA1183578563 | #N/A | #N/A | Not part of a WFD catchment | Not part of a WFD catchment | #N/A | #N/A | #N/A | #N/A | #N/A | TBC When Permit Issued | Not Applicable | Not Applicable | Not Applicable | 131:30 | 21 | 21 | 2024 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02294
YWS02295 | Yorkshire Water | Permit Application being prepared | TBC When Permit Issued | BARKER LANE S40/CSO | Unpermitted | TBC | TBC | SO on sewer network | SK3693570838 | #N/A | #N/A | GB104027057660 | Hipper from Source to River Rother | #N/A | #N/A | #N/A | #N/A | #N/A | TBC When Permit Issued | Not Applicable | Not Applicable | Not Applicable | 12:45 | 12 | 12 | 2024 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02295
YWS02296 | Yorkshire Water | Live | BROOKLANDS LNE/NORTH PARKWAY CSO | BROOKLANDS DRIVE/SCC | WRA8097 | WRA8097 | A1 | SO on sewer network | SE3429035480 | #N/A | #N/A | GB104027062880 | Wyke Beck from Source to River Aire | #N/A | #N/A | #N/A | #N/A | #N/A | WYKE BECK | Not Applicable | Not Applicable | Not Applicable | 112:45 | 17 | 17 | 2024 | 100 |  |  | High spill threshold not met | High spill threshold not met | No investigation activity in reporting period | No improvement action in reporting period | No SOAF investigation required | YWS02296