Yorkshire Water Drought Permit Application

- North West Area Supporting Information

September 2022

Content

1.	Introduction	4

1.1.	The Yorkshire Water Supply area	4

2.	Drought permit description	7

2.1.	Location of North West Area reservoirs impacted by the proposed drought permits	7

2.1.1.	Summary of the North West area reservoirs and reservoir groups	9

2.1.2.	Operation of North West Area reservoirs	14

2.2.	Water Resources management arrangements relating to the application	18

2.3.	The drought permit proposals	19

3.	Drought permit justification	26

3.1.	Why we need a drought permit	26

3.2.	Benefits of these drought permits	26

3.3.	Deficiency of supplies due to an exceptional shortage of rain	27

3.4.	Reservoir Stocks	28

3.5.	The effects of the current water shortage	33

3.6.	Population affected by the drought permit	34

3.7.	Summer 2022 demand	34

3.8.	Leakage control	37

3.9.	Demand on the affected water source	38

3.10.	Drought permit alternatives considered	39

3.11.	Consequences if the drought permit is not granted	40

4.	Actions taken to reduce demand and conserve supplies	41

4.1.	Demand management during normal operating conditions	41

4.2.	Metering	42

4.3.	Leakage reduction activity	43

4.4.	Trigger: Reservoirs crossed our normal control line	44

4.5.	Trigger: Reservoirs crossed Environment Agency early warning trigger line	44

4.6.	Trigger: Reservoir stocks predicted to be 10 weeks from crossing the drought control line	46

4.7.	Trigger: Reservoir stocks predicted to be 8 weeks from crossing the drought control line	47

4.8.	The use of sources in 2022	47

5.	Environmental impacts of drought permit	51

6.	Water Supply Strategy for the Continuation of Drought	52

6.1.	Operational changes we will make to avoid future drought-related problems	54

7.	Notices and advertisements relation to application	55

7.1.	Public inspection arrangements	55

7.2.	Environment Agency	56

7.3.	Natural England	56

7.4.	Local rivers trusts and wildlife trusts	56

7.5.	Navigation Authority	56

7.6.	Internal Drainage Board	56

7.7.	Retailers	56

8.	Appendices	57

8.1.	Appendix 1: Summary of water saving communications	57

8.2.	Appendix 2: Notice relating to the North West reservoir group drought permit application	63

# Introduction

This drought permit application contains drought options in Yorkshire Water’s Drought Plan 2022. An application is being made for these permits to reduce compensation flows because of a dry spring and summer in 2022.  These interventions are required to reduce the risk of a shortage of supply, or failure to supply compensation flows, should there be insufficient rainfall to allow reservoirs to recover. This helps conserve reservoir supplies until we receive sufficient rainfall for levels to return to normal.

This document provides supporting information to Yorkshire Water’s twelve drought permit applications in the North West Yorkshire area (North West Area). The applications are to reduce compensation flows from eleven reservoirs and to reduce a maintained flow on the River Worth. The reductions, if the applications are granted, will be in place up to the end of March 2023.

We have submitted an application (form WR80) to the Environment Agency for each of the eleven sites that we are requesting a drought permit. Individual permits (form WR82) have been prepared for each individual licence and draft copies have been provided in support of the applications. Copies of the application form and the draft permits are provided in a separate document, ‘North West Area permit application and licence information’.

The sites are included as drought options in the Yorkshire Water Drought Plan 2022 available to view on the Yorkshire Water website (https://www.yorkshirewater.com/about-us/resources/drought-plan/.  In accordance with regulatory requirements Yorkshire Water has a Drought Plan that sets out the actions it can implement in a drought. The Drought Plan is revised every five years and submitted to Defra.

The North West Area options include twelve options in total and we are submitting drought permit applications for all twelve. These are compensation reductions at Leeming, Leeshaw, Doe Park, Hewenden, Eldwick, Reva, Weecher, Silsden, Embsay, Carr Bottom and Grimwith Reservoirs, and a reduction in the maintained flow of the River Worth at Springhead Weir, supported by Ponden and Lower Laithe Reservoirs.

We have provided the supporting information in one document as the reservoirs are used conjunctively and we consider the combined impacts in the environmental assessment, as well as providing individual assessments for each site.

The potential environmental impacts of implementing the drought permit have been considered and an environmental assessment report is provided in support of the application (section 5).

# The Yorkshire Water Supply area

Yorkshire Water supplies water to over five million customers. Under normal weather conditions, approximately 45% of this water is from impounding reservoirs, 30% from rivers and 25% from boreholes (groundwater). This varies from year to year depending on weather conditions. In dry years rivers are used more, with about 40% of supply coming from reservoirs, 40% from rivers and 20% from groundwater. By increasing river abstraction, we make use of supplies that would otherwise be lost and retain reservoir and groundwater supplies for longer. In normal weather conditions reservoir and groundwater stocks are replenished through rainfall and we do not need to rely on rivers as much.

For planning purposes, the Yorkshire supply region is divided into two water resource zones, shown in Figure 1.1. Most of our region is within our Grid Surface Water Zone (Grid SWZ), with 1% of customers in our East Surface Water Zone (East SWZ). The Grid SWZ has an integrated supply network dominated by the operation of lowland rivers and Pennine reservoirs. The East SWZ, is a much smaller zone covering Whitby and the surrounding area. It is supplied by a river abstraction and moorland springs in the Whitby area. We are not applying for any drought permits in our East SWZ.

Figure 1.1: Water resource zones

Our Grid SWZ includes five interconnected operating areas, which we refer to as North, North West, South, South West and East areas. The drought permit applications relate to compensation reductions from reservoirs in the North West area.

Our Drought Plan 2022 includes 49 drought options that are designed to conserve reservoir supplies or provide additional river or groundwater supplies when droughts occur in our Grid SWZ. The majority (43) of our drought options are related to reservoir compensation releases and we have a high number of these as there are over 100 reservoirs in our region. We have six drought options in our Drought Plan relating to existing river abstractions that can be used to provide additional resources to our Grid SWZ without the need for any new infrastructure.

We operate our Grid SWZ to balance resources through our five operating areas rather than drawing down individual reservoir groups in each area. Our river sources can be used in preference to reservoir supplies when stocks are low in order to conserve resources for later in the year if we do not receive sufficient rainfall for stocks to recover. Our Drought Plan is designed to implement drought actions, when needed, across our Grid SWZ to provide benefits regionally rather than at a local level. During droughts our use of river sources can be limited by licence conditions which restrict abstractions at low flows. Drought permits, if granted, can temporarily alter these restrictions in order to provide additional water for supply to customers if our normal resources are low due to exceptional shortage of rainfall.

We are applying for drought permits that will enable us to implement several of the drought options in our Drought Plan (a list of these options is provided in Section 6 ). The permit applications have been selected through modelling and analysis of our drought plan options. We are prioritising our permit applications to those that will offer the maximum benefits to protecting public water supply in the current situation.

Figure 1.2: Grid SWZ integrated network

Figure 1.2 is an outline of our grid network, which connects most of the water resources in our Grid SWZ. The grid network enables highly effective conjunctive use of different water resources using raw and treated water pipelines. Water abstracted from the river intakes is used to support the five operating areas either directly or indirectly, so they are not solely dependent on local resources.

During dry weather we aim to maximise use of river sources to conserve reservoir stocks for longer. However, this year we have experienced exceptionally high demand and low rainfall. At times we have had to maximise use of rivers and reservoirs simultaneously and during periods of low river flow we have had to rely on reservoir supplies. We balance the drawdown of reservoirs across the zone through use of our grid system. This makes our region more resilient to supply risks but following exceptional weather conditions during 2022, stocks in the reservoirs across our region are lower than average. Our use of the licences in this application is described in Section 4.8.

As a result of the low rainfall our reservoirs are below average for the time of year and there is a risk to security of supply if we do not take action to conserve reservoir stocks as much as possible. We are applying for drought permits to conserve supplies in reservoirs in case the dry weather continues. These drought permits, if granted, will reduce the amount of water we release from reservoirs to rivers allowing us to maintain these compensation flows for longer, and aiding the recovery of these reservoirs.

# Drought permit description

The North West Area of our grid network supplies a considerable area of West Yorkshire including Bradford, Keighley and Skipton.  The area includes five reservoir groups and six additional reservoirs. Not all the reservoirs provide water for public water supply. The North West Area can also receive supply form river sources in our region as it is connected to our grid system.

We are applying for drought permits to temporarily reduce compensation flows from the following impounding reservoirs (IREs) and to reduce one maintained flow in the North West Area:

Leeming IRE

Leeshaw IRE

Doe Park IRE

Hewenden IRE

Eldwick IRE

Reva IRE

Weecher IRE

Silsden IRE

Embsay IRE

Grimwith IRE

Carr Bottom

Springhead Weir maintained flow (Ponden and Lower Laithe reservoirs)

Compensation releases are a requirement under Acts of Parliament or licence agreements we hold with the Environment Agency. The flow releases support the environment by compensating the watercourses downstream from the reservoirs. We are applying for drought permits to conserve supplies to ensure continuation of public water supply and to help our reservoir stocks recover.

# Location of North West Area reservoirs impacted by the proposed drought permits

Figure 2.1, Figure 2.2 and Figure 2.3 show the reservoirs in the North West Area of our Grid SWZ that will be impacted if the North West Area drought permits are granted. The permits will allow compensation releases and a maintained flow to be temporarily reduced for the duration the permits are in place. The reservoirs are in the north west of Yorkshire and are located from the upper reaches of the Wharfe Valley near Grassington, down to the Worth Valley between Keighley and Halifax to the south. They release compensation flows to tributaries of the River Wharfe, River Worth, and River Aire.

The reservoirs impacted by the proposed drought permits are listed in Table 1.

| Reservoir Name | Grid reference | Location description | Reservoir / Reservoir Group |
| --- | --- | --- | --- |
| Leeming Reservoir | SE 03 34 | South east of the village of Oxenhope | Leeming and Leeshaw compensation reservoirs |
| Leeshaw Reservoir | SE 01 35 | West of Oxenhope | Leeming and Leeshaw compensation reservoirs |
| Doe Park Reservoir | SE 07 34 | East of the town of Denholme | Thornton Moor and Stubden Group |
| Hewenden Reservoir | SE 07 35 | West of the village of Harecroft | Thornton Moor and Stubden Group |
| Eldwick Reservoir | SE 12 41 | North of the village of Eldwick; | Eldwick Reservoir |
| Reva Reservoir | SE 15 42 | North west of the village of Hawksworth | Rombalds Group |
| Weecher Reservoir | SE 13 42 | West of the village of Hawksworth | Rombalds Group |
| Silsden Reservoir | SE 04 47 | North of the town of Silsden | Silsden Reservoir |
| Embsay Reservoir | SD 99 54 | North west of the village of Embsay | Embsay Reservoir |
| Grimwith Reservoir | SE 06 64 | North east of the village of Hebden | Grimwith Reservoir |
| Carr Bottom Reservoir | SE 14 44 | Near Burley in Wharfedale | Rombalds Group |

Table 1 Reservoirs impacted by drought permit proposals

We are also applying for a reduction in the flow of the River Worth at Springhead Weir (grid reference SE 02 37). which is maintained by compensation releases from Ponden and Lower Laithe Reservoirs.

# Summary of the North West area reservoirs and reservoir groups

A brief description of each of the reservoirs and reservoir groups is provided below. The group names have been defined for Yorkshire Water to use operationally and have been determined by the connectivity between the reservoirs that make up the groups.

### Nidd/Barden Group

The Nidd/Barden Group supplies Chellow Heights Water Treatment Works (WTW) in Daisy Hill near Bradford. The group comprises Angram and Scar House supply reservoirs.

### Upper/Lower Barden and Chelker Group

The Barden and Chelker Group supplies Chellow Heights WTW in Daisy Hill near Bradford and Graincliffe WTW near Bingley. The group comprises Upper Barden, Lower Barden, and Chelker supply reservoirs.

Thornton Moor and Stubden Group

The Thornton Moor and Stubden Group supplies Chellow Heights WTW in Daisy Hill near Bradford. The group comprises of Thornton Moor and Stubden supply reservoirs, and Doe Park and Hewenden compensation reservoirs. Thornton Moor and Stubden do not release compensation flows but can support Doe Park and Hewenden compensation reservoirs downstream.

Worth Valley Group

The Worth Valley Group supplies Oldfield WTW and Sladen Valley WTW which are located between Haworth and Keighley. The group comprises of Watersheddles, Keighley Moor, Ponden, and Lower Laithe reservoirs. Ponden and Lower Laithe reservoirs are used to support a maintained flow at Springhead Weir.

Rombalds Group

The Rombalds Group supplies Graincliffe WTW near Bingley. The group comprises of Reva, Carr Bottom, Panorama, Graincliffe, and Weecher supply reservoirs. Compensation flows are released from Carr Bottom, Reva and Weecher reservoirs.

Embsay Reservoir

Embsay IRE provides water to Embsay WTW, and can be supported by Jenny Gill and Whinny Gill reservoirs.

Grimwith Reservoir

Grimwith Reservoir stands alone and provides a regulated release to support abstractions at low flows from the River Wharfe, it also provides compensation flow to the River Dibb, a tributary of the Wharfe. It has a small licence to supply Chellow Heights WTW directly.

Leeming and Leeshaw compensation reservoirs

Leeming and Leeshaw Reservoirs provide compensation flows to Leeming Water and Moorhouse Beck in the River Worth catchment.  The flows released are dependent on stocks in these reservoirs, and the value of the required maintained flow at Springhead Weir on the River Worth is dependent on the combined release from Leeming and Leeshaw reservoirs. Under normal conditions Leeming and Leeshaw release a total of 8Ml/d and the maintained flow at Springhead Weir on the River Worth must be greater than 6Ml/d.  When stocks in Leeming and Leeshaw are both below their operational control lines, the releases reduce to a combined 6Ml/d and the Springhead Weir maintained flow must increase to 8Ml/d.  There are rules that govern the releases of Leeming and Leeshaw if only one is below the control lines, and these are detailed in the licences.

Silsden Reservoir

Silsden is used for compensation only and is released to Silsden Beck, a tributary of the River Aire. We have a long-term drought option to use the reservoir in supply and if this is required, we will apply for authorisation under a separate drought permit application.  The compensation release at Silsden is a prescribed flow, which is only required if we are abstracting from Silsden reservoir, although we routinely make this release to Silsden Beck.  In July 2022 we reduced the flow to preserve stocks in the reservoir and increase the time we would be able to maintain a release.  We carried out extensive monitoring before, during and after the reduction in prescribed flow, as though this were being done under a drought permit in line with our Environmental Monitoring Plan, although no permit was required.

Eldwick Reservoir

Eldwick Reservoir is a compensation reservoir releasing water to Eldwick Beck in the River Aire catchment.

Figure 2.1   Map of Worth Valley Group and Thornton Moor and Stubden Group drought permit sites in the North West Area

Figure 2.2  Map of Eldwick, Weecher and Reva reservoir drought permit sites in in the North West Area

Figure 2.3 Map of Embsay, Silsden, Carr Bottom and Grimwith reservoir permit sites in the North West Area

# Operation of North West Area reservoirs

The reservoirs in the North West Area provide water to water treatment works at Chellow Heights, Graincliffe, Oldfield, Sladen Valley and Embsay, and supply Bradford, Keighley, Skipton, and surrounding areas. The reservoirs in this area are operated conjunctively with the River Wharfe abstraction at Lobwood, which also supplies Chellow Heights Water treatment works via Chelker Reservoir. This area can be supported from our Central Area (Eccup to Graincliffe transfer), from either the Washburn reservoirs or the River Ouse abstraction at Moor Monkton.  Figure 2.4 shows a high level schematic of the north west area.

Figure 2.5 and Figure 2.6 show the Water Resource Allocation Plan (WRAP) schematic for the North West Area. As well as the supply reservoir groups, it shows the transmission network, and the demand zones supplied by these reservoirs. The system is highly interconnected, with most zones being able to be supported from sources other than their primary source. We therefore consider the demands in the area as a whole and adjust water treatment works flows and source use to balance stocks as much as possible.

We run our WRAP model each week to optimise supplies and balance stocks. We also use our WRAPsim simulation model to plan for medium term scenarios (using our 1995/96 drought as worst historic but looking at all historic years to consider all scenarios). We have run the WRAPsim model weekly during the spring and summer, and used it to identify where to protect stocks, and when to reduce flows to do so. By doing this we have tried to balance stocks both within areas and across the region, although asset availability and differences in rainfall has meant this process and these decisions are constantly reviewed. Some of the actions taken as a result of these decisions are described in sections 4.4 to 4.7, where we describe the actions we have taken as triggers are crossed or are predicted to be crossed.

Figure 2.4 North West Area schematic

Figure 2.5 WRAP Schematic of the central North West Area

Figure 2.6 WRAP Schematic of the rural North West Area

# Water Resources management arrangements relating to the application

The drought permit applications propose reductions in compensation releases from eleven reservoirs. These are: Doe Park Reservoir; Hewenden reservoir; Eldwick Reservoir; Reva Reservoir; Weccher Reservoir; Silsden Reservoir; Embsay Reservoir; Grimwith Reservoir; Carr Bottom Reservoir; Leeming Reservoir; and Leeshaw Reservoir. A reduction in the maintained flow at Springhead Weir, downstream of Ponden and Lower Laithe Reservoirs is also proposed.

The licences and downstream watercourses relating to the drought permit applications in the North West Area are:

Doe Park Reservoir under conditions defined by the abstraction licence NE/027/0016/021, releasing flow to compensate the Denholme Beck and the River Aire.

Hewenden Reservoir under conditions defined by the Bradford Waterworks Act 1854, releasing flow to compensate the Hewenden Beck and the River Aire.

Eldwick Reservoir under conditions defined by the Shipley Waterworks and Police Act 1854, releasing flow to compensate the Eldwick Beck and the River Aire.

Reva Reservoir under conditions defined by the Yeadon Waterworks Act 1916, releasing flow to the Hawksworth Beck Goit and the River Aire.

Weecher Reservoir under conditions defined by the Baildon Local Water Act 1890, releasing flow to the Weecher Brow Beck and the River Aire.

Silsden Reservoir under condition defined by the abstraction licence 2/27/15/149, releasing flow into the Silsden Beck and the River Aire.

Embsay Reservoir under conditions defined by the Skipton Water Improvement Act 1904 and by Abstraction Licence 2/27/15/45, releasing flow into Embsay Beck and the River Aire.

Grimwith Reservoir under conditions defined by the abstraction licence NE/027/0019/011, releasing water into the River Wharfe.

Leeming Reservoir under conditions defined by the Leeming Reservoir impoundment licence (NE/027/0014/010), releasing flow to compensate Leeming Water and the River Worth.

Leeshaw Reservoir under the Leeshaw Reservoir impoundment licence (NE/027/0014/011), releasing flow to compensate Dunkirk Water and the River Worth.

Ponden Reservoir under conditions defined by the Ponden Reservoir abstraction licence (2/27/14/058), releasing flows to compensate the downstream watercourse, the River Worth

Lower Laithe Reservoir under conditions defined by the Lower Laithe Reservoir abstraction licence (2/27/14/009), releasing flows to compensate the downstream receiving watercourse, Sladen Beck.

The maintained flow at Springhead Weir under conditions defined by abstraction Licences 2/27/14/058 Ponden & 2/27/14/009 Lower Laithe.  The value of the maintained flow is dependent on the releases from Leeming and Leeshaw reservoirs, which vary with the reservoir levels relative to operational control lines defined in the impoundment licences.

Carr Bottom Reservoir under conditions defined by the Burley-in-Wharfedale Water Act 1899, releasing flows to compensate the downstream receiving watercourse, the Carr Beck.

# The drought permit proposals

The drought permit applications in the North West Area propose to temporarily reduce the compensation releases from eleven reservoirs and the maintained flow requirement at Springhead Weir, supported by Ponden and Lower Laithe Reservoirs.  Table 2 gives the statutory volumes and the reduced volumes for the duration of the drought permits.

Further details on the drought permit applications are provided below. The reductions proposed relate to the water level (or stocks) in either individual reservoirs or the combined stocks of all the supply reservoirs we operate, referred to as “regional reservoir stocks.” If granted the permits will be in place for 6 months from the date of approval. If we receive sufficient refill for our regional reservoirs stocks to recover to a level we refer to as ‘the normal control line’ and no individual reservoir group is below a level we refer to as our ‘early warning trigger line,’ we will increase the compensation flow to the volumes defined in the licence agreements. Plots of the reservoir stocks and further explanations about the triggers to be used for compensation flow reductions can be found in Section 3.

Leeming Reservoir (SE 03 34)

We release water from Leeming Reservoir under conditions defined by the Leeming Reservoir impoundment licence (NE/027/0014/010). The terms of the licence state we must release flow from Leeming Reservoir to compensate the downstream receiving watercourse, Leeming Water. The volume we release is dependent on the stock levels in Leeming Reservoir and in Leeshaw Reservoir, which is operated under the terms of the Leeshaw Reservoir impoundment licence. Under the Leeming Reservoir impoundment licence conditions, we must continuously discharge not less than 4.00 Ml/d when Leeming reservoir is either above or below its control line and Leeshaw is above its control line, or 5.250 Ml/d when the Leeming reservoir level is above the control line and Leeshaw reservoir level is below the control line, or 3.250 Ml/d when both the Leeshaw and Leeming reservoir levels are below the control lines.

The drought permit application for Leeming Reservoir is to reduce the compensation release required when Leeming reservoir level is above or below the control line and Leeshaw reservoir level is above the control line to 2.00 Ml/d, to reduce the compensation release when Leeming reservoir level is above the control line and Leeshaw reservoir level is below the control line to 2.63 Ml/d and to reduce further when the reservoirs are both below the control lines to 1.625 Ml/d. There would then be a further reduction to 1.33 Ml/d when Leeming reservoir level is above or below the control line and Leeshaw reservoir level is above the control line, and to 1.75 Ml/d when the Leeming reservoir level is above or below the control line and Leeshaw reservoir level is below the control line or 1.083 Ml/d when both the Leeshaw and Leeming reservoir levels are below the control lines, if regional reservoir stocks were below the regional Drought Control Line for four consecutive weeks or more, as defined in the Yorkshire Water Drought Plan.

Leeshaw Reservoir (SE 01 35)

We release water from Leeshaw Reservoir under conditions defined by the Leeshaw Reservoir impoundment licence (NE/027/0014/011). The terms of the licence state we must release flow from Leeshaw Reservoir to compensate the downstream receiving watercourse, Dunkirk Beck. Under the licence conditions, we must continuously discharge not less than 4.00 Ml/d when the reservoir level is above the control line defined in the licence, or 2.750 Ml/d when the reservoir level is below the control line.

The drought permit application for Leeshaw Reservoir is to reduce the compensation release required when Leeshaw Reservoir stocks are above the control line to 2.00 Ml/d, or when the reservoir stocks are below the control line to 1.375 Ml/d. There would then be a further reduction to 1.33Ml/d when the reservoir level is above the control line or 0.92 Ml/d if below the reservoir control line, if regional reservoir stocks were below the regional Drought Control Line for four consecutive weeks or more, as defined in the Yorkshire Water Drought Plan.

Springhead Weir Maintained Flow (SE 02 37)

We are licensed to abstract water from Ponden Reservoir for supply to customers under abstraction licence number 2/27/14/058. The terms of the licence state we must release flow from Ponden Reservoir to compensate the downstream receiving watercourse, the River Worth. We are licensed to abstract water from Lower Laithe Reservoir for supply to customers under the abstraction licence (2/27/14/009). The terms of the licence state we must release flow from Lower Laithe Reservoir to compensate the downstream receiving watercourse, Sladen Beck. Under both Ponden and Lower Laithe licence conditions Yorkshire Water must ensure the flow of water at Springhead Weir, which is below the confluence of the two watercourses, shall not fall below 6.00 Ml/d, when the combined compensation flow from Leeming and Leeshaw reservoirs is 8.00 Ml/d, or 8.00 Ml/d when the combined compensation flow from Leeming and Leeshaw reservoirs reduces to 6.00 Ml/d.

The drought permit application for the Springhead Weir Maintained Flow is to reduce the maintained flow at Springhead Weir when regional stocks are at or approaching the drought control line. The maintained flow would reduce to 3.00 Ml/d if either Leeshaw or Leeming reservoirs are above the control lines and to 4.00 Ml/d if Leeshaw and Leeming are both below the control lines. There would then be a further reduction further to 2.00 Ml/d if either Leeshaw and Leeming reservoirs are above their control lines and to 2.67 Ml/d if both Leeshaw or Leeming are below the control lines, if regional reservoir stocks are below the regional Drought Control Line for four consecutive weeks or more, as defined in the Yorkshire Water Drought Plan.

Doe Park Reservoir (SE 07 34)

Under the terms of abstraction licence NE/027/0016/021, we must release water from Doe Park Reservoir to compensate the downstream water course. The licence states that we must release flow from Doe Park Reservoir to the Denholme Beck so as to maintain a flow of no less than 3.6 Ml/d in Denholme Beck.

The drought permit application for Doe Park Reservoir is to provide a release of 1.8 Ml/d at all stock levels, which could be reduced to 1.2 Ml/d if regional reservoir stocks were below the regional Drought Control Line for four consecutive weeks or more, as defined in the Yorkshire Water Drought Plan.

Hewenden Reservoir (SE 07 35)

Under the terms of the Bradford Waterworks Act 1854, we must release water from Hewenden Reservoir to compensate the downstream water course, the Hewenden Beck. The terms of the Act state that we must release flow from Hewenden Reservoir at mill owners’ discretion. We currently operate the compensation flow under the terms of a flow trial agreement held with the Environment Agency, whereby we continuously discharge not less than 6.3 Ml/d.

The drought permit application for Hewenden Reservoir is to reduce the compensation release required to 3.15 Ml/d. The drought permit application for Hewenden Reservoir is to provide a continuous release of 3.15 Ml/d, which could be reduced to 2.10 Ml/d if regional reservoir stocks were below the regional Drought Control Line for four consecutive weeks or more, as defined in the Yorkshire Water Drought Plan.

Eldwick Reservoir (SE 12 41)

Under the terms of Shipley Waterworks and Police Act 1854, we must release water from Eldwick Reservoir to compensate the downstream water course, the Eldwick Beck. The terms of the Act state that we must release two fifths of the average daily inflow to the reservoir between 05:00 and 20:00 every day (barring Sunday, Christmas Day, and Good Friday). We currently operate the compensation flow under the terms of a flow trial agreement held with the Environment Agency, whereby we continuously discharge not less than 1.00 Ml/d.

The drought permit application for Eldwick Reservoir is to reduce the compensation release required to 0.50 Ml/d. The drought permit application for Eldwick Reservoir is to provide a continuous compensation release of 0.50 Ml/d, which could be reduced to 0.33 Ml/d if regional reservoir stocks were below the regional Drought Control Line for four consecutive weeks or more, as defined in the Yorkshire Water Drought Plan.

Reva Reservoir (SE 15 42)

We are licensed to abstract water from Reva Reservoir for supply to customers under the Yeadon Waterworks Act 1916. The terms of the Act state that we must release not less than 0.791 Ml/d (174,000 gallons per day) to compensate the downstream water course, the Hawksworth Beck.

The drought permit application for Reva reservoir is to reduce the compensation release required to 0.396 Ml/d. There would be a further reduction to 0.264 Ml/d if regional reservoir stocks were below the regional Drought Control Line for four consecutive weeks or more, as defined in the Yorkshire Water Drought Plan.

Weecher Reservoir (SE 13 42)

We are licensed to abstract water from Weecher Reservoir for supply to customers by permit under the Baildon Local Water Act 1890. The terms of the Act state that we must release not less than 110,273 gallons (0.501 Ml) per working day Monday to Saturday to compensate the downstream water course, the Weecher Brow Beck. We currently operate the compensation release under an agreement held with the Environment Agency to discharge 0.43 Ml/d.

The drought permit application for Weecher Reservoir is to reduce the compensation release required to 0.215 Ml/d. There would be a further reduction to 0.143 Ml/d if regional reservoir stocks were below the regional Drought Control Line for four consecutive weeks or more, as defined in the Yorkshire Water Drought Plan.

Silsden Reservoir (SE 04 47)

We are licensed to abstract water from Silsden Reservoir for supply to customers under abstraction licence number 2/27/15/149. The terms of the licence include a prescribed flow condition of 2.409 Ml/d to be discharged to Silsden Beck, whereby no water can be abstracted if the flow exiting the reservoir is below this level.  We do not currently abstract from Silsden Reservoir, however under normal operations we release the prescribed flow volume to compensate the downstream watercourse.

We have a drought action for Silsden Reservoir to reduce the compensation release to 1.20 Ml/d. There would be a further reduction to 0.80 Ml/d if regional reservoir stocks were below the regional Drought Control Line for four consecutive weeks or more, as defined in the Yorkshire Water Drought Plan.

This action does not require a drought permit unless we are abstracting from the reservoir. We would only use this reservoir for public water supply if we implemented a long-term drought action, which requires additional infrastructure to be installed. We are not currently implementing this drought action therefore do not require a drought permit to reduce the compensation releases. [The notice includes text for advertising a permit in case it is required.]

Embsay Reservoir (SD 99 54)

We are licensed to abstract water from Embsay Reservoir for supply to customers under the Skipton Water and Improvement Act 1904 and abstraction licence number 2/27/15/45 (the “Embsay licence”). The terms of the Act state that we must release not less than 1.186 Ml/d (261,000 gallons per day) to compensate the downstream water course, the Embsay Beck. The Embsay licence states a flow of not less than 0.273 Ml/d (60,000 gallons per day) must remain in Mill Beck, immediately downstream of the abstraction point, when abstraction takes place.

The drought permit application for Embsay Reservoir is to reduce the compensation release required to 0.593 Ml/d. There would be a further reduction to 0.395 Ml/d if regional reservoir stocks were below the regional Drought Control Line for four consecutive weeks or more, as defined in the Yorkshire Water Drought Plan. All releases would be greater than 0.273 Ml/d, therefore consistent with the Embsay licence condition.

Grimwith Reservoir (SE 06 64)

Under the terms of abstraction licence NE/027/0019/011 we must release flow from Grimwith Reservoir to compensate the downstream water course, the River Dibb, a tributary to the River Wharfe. The volume released changes throughout the year. From 1st January to 19th April we must release no less than 15.1 Ml/d; from 20th April to 10th May no less than 7.8 Ml/d; from 11th May to 11th October no less than 3.8 Ml/d; from 12th to 31st October no less than 7.8 Ml/d; from 1st November to 31st December no less than 15.1 Ml/d.

The drought action applicable to the Grimwith Reservoir compensation release is to reduce the compensation release requirement to: 7.55 Ml/d from 1st January to 19th April; 3.90 Ml/d from 20th April to the 10th May; 1.90 Ml/d from 11th May to 11th October; 3.90 Ml/d from 12th to 31st October; 7.55 Ml/d from 1st November to 31st December. There would be a further reduction to 5.03 Ml/d Ml/d from 1st January to 19th April; 2.60 Ml/d from 20th April to the 10th May; 1.27 Ml/d from 11th May to 11th October; 2.60 Ml/d from 12th to 31st October; 5.03 Ml/d from 1st November to 31st December if regional reservoir stocks were below the regional Drought Control Line for four consecutive weeks or more, as defined in the Yorkshire Water Drought Plan.

A drought permit is not currently required for the above drought action, however if the flow trial conditions are formalised a permit will be required. The action will be dependent on the time of year it is required, and the text will be amended to reflect this.

We are also required to release a regulating flow from Grimwith Reservoir to support abstractions from the River Wharfe at low flows. We can abstract from two abstraction points on the River Wharfe, which are at Lobwood (under the terms of licence 2/27/19/129/R01) and Arthington (under the terms of licence 2/27/20/196/R01). We have a drought option to temporarily suspend the regulatory flow and a further option to increase the annual volume we take from the River Wharfe at Lobwood. Both options require a drought permit and details will be provided in our River Wharfe supporting document when that permit application is submitted.

Carr Bottom Reservoir (SE 15 45)

We are licensed to impound water at Carr Bottom Reservoir for supply to customers under the Burley-in-Wharfedale Water Act 1899. The terms of the Act state that we must release not less than 0.085 Ml/d (18,600 gallons per day) into the downstream watercourse, the Carr Beck.

The drought permit application for Carr Bottom Reservoir is to reduce the compensation release required to 0.0425 Ml/d. There would be a further reduction to 0.028 Ml/d if regional reservoir stocks were below the regional Drought Control Line for four consecutive weeks or more, as defined in the Yorkshire Water Drought Plan.

| Compensation Water Source | Receiving Watercourse | Relevant Authorising Act or Licence | Current Legal Requirement (Ml/d) | Drought Permit Quantities applied for |  |
| --- | --- | --- | --- | --- | --- |
|  |  |  |  | Flow reduced by half (Ml/d) | Flow reduced by two thirds (Ml/d) |
| Leeming Reservoir | Leeming Water, River Worth | Leeming Reservoir Impoundment Licence NE/027/0014/010 | Compensation releases; 4.00 when Leeming is either above or below the control line (CL) and Leeshaw is above CL, 5.25 when Leeming above CL and Leeshaw below control line, 3.25 when Leeming and Leeshaw below CL | 2.00 when Leeming is above or below CL and Leeshaw is above CL, 2.63 when Leeming above CL and Leeshaw below CL, 1.63 when Leeming and Leeshaw below CL | 1.33 when Leeming is above or below CL and Leeshaw is above or below CL, 1.75 when Leeming above CL and Leeshaw below CL, 1.08 when Leeming and Leeshaw below CL |
| Leeshaw Reservoir | Dunkirk Beck, River Worth | Leeshaw Reservoir Impoundment Licence NE/027/0014/011 | 4.00 above Leeshaw CL, 2.75 below Leeshaw CL | 2.00 when Leeshaw above CL, 1.38 when Leeshaw below CL | 1.33 Leeshaw above or below CL, 0.92 when Leeshaw below CL |
| Springhead Weir Maintained Flow | River Worth | Ponden 2/27/14/058 and Lower Laithe 2/27/17/009 Abstraction Licences | 8.00 when Leeming and Leeshaw are below CL 6.00 when Leeming and Leeshaw are above CL | 3.00 when either Leeming or Leeshaw above CL, 4.00 when both reservoirs below CL | 2.00 when either Leeming or Leeshaw above CL, 2.67 when both reservoirs below CL |
| Doe Park Reservoir | Denholme Beck River Aire | Abstraction licence NE/027/0016/021 | 3.60 | 1.80 | 1.20 |
| Hewenden Reservoir | Hewenden Beck River Aire | Bradford Waterworks Act 1854 | 6.30 | 3.15 | 2.10 |
| Eldwick Reservoir | Eldwick Beck River Aire | Shipley Waterworks and Police Act 1854 | 1.00 Two fifths of the average daily inflow to the reservoir between 05:00 and 20:00 every day except Sunday, Christmas Day and Good Friday. | 0.50 | 0.33 |
| Reva Reservoir | Hawksworth Beck River Aire | Yeadon Waterworks Act 1916 | 0.791 | 0.396 | 0.264 |
| Weecher Reservoir | Weecher Brow Beck River Aire | Baildon local Water Act 1820 | 0.43 110,273 gallons per working day (Mon-Sat) | 0.215 | 0.143 |
| Silsden Reservoir | Silsden Beck River Aire | Abstraction Licence 2/27/15/149 | 2.409 Ml/d | 1.20 | 0.80 |
| Embsay Reservoir | Embsay Beck River Aire | Skipton Water and Improvement Act 1904 and Abstraction Licence 2/27/15/45 | 1.186 | 0.593 | 0.395 |
| Grimwith Reservoir | River Wharfe | Abstraction licence NE/027/0019/011 | 15.1 from 1st Nov to 19th Apr 7.8 from 20th Apr to 10th May 3.8 from 11th May to 11th Oct 7.8 from 12th to 31st Oct | 7.55 Nov-Apr 3.90 Apr-May 1.9 May-Oct 3.90 Oct | 5.03 Nov-Apr 2.60 Apr-May 1.27 May-Oct 2.60 Oct |
| Carr Bottom | Carr Beck | Burley-in-Wharfdale Act 1899 | 0.085 | 0.0 425 | 0.028 |

Table 2 Summary of drought permit proposals and relevant licences

Reservoir levels across our region are currently lower than normal due to below average rainfall during 2022, as well as periods of high summer demand, particularly in June and July, during prolonged hot dry weather. In most years, we receive sufficient rainfall for our reservoirs to refill over winter, which ensures we have sufficient stocks to meet customer demand and maintain compensation releases over the autumn. However, if the dry weather continues into autumn, there is a risk our reservoirs will not refill over winter.

If granted, the permits will help conserve reservoir supplies in the North West Area and increase our chances of returning to normal reservoir stocks by April 2023. This will increase the volume of water available for meeting public supply during the autumn and winter. It will temporarily reduce the flow to the receiving watercourses, which has potential to impact on the downstream environment. However, conserving supplies to aid winter refill will put us in a better position to maintain compensation releases during the coming months. Environmental assessments and monitoring plans for each site have been submitted as part of each application and mitigation measures identified to reduce the environmental impacts.

Graphs showing the reservoirs stocks in all these groups are shown in section 3.4.  The benefits of these drought permit proposals are described and evaluated in section 3.2.

# Drought permit justification

This drought permit application is necessary due to an exceptional shortage of rain threatening a serious deficiency of supplies of water in the area supplied by Yorkshire Water. Evidence to demonstrate the exceptional shortage of rain is shown in the separate document on ‘Exceptional shortage of rain 2022’, provided in support of this application.

We are applying for drought permits in the North West Area to reduce the rate of decline in reservoir stocks, and to aid the recovery of reservoir stocks during the winter. Furthermore, by maximising our prospects for winter recovery, we will decrease the likelihood of requiring drought permits in 2023 during the more environmentally sensitive spring and summer periods.

# Why we need a drought permit

Our Grid SWZ has an interconnected network (grid system) that enables highly effective conjunctive use of the available water resources using raw and treated water pipelines. During dry weather we aim to maximise use of river sources to conserve reservoir stocks for longer. However, during 2022 we have experienced exceptionally low rainfall as well as periods of very high demand; this has led to greater draw down of reservoirs, and the below average rainfall has meant reservoirs have not refilled.

Rainfall over the winter period of 2021/22 was very variable, it was dry until January with reservoir stocks at 87% full at the start of the year. A very wet February meant that stocks recovered to 95% full by the end of February 2022. However, rainfall was significantly below long term average (LTA) in March and April, with stocks falling to 87% at the end of April.

Reservoir stocks crossed our ‘Normal Control Line’ in mid-March 2022. This triggered additional activity to manage water resources and to abstract, treat and distribute more water from rivers to reduce our draw on reservoir stocks. This activity continued during the summer and will continue into autumn and winter until the water resources position recovers. We have used our grid system to move water up to 70 miles from river sources to areas in the south and west of the region which are usually supplied by local reservoirs. Throughout this period, we have been managing reservoir levels to ensure, as far as possible, that stocks are drawn down evenly across all areas.

In June and July, we experienced high customer demand due to ongoing dry weather coupled with a period of high (and very high) temperatures. The very high temperatures were unprecedented, with the highest temperatures ever being recorded across the UK, and the first Met Office Red weather warning for heat being issued. At times we had to maximise use of rivers and reservoirs simultaneously to meet customer demand, and during periods of low river flow we had to rely on reservoir supplies more than would normally be the case.

This led to our reservoir stocks depleting at a much faster rate and if the dry weather continues there is a risk, we will not be able to maintain supplies in some areas, or receive sufficient refill for levels to return to normal in the autumn. Areas of our north west reservoir group are particularly vulnerable, with the Worth Valley being a particular area of concern.  Stocks in the Worth Valley reservoirs are extremely low, and if no significant rainfall occurs, there is a risk of being unable to continue to meet demand and make compensation releases.   Stocks in the Worth Valley have declined more rapidly than in previous drought scenarios.

A temporary reduction in the compensation releases across the North West Area will help preserve stocks so that any risk to public water supplies is reduced.

# Benefits of these drought permits

The drought permit applications are all to reduce the compensation flows released to rivers from reservoirs. The sum of the benefits in these applications is up to an additional 17Ml/d or 32Ml/d which will be retained in reservoirs in the North West Area, depending on whether the reduction in flows is to half or one third of the normal compensation. The actual benefits will depend on the timing of implementation. However, assuming these permits are implemented in late summer or early autumn, the benefits of a 50% reduction in compensation flows could be about 17 Ml/d, which would give a benefit of 500 Ml per month, which is about 1% of North West Area stocks and 0.3% of regional stocks per month. If compensation flows were reduced to one third, the benefit could be up to 635Ml per month, which is 1.3% of North West Area stocks and 0.35% of regional stocks per month. However, the main benefit of reducing these compensation flows is preserving reservoir stocks to enable a compensation flow to be maintained, thereby protecting the downstream environment.

The North West area forms part of our Grid SWZ and we can provide support to it from our Grid system. However, there are limitations on how much support can be provided and for how long. Our Grid system is also used to support other areas of our Grid SWZ and we balance supplies to try to ensure stocks in each area of our region are drawn down evenly. If Grid supplies to the North West area are increased for a prolonged period, we may be increasing the risk in other areas of our region.

The reservoirs in the North West area are used in conjunction with river abstraction from the River Wharfe. Whilst we can provide support to the area, we are reliant on winter recharge of reservoir stocks to ensure supply resilience into the spring.

Lowering compensation flows will allow us to protect reservoir stocks. Lower flows from the compensation only reservoirs will minimise the support required from the supply reservoirs. The lowering of compensation flows should have less environmental impact in the winter and will give reservoirs a greater chance of recovery over the winter period. During this time, we will maximise our use of river abstractions and grid transfers.

# Deficiency of supplies due to an exceptional shortage of rain

Our drought triggers include data from a number of sources – rainfall, river flows, ground water levels and reservoir levels. Our report ‘Exceptional shortage of rainfall 2022’ provides a regional overview of conditions across the Yorkshire Water area and details the analyses we have carried out on rainfall and climate data in Yorkshire. This document is presented in support of our application. The following analyses are included in our rainfall and climate analyses in our separate report:

- Standardised Precipitation Index (SPI) calculations

- Rainfall ranking

- Rainfall probability bands

- Rainfall percentage of Long term average

- Soil Moisture Deficit (SMD)

We have analysed rainfall for the Yorkshire river catchments, and 7 reservoir group catchments. The Nidd, Ponden and Lower Laithe, Leeming and Leeshaw, and Grimwith catchments are all in the north west area, so are the most relevant to this application. These catchments all show that rainfall has been low.

The results are summarised below, but can be found in greater detail in the separate report:

- 1 month SPIs are moderately dry or severely dry

- 3 month SPIs moderately, severely or extremely dry

- 6 month SPIs are severely or extremely dry

- The 6 months March-August is ranked 2-6 for relevant catchments, with between 54% and 65% of the LTA over this period.  These are all classified as exceptionally low according to the Cunnane classification.

- Ponden and Lower Laithe (54%) and Leeming and Leeshaw (55%) have the lowest LTAs, and are both the 2nd driest 6 months ending in August in the period of record, with only 1995 being drier

- The SMD analyses show high SMDs for most areas of Yorkshire from early July, with SMDs especially high in the east of the county, and only remaining below 100 in the north and west areas.

Plots of monthly rainfall as percentage of the 1961-1990 LTA are shown in the Exceptional Shortage of Rainfall report, as are the SPI values and the results of rainfall ranking analyses.

River flows and reservoir stocks and their use as an indicator for a deficiency of supplies are discussed in the next sections of this document.

# Reservoir Stocks

Our reservoir control lines represent the value of reservoir storage that is required to guarantee a continuous rate of supply (equivalent to yield) such that the reservoir storage never falls below a critical storage line given the minimum historical inflows.

We calculate two sets of control lines:

Drought Control Line (DCL) - the DCL is designed such that stocks will never fall below marginal storage when the reservoirs supply 85% of their calculated yield.

Normal Control Line (NCL) - the NCL is designed such that stocks will never fall below the DCL when the reservoirs supply their calculated yield.

Once we have calculated the NCL and DCL, we linearly interpolate between the 100% full level and the NCL, the NCL and DCL, and the DCL and emergency storage level, to obtain the ten control lines (CLs) used in our modelling and reservoir stocks monitoring. The NCL is control line (CL) 3, the DCL is CL7, and we use CL4 as the Environment Agency trigger line. This is the trigger for Yorkshire Water and the Environment Agency to initiate communications around a potential emerging dry weather situation. The control lines are the grey curves shown in Figure 3.1; these provide Yorkshire Water’s internal control lines, used to help manage the reservoirs.

The control lines are updated on a regular basis and were last updated in 2022 based on minimum inflows from 1900 to 2020. We have remodelled our historic inflows using GR6J rainfall runoff models and extended our historic record back to 1900.

Control lines have been revised since our most recent drought plan, but the triggers in our drought plan related to control lines are still applicable to the updated control lines. We will carry out a further review of our control lines after the current drought period has ended, and when inflows are updated to include this current period.

In the operation of our reservoirs, we aim to abstract the reservoir yield when stocks fall below the NCL, but at times of high demands or in response to other system constraints we will often use a source above its yield for periods of time, and then reduce to below yield later in the year to compensate.

The figures below show regional and area reservoir stocks for this year compared to the last few years and selected dry years.

Figure 3.1 shows the regional reservoir stocks as shown in our weekly water situation report. It shows that stocks in 2022 have been very low. In recent times, only 1995 and the start of 2020 have been drier during parts of the year.

Figure 3.1 – Regional Reservoir Group stocks (from Water Situation Report)

Figure 3.2 shows the area stocks for the North West Group of reservoirs supplying Skipton, Keighley and Bradford. This area can be supported by the Moor Monkton abstraction by the transfer from Eccup in the North to Graincliffe in the North West.

Figure 3.2 – North West Area Reservoir stocks

Figure 3.3 – Nidd/Barden group reservoir stocks

Figure 3.3 shows the area stocks for the North Nidd/Barden group of reservoirs.

Figure 3.4 shows the stocks for the Thornton/Stubden Reservoir group.  Stocks in this group are relatively high because we have committed to the DWI to keep Stubden at a higher level (by topping it up from Thornton Moor) to reduce the risk of taste and odour failures at Chellow Heights WTWs.  The root cause analysis into the taste and odour issues concluded that low levels at Stubden resulted in algae drying on the reservoir banks.  When the reservoir refilled, algae was then washed into supply.  Stubden has again developed an algal bloom,  so is currently unable to be used for supply or to support compensation reservoirs until mitigation can be put in place.

Figure 3.4 – Thornton/Stubden Reservoir stocks

Figure 3.5 – Worth Valley group  Reservoir stocks

Reservoir stocks for the Worth Valley Group are shown in Figure 3.5.  These reservoirs supply Keighley, as well as providing compensation flows to the River Worth, and stocks have fallen particularly rapidly this year.

Figure 3.6 –Grimwith Reservoir stocks

Figure 3.6 shows the stocks for Grimwith Reservoir. Stocks are lower in Grimwith than they have been at this time of year in the past 8 years.

We have shown that regional stocks, north west area stocks and stocks in some of the subgroups in the north west area are well below the NCL and rapidly approaching the DCL.  The low reservoir stocks, at an earlier stage of the year than we have previously seen them (except for our most severe drought) result in an increased risk position and are reflective of an exceptional shortage of rainfall.

# The effects of the current water shortage

The current water supply situation is a result of the exceptional shortage of rainfall described in the associated report (Exceptional Shortage of Rainfall evidence, August 22). As well as the exceptional shortage of rain, the water stocks situation has been exacerbated by exceptionally high temperatures, which resulted in very high demand for water during summer 2022 (demonstrated in Sections 6). Reservoir stocks are depleted and to reduce the risk to supplies and the environment, we are preparing for the possibility of continued dry weather by taking actions in line with our drought plan. There are specific hot-spots (e.g. Worth valley), where stock levels are declining more rapidly than the average regional level and this is resulting in higher levels of risk which are a cause for increased concern.

Throughout the spring and summer, we have continually modelled and monitored our water resources situation, including estimates of the projected dates that temporary use bans (TUBs) and drought permit triggers could have been crossed. Since early June, our modelling has consistently shown that if we had a repeat of 1995/96 inflows, we would expect to cross TUBS triggers in late August or early September 2022, and drought permit triggers (our drought control line) regionally in the winter. Although our modelling shows that in most scenarios these permits will not be required, the fact that the rainfall patterns for 2022 are similar to those in 1995 and the rainfall quantities for the January to July period have been similar, means that we need to plan for this worst-case scenario.

We have operated according to the high-level strategy outlined in our drought plan, increasing the use of river sources as reservoir stocks fell through control lines. The continued low reservoir stocks have led us to plan for these permits to reduce compensation flows in order to reduce the rate of reservoir decline.

The potential threat to water supplies is a direct result of the weather conditions during this spring and summer. The threat will only occur if the conditions continue to be dry, or if we experience a prolonged period of high demand. We have acted in line with our drought plan triggers, preparing for TUBs in the summer when models suggested they would be required, and implementing TUBs, in line with our drought plan and model forecasts, from 26th August 2022.

We have modelled many scenarios for both inflows and demands and selected the permits which we think will give the most benefit and put us in the best position we can be for winter 2022 and for 2023 if the dry weather continues.

Figure 3.7: Actual and forecast Reservoir stocks

Figure 3.7shows regional reservoir stocks as part of the output of our Water Resources Planning Report (WRPR) which we generally produce monthly during the summer but have been producing weekly this year as drought conditions have continued. We use it to forecast expected reservoir stocks based on current and future asset availability. This shows the results for a repeat of 1995/96 inflows, at an annual average demand of 1295Ml/d. As well as the regional picture, we also produce graphs of area stocks, and predict WTW outputs which we use to inform our weekly production planning process.  This forecast does not show regional stocks crossing the drought control line, but stocks do fall below the DCL in some areas, and some of our previous model runs showed regional stocks falling below the DCL.

# Population affected by the drought permit

This drought permit application will alter how we operate our reservoirs in our North West Area operating zone. The North West Area is connected to our conjunctive use grid system and we are also applying for drought permits in other parts of our region. The population affected by the water shortage is that of our Grid SWZ (5,316,740 for 2021/22 as estimated population from our final WRMP 2019). The proposed permit applications will enhance our ability to supply potable water to customers and conserve water for maintaining compensation flows for longer, although at a reduced level, if the dry weather continues.

The North West Area reservoir groups supply our Bradford and Skipton forecasting zones (FCZs), which includes Ilkley and Keighley. The Skipton forecasting zone (FCZ) population is approximately 15,000 and the Bradford FCZ population 535,000 based on most recent census data.

# Summer 2022 demand

Customer water use tends to increase in summer as a result of increased garden watering, jet washing, showering and use of paddling pools and hot tubs. In the summer of 2022, we saw a large uplift in water use.

Figure 3.8: Regional Weekly Demand (from Weekly Water Situation Report)

Figure 3.8 shows the high demands experienced in 2022 compared to the preceding five years and other years selected to represent previous high demand years. This shows that in 2022 we had one of the highest weekly summer peak demands we have ever seen, except for 1996, although it should be noted that a higher proportion of the 1996 demand was due to leakage. Demand was close to levels seen in 2018, but high demand did not occur for as long. We had a weekly peak demand of 1480 Ml/d in the week of 20th July, and peak day demand of 1573 Ml/d on 19th July.  This high demand has been driven by exceptionally high temperatures and dry weather, with the first ever Met Office Extreme Heat red weather warning issued on the 15th July 2022 for the 18th-19th July 2022. Further demand peaks occurred in August with an amber weather warning for extreme heat from 11th-14th August.

Figure 3.9: Regional Monthly 2022 Demand and Temperature

Figure 3.9 shows monthly 2022 regional demand plotted alongside monthly average temperatures (calculated from weekly MORECS data), for the 1993-2021 average and for 2022. The peak demand in July corresponds to the far higher than average temperatures.

Figure 3.10 Relationship between average temperature and demand

Figure 3.10 shows weekly regional demand plotted alongside average weekly temperature, and Figure  3.11 shows weekly 2022 regional demand plotted alongside average weekly sunshine hours.  Both show that demand increases in relation to high temperatures and longer sunshine hours.

Figure 3.11 Relationship between average hours sunshine and demand

# Leakage control

In the reporting year 2021-22, leakage was 283.08 Ml/d which overachieved the Ofwat in-year target of 286.3 Ml/d. This was a reduction of 7.9% in the AMP7 period, against the target of 7.4% after year 2. In years such as 1995-6 and 2017-18 when demand levels were higher, leakage levels were also significantly higher at 535 Ml/d in 1995-6 (which is equivalent to 323 Ml/d when using modern leakage reporting methodology. The introduction of mandatory leakage targets, and significant investment in monitoring infrastructure to facilitate detection and repair, has resulted in a 47% reduction in reported leakage.

Each year we find and repair leaks on our distribution network to drive down our average daily leakage. These reductions in leakage are achieved through additional find and fix resources and new and innovative leakage detection techniques. Our regional leakage target for 2022-23 is 285.21 Ml/d to hit the three-year rolling average and keep on track for a target reduction of 15% by 2025.

During hot, dry weather customer demand increases significantly, and the pattern of customer demand changes, making it much harder to determine where leakage is occurring and where increasing flows are due to leaks or increased customer demand. This summer we have experienced increased breakout of leaks as during hot, dry weather, ground movement increases causing our pipes to burst. In a normal year ground movement causes about half of our leaks, but the change in soil moisture this year is unprecedented, and the number of burst mains has increased by 33%.

We started this financial year ahead of this year’s target, having overachieved during the mild winter of 2021-22. Our additional leakage activity reduced leakage to planned low levels after the normal winter peak by the middle of June. However, we saw an increase of 25Ml/d at the beginning of July due to the extremely hot and dry weather spell which put pressure on the Water Network due to high demand and low soil moisture. Our current leakage figure (which relies on some in-year projections) is 286.34 Ml/d, which is above our business plan due to the extreme weather but still within parameters to hit the year end regulatory target.

# Demand on the affected water source

Table 3.1 shows demand volume in the Yorkshire Water region divided into forecasting zones. The zones directly affected by this Drought Permit are shown in bold text.

The average demand in the Bradford and Skipton FCZs is approximately 180 Ml/d, and the present demand is 178 Ml/d to supply. Our compensation requirements for the group are up to 46Ml/d but can be less as some reservoirs releases are dependent on control lines and Grimwith Reservoir is subject to seasonal variations.

| Yorkshire Water Forecasting Zones | Area | Demand in Zone (31st August 2022) Ml/d |
| --- | --- | --- |
| Leeds, Harrogate and Dales | North/Central | 229 |
| Sheffield | South | 255 |
| Bradford & Skipton | North West | 169 |
| Calderdale & Wakefield | South West | 217 |
| Hull | East | 163 |
| Malton, York, Doncaster, Selby | Grid and groundwater | 219 |
| Regional | Regional | 1251 |

Table 3: Weekly Water Demand

The Yorkshire region is divided into forecasting zones (FCZ) for assessing demand. FCZs group parts of Yorkshire by the water treatment works which are most commonly used to meet their demand. The FCZs are not discrete areas and connections within the grid system allow water to be imported and exported between FCZs.

The Grid water network in the Grid SWZ utilises Elvington and Loftsome Bridge WTWs in the East and Chellow Heights WTW in Bradford to support the local supply sources in the Yorkshire region. Elvington and Loftsome Bridge WTW take water from the Rivers Derwent and Ouse, which is then transferred via the Grid network of pipelines across Yorkshire. Grid sources are currently being maximised to conserve reservoir stocks where possible across the region. Table 3.2 shows the water treatment works outputs supplying the Yorkshire Grid.

| WTW | Current Output to Grid Ml/d (1st September) | Main Sources |
| --- | --- | --- |
| Elvington | 189 | River Derwent at Elvington and River Ouse at Moor Monkton |
| Loftsome Bridge | 64 | River Derwent at Loftsome Bridge |
| Chellow Heights | 125 | Nidd Barden and Grimwith Group and Thornton Group and River Wharfe at Lobwood |

Table 4: Grid Water Treatment Works

A graph of current and historical regional demands is shown in Figure 3.8.  It shows the high demands experienced in 2022 compared to previous years including years selected to represent previous high demand years. This shows the peak demands have been high, and we have had some of the highest daily peaks we have seen. These high demands have been driven by exceptionally high temperatures and dry weather in a series of heatwaves, including record breaking temperatures in July.

Figure 3.12 shows the demand on the water treatment works in the north west area, and for Sladen and Oldfield WTWs. Some of the water is exported to other areas, and the area can also be supported by transfers from the Grid, but these transfers are limited by network constraints and allowed abstractions when river flows are low, or as we start to plan to preserve our annual licenced quantities for periods of high demand in the winter.

The interventions to reduce the abstractions from the Worth Valley can be seen by the decreasing use of the Sladen and Oldfield WTWs from June 2022. These interventions are described in section 4.6.

Figure 3.12 Demand and Output of North West WTWs (from Water into Supply report)

# Drought permit alternatives considered

We have so far managed the situation by promotion of water saving to customers, maximising leakage reduction activity, and maximising our river abstractions where possible to conserve reservoir stocks. In the north west area we have increased abstractions on the River Wharfe at Lobwood (and Arthington in the north area) when river flows have allowed.  River flows have been low for the time of year for much of the time, so our allowed unsupported abstractions have been limited.

All reservoir fed water treatment works have been minimised and the Grid has operated at higher flow rates for long periods.

Additional staffing and standby provision have been employed across all areas of Yorkshire to ensure that any interruptions due to mechanical failures are resolved as soon as possible

We intend to apply for drought permits to increase allowed abstractions on the Rivers Ure and Ouse, to reduce the regulating release in the lowest flow band for abstractions from the river Wharfe at Lobwood, and to reduce compensation flows for the south, north and south west reservoir groups.

We have followed the steps in our Drought Plan 2022 and are applying for these permits in order to preserve stocks as much as possible in anticipation of an event worse than one we have experienced before.  We believe applying for these permits, and the others listed in Section 6.0 is the best course of action at this point in time.

# Consequences if the drought permits are not granted

We have considered not applying for these permits, and our modelling of past events shows that we could maintain supplies through most of our historic years without permits, but to adequately ensure supplies are maintained in some of our worst drought years, permits are required.

If these permits are granted, we will be able to manage our system in a more resilient way. If these permits are not granted (or the decision to grant them occurs too late for us to manage supplies as if it were granted), we will have to operate according to the current licence conditions, and this may result in the overdrawing of reservoirs.

If we had a repeat of 1995 inflows and these permits were in place, reservoir stocks in the North West Area supply reservoirs could be increased by up to 12% and by 3% regionally if the changes associated with the application are applied in full. The actual benefit of the drought permits would depend on river flows and reservoir inflows during the period, and how much and where reservoir stocks had recovered.

If these permits are not granted, (or the decision to grant them occurs too late to manage supplies as if it were granted), we face the risk of entering winter with the reservoir stocks below the drought control line throughout the north west area. In respect of specific hot-spots (the Worth Valley), there is also heightened risk in that public water supply could be impacted due to the higher rate of decline of stocks in this area. Additional mitigation measures are being developed to reduce the risk of this situation materialising, though these measures alone shall not alleviate the risk to the public water supply.

# Actions taken to reduce demand and conserve supplies

Promoting water efficiency to our customers is part of our day-to-day operations during all weather conditions. In line with our Drought Plan we implemented additional demand management actions in reaction to crossing drought triggers in 2022. Demand reduction helps us conserve supplies for later in the year if the situation does not return to normal. At the same time, we constantly review our raw water resources to make best use of the water available to us. Wherever possible, we operate to conserve supplies that can be stored for use later in the year by reducing the use of reservoirs and increasing the use of river abstractions.

Customer-use demand reduction actions are implemented in response to crossing drought control lines using a phased approach.  This starts with appeals for voluntary reductions in use, escalating to imposing temporary use bans then applying for a drought order to restrict non-essential use. In 2022 lower than normal reservoir stocks triggered the need for appeals for voluntary reductions, and we are planning to impose Temporary Use Restrictions on the 26th of August.

In February 2022, our regional reservoir stocks were above 95% and we started the spring in a good stocks position, with many reservoirs full. At this time, we were implementing our normal water efficiency measures and preparing for our annual summer campaign. We have had below average rainfall since March, and reservoir stocks have decreased steadily, with only 1 week at the start of April showing an increase.

Elevated temperatures in June led to peaks in demand of 1413 and 1434 ML/d on the 17th and 22nd July, respectively. Further elevated temperatures in July led to demands of 1505Ml/d and 1573 on the 11th and 19th of July. These July peaks occurred at a time of a heatwave and the first ever Met Office Extreme Heat red weather warning.

As a result of the peak demand and lower than average rainfall, reservoir stocks reduced to lower than average levels, and we crossed our normal control line and early warning Environment Agency control line. In line with our Drought Plan we implemented demand management actions to reduce demand and conserve available water resources in reaction to crossing these triggers.

The following sections list the actions we carried out as a result of crossing control lines. A timeline of the customer communications appealing for reductions in water use during 2022 is provided in Appendix 1. This provides a breakdown of the measures we used to raise awareness of the heightened need to use water wisely in our region and the number of customers exposed to the messages (reach).

# Demand management during normal operating conditions

During normal operating conditions, the Yorkshire Water website provides water saving information and a link for customers to order free water saving packs. It includes a page dedicated to water resource management, where our current Drought Plan and Water Resource Management Plan (WRMP) are available to download.

We have education centres at several sites (Headingley WTW, Ewden WTW, Tophill Low Nature Reserve) and a Living with Water Learning Lab hosted by Wilberforce College (Hull), which schools and other groups can arrange to visit.  We cover a range of topics including the water cycle and water conservation during the sessions, alongside other themes such as flooding, wastewater education and water safety.   We also offer an outreach programme and virtual live assemblies. Our website offers our green classroom pack for teachers to download. These lesson packs provide educational material on the water cycle and the importance of water conservation.

Each summer the Yorkshire Water Brand and Communications Team delivers a water efficiency campaign, which educates customers on ways to save water in their homes and gardens and encourages customers to find out more information about water conservation via the Yorkshire Water website. This typically involves a media plan of activity such as ‘paid for’ social media advertising, digital display ads, a detailed content plan for organic social activity and customer emails, along with a mixture of other paid for advertising such as: radio (traditional and digital), press, digital out of home adverts and TV advertising.

The Communications team also ensure there is a presence at large events in the region, this year sponsoring The Great Yorkshire Show and having a stand dedicated to Water conservation messages to engage and educate customers of all ages about water conservation. We also teamed up with local radio stations to deliver ‘on the street’ events in four busy town centres during the summer holidays (Leeds, Hull, Sheffield, and York) this gave us the opportunity to talk to customers face to face about ways to save water and answer any questions or concerns they have about water conservation, droughts, hosepipe bans etc.

There is also a media plan of pro-active press office activity, including: joint press releases with other partners, paid for editorials in local newspapers and a PR campaign that works with social media influencers to recommend water saving tips and advice. Included in the Communications plan is a content plan for colleagues within the business as well as promotional material for the retail team to share with non-household customers to encourage them to become more water efficient.

This year’s campaign was developed from the insight and learning we gained after 2018, after carrying out research on customer’s views on water efficiency and TUBs. The research carried out told us that customers were more likely to get on board with messaging and change their behaviours when the advice feels achievable, and they can understand why there is a need for change. The research also showed for some segments of customers, a financial benefit is more likely to make them change too. We also had to take into consideration the current external climate and other financial or personal challenges that many of our customers might be facing. Having this in mind helped us develop the ‘Use Less. Save more’ campaign, in which we crafted messaging and creative materials that speak to customers in the right tone of voice, feels relatable and includes enough of the ‘why’ (explaining why we need to save water) as well as practical, achievable tips that most people can apply in their everyday lives. Some of the more dynamic channels in our media plan, such as social and digital advertising allow the flexibility to be able to switch the messaging on ads depending on the weather, for instance: we have referred to ‘There’s not been much rain lately’ or ‘No need to water the lawn, there’s been a bit of rain.’ This was to help customers understand the link between rainfall, the impact on our reservoir levels and how they can help.

Our communications to customers during the hot, dry weather this year has been at a regional level aimed at targeting all Yorkshire Water customers. The North West Area is part of our Grid SWZ and in line with our Drought Plan we implement water saving messages at a zonal level.

# Metering

The number of domestic customers in the Yorkshire Water supply area receiving water via a metered supply is currently 58%. Most commercial properties are metered, with the exception of some small water users where metering is not practical. All new build properties receive a metered supply and unmetered households can opt to have a meter installed free of charge. The Yorkshire Water region is not classified by the Environment Agency as a severely water stressed area, therefore we are not able to compulsorily install meters in domestic customers’ properties.

We promote metering to our customers as a means of saving water and money. We are transparent on all unmeasured bills, showing the comparative metered costs to all customers. This allows customers to make informed decisions as to whether a meter is right for them.  Demand for meters was impacted through COVID and is yet to return to expected volumes, although we have seen an increase. We believe this slow return to be due to the current financial crisis meaning customers prefer guaranteed bills.

We have an extensive partnership network to help increase our reach to customers experiencing affordability challenges. We plan to continue to utilise this network in understanding where a meter could reduce charges for customers and continue with other forms of support to vulnerable customers.

# Leakage reduction activity

Enhanced leakage reduction is included as a drought option in our Drought Plan for implementation when reservoir stocks are predicted to be 10 weeks from crossing the drought control line. We retained an increased number of leakage inspectors since the escalation of 2018 in order to meet our 2025 leakage target. This year we have employed additional resources to fix leaks and bursts in our region. This additional activity includes a new ‘Smart Leakage Team’ to support leakage reduction through the integration of ‘smart technology’ in our networks. Enhanced leakage activities include:

Overtime including 7-day working for leakage inspectors, support staff & field technicians.

Additional personnel fixing leaks - We had 56 contractor teams (112 people) on primary leakage work in July 2022. This is a 25% increase on the 45 teams (90 people) we had in July 2021, despite the workbasket being 25% lower this year.

We have found and fixed 10,968 leaks in the first 4 months of this financial year.

295 Pressure Reducing Valves (PRVs) maintained and or optimised in the last 4 weeks to reduce bursts and leakage.

We have repaired or renewed 2,000 customers’ leaking supply pipes to help our customers tackle their leakage.

We have dedicated teams to find leaks on trunk mains - using satellites in rural areas where leaks are more difficult to identify.

We have optimised our fleet of 38,000 acoustic loggers to more quickly and efficiently find and fix breakout leakage.

We are utilising a live hydraulic model across several of our most challenging leakage areas to understand underlying causes of network performance. The hydraulic model solution aims to reduce leakage in these areas to their lowest ever level.

Leakage activity in the North West Area

Leakage in the North West of Yorkshire is lower than the regional average due in part to its rural nature. Leakage hotspots are focused around the urbanised areas of Keighley and Skipton. As part of our ongoing work to reduce leakage in our region and achieve a 15% reduction by 2025 we are including a number of new approaches and these have been deployed in the North West area.

We have permanently installed 4,600 acoustic loggers listening for leaks in some of our most leaky areas, this includes several DMAs in Keighley and Skipton.

We installed an additional 500 lift and shift acoustic loggers to locate leaks in higher leakage rural areas where network coverage is limited.

We invested in a number of new permanent and temporary meters to narrow down leaks into smaller discrete areas for ease of locating leaks.

We have installed a network of high density pressure loggers to identify and locate leakage.

We developed hydraulic models for the most difficult areas to support leakage reduction.

We have used satellite imaging to find leaks in rural areas where leaks are more difficult to identify.

We tested the raw water mains for leakage.

We have shifted resources from other parts of the region to support this activity.

In the Keighley water supply system (WSS) we have reduced leakage by 30% since July and we are repairing any leaks in the Keighley WSS twice as fast as the regional average.

# Trigger: Reservoirs crossed our normal control line

We meet customer demand through use of our licensed water resources, which include reservoir, river, and groundwater supplies. In most years, we have sufficient rainfall to balance our resources to ensure regional reservoir stocks remain above the normal control line. If the normal control line is crossed it is a trigger for us to review our operations and identify where the use of river supplies can be increased in preference to reservoir supplies. This helps to conserve reservoir stocks during periods of low rainfall.

In 2022 regional reservoir stocks crossed the normal control line on 28th March 2022. In reaction to this we reduced our use of reservoir supplies in our Grid SWZ and increased our use of river and groundwater abstractions to meet demand. This included increased abstraction from the River Derwent at Loftsome Bridge to reduce abstraction from reservoirs across our region. Although regional stocks crossed the NCL on 28th March, the NCL for individual reservoirs and groups was crossed at different times. Our operating strategy is to try to balance the rate of fall of reservoirs as much as possible to ensure a balanced risk across the region. We have operated the Worth Valley reservoirs at or below yield since they dropped below the group NCL in the week commencing 18th April, and they have operated at or below yield since then.

All year, free water saving packs are available for customers to order through the Yorkshire Water website.  Our Communications Team started to talk to our customers about water saving in April, followed by adverting using social medial channels and our website in May.

# Trigger: Reservoirs crossed Environment Agency early warning trigger line

Regional reservoir stocks reached the Environment Agency early warning trigger on 23rd May 2022 and we started implementation of our drought communications plan. At this stage, our region was not considered to be in drought and this trigger ensures we start implementing actions early to lessen the impacts if the situation worsens.

In reaction to the dry weather and elevated temperatures we launched our “Using Water Wisely” campaign to raise awareness of the increased demand we were experiencing and to notify customers of the heightened importance for reducing water use. As a follow up, we launched our 'Thanks for' water saving campaign which focused on thanking customers for “using water wisely and helping to keep Yorkshire flowing.”

By changing the artwork and messages in media promotions we were aiming to keep customers’ attention and reiterate the water saving message.

The actions included:

Raising awareness of the developing situation, such as increased demand due to elevated temperatures and declining water stocks due to low rainfall.

Promoting the importance of reducing demand for water in our region and requesting customers to make voluntary reductions in water use.

Promoting our free retrofit devices and tips on how to save water.

Requesting customers to report any leaks or bursts in our region.

As part of our advertising for our priority services we asked any customer who needed extra care, support or are vulnerable during the hot weather to contact us.

Our Wholesale Service Desk opened discussions with retailers and in collaboration with Water UK and other water companies provided advice to commercial users on saving water. This was made available through our website and proactively highlighted to Retailers by email and the ‘Retailer Portal.’

Liaised with retailers and commercial water users on any changes to water services such as re-routing supplies, which can impact on the products or processes of commercial users.

Free ‘flushsaver’ devices offered to commercial water users on our website.

Information was communicated to customers through a variety of media channels. A programme of media promotions during summer 2022 and the number of customers reached is provided in Appendix 1. Social media and digital advertising offer the ability to reach a large number of customers, although only a proportion will click on the links for further detail. Radio and newspaper advertising were used to reiterate the messages and reach those customers not exposed to digital advertising.

The media channels are outlined below:

The Yorkshire Water homepage banner was focused on water saving and the Yorkshire Water intranet front page included an article on the dry weather situation to inform colleagues.

Repeated messaging on Yorkshire Water’s social media channels (Facebook and Twitter) promoted water saving messages and requests for voluntary demand reduction.

At the start of July, we launched paid for adverts on social media reaching to up to one million customers a week. At the end of July, we switched to programmatic display advertising, allowing us to focus messages to cohorts of customers. For example, water saving tips for the kitchen and bathroom were aimed at young families whereas using a watering can instead of a hose was the focus in areas with large gardens. This reached up to 7.5 million customers a week.

Google display advertising during July and August was directed to up to 21 million customers a week.

Adverts promoting the need to save water were also delivered by local radio stations including, Yorkshire Coast Radio, Hallam FM, Heart FM, Stray FM, and Capital radio. This was aimed at a combined audience of up to 3 million customers a week.

We partnered with Sunrise FM, Radio Sangram and Coast & Country to deliver radio advertising to our customers in a range of languages including; Urdu, Punjabi, Pathwari, Bengali, Pushto and Polish.

From July to September adverts for water saving were placed in regional newspapers including the Sheffield Star, Sheffield Telegraph, Harrogate Advertiser Series, Scarborough Evening News, Yorkshire Post, Yorkshire Evening News, and The York Metro. The combined estimated readership is over 180,000.

Outdoor digital advertising reached an estimated 145,000 customers.

Bill inserts with water saving tips were included in water bills sent to 87,500 households each week.

Yorkshire Water representatives delivered television and radio interviews on local news channels.

In addition to heightened water saving messages, we continued to optimise operations across our Grid SWZ to preserve regional reservoir stocks:

We maximised river abstractions where possible, but due to low river flows and asset availability this was limited at times.

We maximised groundwater abstractions within licence constraints.

We experienced extremely high demands most notably in late June and into July, and at times we had to maximise use of reservoirs as well as river abstractions where available. River sources and our grid system were used strategically to support each area of our Grid SWZ as much as possible and balance the drawdown of reservoirs across the region to ensure no area was unnecessarily exposed to a greater reduction in available resources.

Normally we try to release approximately 10% above our required compensation flow releases, to ensure that we are meeting our statutory obligations for compensation. This summer, to help preserve reservoir stocks, we reduced this tolerance on compensation releases from 10% to 5% where an assessment identified this was feasible. This is in line with our operating strategy when the Environment Agency trigger line is crossed.

Where possible we have taken action to reduce the output of water treatment works supplied by the reservoirs and meet demand through increased use of our grid system to reduce the rate of draw down from the reservoirs. The actions to reduce the use of reservoir sources are explained below:

We have maximised all river abstractions where river flows and asset availability allow.

We have maximised abstractions on the River Ouse at Moor Monkton to Eccup and Wetherby when assets and river levels allowed.

Use of River Wharfe abstraction at Lobwood increased when river flows allowed, preservation of Grimwith reservoir stocks and stocks in the Nidd reservoirs.

Increase in Grid to Eccup supplies, allowing increase in Eccup to Graincliffe transfers, reducing the use of North West Area reservoirs whenever the River Ouse was available at higher flows.

Reduction in Compensation flows to allow lower margin of tolerance above required

In July heatwave abstraction remained below yield in the Worth Valley.

# Trigger: Reservoir stocks predicted to be 10 weeks from crossing the drought control line

The next trigger for implementing drought actions is when regional stocks are predicted to be 10 weeks from the drought control line. During dry periods we model reservoir stocks against forecasts of a repeat of previous droughts in our region. On the 6th June 2022, our modelling predicted a risk of reservoir stocks reaching the 10 weeks from crossing our drought control line (4 weeks before implementing TUBs) on 1st August if we had a repeat of the 1995/96 rainfall. The modelling was repeated weekly to represent the actual demand and rainfall experienced each week. By re-modelling declining stocks each week, we were able to monitor the situation and the likelihood of meeting the 10-week trigger line. The modelled data of crossing the 10-week trigger stayed relatively constant throughout the summer, and we crossed this tigger (4 weeks before TUBs implemented) on 25th July.

We took the decision to start implementing some of the actions triggered by stocks being 10 weeks from crossing the drought control line early, rather than wait until we reached this trigger. These actions were to ensure we were prepared for restrictions on use and drought permits if required later in the year, and included:

Preparation of notices, adverts, and website content for temporary use bans in case needed.

Preparation of supply side drought permit application templates with details on the 2022 dry period.

Environmental assessments, including walkover surveys of potentially affected river reaches, and updating of our Environmental Assessment Reports to reflect the drought situation (see Section 6).

When demand dropped after the July heatwave this has allowed us to import additional treated water into the Keighley area

The following re-zoning has been carried out over the past few weeks.

  - 0.5Ml/d import from Chellow WTW to Keighley.

  - 1.5Ml/d import from Riddlesden into Bracken Bank distribution from Graincliffe WTW

  - 2.0Ml/d additional from Riddlesden to Blackhill SRE from Graincliffe WTW & Embsay WTW.

  - (An additional 1.0Ml/d to 1.5Ml/d on the above links into Blackhill SRE will be completed in the next 7 days)

All the above changes combined will reduced WTW output to around 8.5-9.0Ml/d which is just above 50% of yield of the Worth Valley reservoirs.

Additional actions are being developed and assessed to increase support to the Worth Valley, as the rate of stocks decline remains higher than the average regional rate.  The aim is to implement these interventions over the next 2-4 weeks in conjunction with the drought permit application to reduce compensation releases.  Interventions will continue to focus on supporting this area through raw water support and network re-zoning.

# Trigger: Reservoir stocks predicted to be 8 weeks from crossing the drought control line

This trigger was predicted to be crossed on the 15th August in our 1st August model runs. We ramped up our drought permit application work and our TUBs preparation, and, in line with our Drought Plan process, on 12th August we advertised that TUBs would be implemented on 26th August. TUBs were duly implemented on 26th August.

Following the implementation of TUBs on 26th August 2022 we have seen an estimated 2% reduction in Distribution Input (DI) resulting in a demand reduction of 88Ml/d on our network.

In the following analysis, we have compared our current DI and PCC data from June 2022 to September 2022 with the equivalent data in 2018. We have chosen 2018 as the comparative year as we experienced similar conditions to 2022, due to the hot dry summer where we issued drought permits but didn’t need to enact a TUB.

Figure 4.1 shows our DI since 1st June 2022 and the reflective data in 2018, summer demand in 2018 was on average 1351Ml/d which reduced to 1286Ml/d in the 2 weeks following the August bank holiday resulting in a demand reduction of 65Ml/d. Historic data shows that over the same period leakage reduced by 5Ml/d therefore, overall demand reduction was 60Ml/d in 2018.

In 2022, summer demand was on average 1343Ml/d which reduced to 1248Ml/d resulting in a demand reduction of 95Ml/d. Over the same period in 2022 leakage reduced by 7Ml/d therefore, overall demand reduction was 88Ml/d.

Compared to 2018 demand in 2022 is 28Ml/d lower than expected. We consider that TUBs will be a major factor in this reduction, although the slightly wetter weather, compared to the same period in 2018, will also have an impact. We have estimated a 25Ml/d impact of TUBs, allowing a small drop due to weather, which is around 2% of average September/October demands.

Figure 4.1: Distribution Input (DI) since 1st June 2022 to present with 2018’s DI included as a comparable year

We have also seen an associated reduction in consumption based on data from our various consumption samples and monitors. For the purpose of this application, we have used PCC from our Domestic Customer Monitor (DCM) sample as this data is available daily, so we are able to see the impact that a TUB has had on this sample. Our measured household data is only obtained monthly via volumetric reads which means we don’t have the granularity required to see the impact of a TUB on these households.

Figure 4.2 shows our PCC taken from a sample of circa 1000 households on our DCM sample across Yorkshire. We can see from the data that consumption in summer 2018 was on average 141 l/h/d which reduced to 126 l/h/d in the 2 weeks following the bank holiday - a reduction in consumption of 15 l/h/d. In 2022, that consumption in summer was on average 133 l/h/d which reduced to 109 l/h/d resulting in a consumption reduction of 24 l/h/d.

Compared to 2018 consumption in 2022 is 9 l/h/d lower than expected which equates to an estimated 45Ml/d. TUBs are likely to be a contributing factor in this reduction. However, when analysing both DI and PCC reductions since TUBs were implemented, we also need to take into consideration other factors that can impact demand including weather conditions, customer holidays, water conservation activity and non-household consumption. These factors can all influence changes to demand and any decreases that we may see in the data.

Figure 4.2: Per Capita Consumption (PCC) from our DCM sample since 1st June 2022 to present with 2018’s PCC included as a comparable year

# The use of sources in 2022

Due to the high demands in the summer of 2022, we have produced more treated water than in most years. This section describes source outputs this year in comparison to recent years and explains our operation of our sources this year.

Figure 4.3 shows total abstractions for the Yorkshire Water supply area and shows the proportion of those abstractions supplied by the different source types for the licencing years April to March. The figures for 2022/23 are based only for the period until July 2022, so do not include any additional winter demand or the usual increase in the use of reservoir sources when reservoir levels tend to be high in the winter but do include the higher summer demands to date.

Figure 4.3: Total abstractions and proportion supplied by different source types

The figure shows that for most years the proportion of use of reservoirs is greater than that of rivers, apart from 2011/12 and 2018/19. In 2011/12 there was high water production and river use in the winters due to cold conditions and associated freeze thaw events causing increased bursts and leakage. The 2022 data shows a higher proportion of river abstractions compared to the previous wetter years, and this is likely to continue to increase as river flows increase in the autumn and winter and we maximise these sources to allow reservoirs to recover. The increased abstractions in 2020 and 2021 reflect the uplift due to the high Covid-19 demands.

Figure 4.4: Regional Reservoir Stocks

Figure 4.4 shows regional supply reservoir stocks for 2021 and 2022. In 2021 stocks crossed the Normal Control Line in April, but significant rainfall meant that the EA Trigger was not crossed, whereas this year, the NCL was crossed two weeks earlier, but no significant refill has been experienced. When reservoir stocks fall below the Normal Control Line, we increase the use of river sources. The use of two key rivers that supply our ‘grid’ system are shown in Figure 4.5 and Figure 4.6, which show daily abstraction from the River Derwent at Loftsome Bridge and Elvington, and from the River Ouse at Moor Monkton.

Figure 4.5: Abstractions form the River Derwent 2021 and 2022

In 2021 and 2022 there is a similar pattern of use until summer, when this year we increased our use of river sources in response to high demands and decreasing reservoir stocks.

Figure 4.6: Abstractions form the River Ouse at Moor Monkton 2021 and 2022

Figure 4.6 shows the licenced and abstracted amounts for the River Ouse at Moor Monkton. It shows that we have maximised the abstraction within operating constraints and requirements in 2022. In the highest flow band (at river flows above 1000Ml/d) we are licensed to abstract 300Ml/d, although the infrastructure required to abstract that volume is currently not in place.

The two pumping stations at Moor Monkton contain multiple pumps that allow us to pump water to treatment sites at Eccup No 2 WTW, Headingley WTW, Huby WTW and Elvington WTW. Pump availability at Moor Monkton was reduced in spring and early summer due to a pump failure, which initially constrained the volume of water abstracted from the river. The repair was completed in June 2022, and the pumps returned to full operation in early July when river levels recovered sufficiently to allow their use.

Figure 4.7: Flows and abstractions for the River Wharfe

Figure 4.7 shows the gauged flows recorded on the River Wharfe at Addingham for 1995 and 2022, as well as releases from Grimwith Reservoir and abstractions at Lobwood and Arthington for 2022.

For the early part of 2022, flows in the River Wharfe were low, with support required from Grimwith in January (quite unusual) before an extremely wet February, when there was widespread flooding. With only one above average rainfall month in the winter, by the end of March, Lobwood abstractions were again in the lower flow bands, requiring support from Grimwith reservoir, and were lower at times than in 1995. Occasional rainfall has increased river flows above the threshold requiring support for short periods, but most of the time river flows have required support to allow abstraction at Lobwood, so reservoir stocks have been depleted. The rainfall at the end of July allowed a few days where no support was needed. Arthington pumping station was flooded in February and was consequently out of operation until the start of August. Had it been operational, it would have been used when river levels were in the higher bands, and since it has returned to use, it has been used to support Lindley Wood compensation reservoir when river flows allow it to be used without support from Grimwith.

We report use of licences (abstractions vs allowed) monthly. Most of our licences show low use compared to licence because our licenced quantity is far more than demands, allowing us to operate flexibly and in response to current conditions. This year reservoir use is lower due to low reservoir stocks, and although rivers are being used more than reservoirs, we are not approaching annual licenced maxima for some licences as we are also constrained by daily hands-off flow thresholds. For river licences we will monitor the situation as we progress through the year, and if required may apply for licences to increase the annual limit (Derwent at Loftsome Bridge as well as Wharfe at Lobwood).  We submitted a licence variation application in March 22 to increase the annual abstraction licence at Lobwood. The assumption is that this application requires determination rather than YW submitting a Drought Permit requesting the same action.

# Environmental impacts of drought permit

During the preparation of our Drought Plan 2022, a ’shelf copy’ Environmental Assessment Report (EAR) was produced for each supply side drought option or group of options.  The EAR provides an independent and robust assessment of the potential environmental effects of the implementation of our drought options.

The environmental assessment was conducted in accordance with Government regulations and using the Environment Agency’s 2020 Drought Plan Guideline (DPG) and the Environment Agency’s July 2020 ‘Environmental Assessment for Water Company Drought Plans- supplementary guidance’, and comprised the following components:

an assessment of the likely changes in hydrology (flow/level regime) due to implementing the proposed drought options;

identification of the key environmental features that are sensitive to these changes and an assessment of the likely impacts on these features;

identification of mitigation that may be required to prevent or reduce impacts on sensitive features; and

recommendations for baseline, in-drought and post-drought order monitoring requirements.

The environmental assessment focuses on the potential changes to water availability (levels and flows) and any consequent implications for geomorphology, water quality, ecology, and other relevant environmental receptors, for example, landscape, navigation, recreation, and heritage. Cumulative impacts with other drought options are also considered.

The assessments undertaken confirm the features requiring consideration of monitoring and mitigation; which are provided in full in the Environmental Monitoring Plan (EMP).

Throughout the environmental assessment process, we have proactively engaged key stakeholders, including the Environment Agency and Natural England.

During the prolonged dry weather, dialogue was initiated with the Environment Agency and consultants were instructed to prepare ‘application-ready’ EARs and undertake the onset of drought walkovers. The application ready EAR, and EMP, are provided alongside this drought permit application.

# Water Supply Strategy for the Continuation of Drought

Our grid system allows us to move water around the region and we aim to balance resources so that our customers receive the same levels of service. This makes us resilient to drought conditions and in recent dry years (2003, 2006 and 2011) we have not been required to apply for drought permits. However, following an exceptionally dry year and unprecedented summer demand in 2018 we applied for winter drought permits to aid reservoir stock recovery, but did not need to implement them when reservoir stocks recovered after heavy rainfall.

Our Grid SWZ has an interconnected network (grid system) that enables highly effective conjunctive use of the available water resources using raw and treated water pipelines. During dry weather we aim to maximise use of river sources to conserve reservoir stocks for longer. However, during 2022 we have experienced exceptionally low rainfall as well as periods of very high demand; this has led to greater draw down of reservoirs, and the below average rainfall has meant reservoirs have not refilled.

Reservoir stocks crossed our ‘Normal Control Line’ in mid-March 2022. This triggered additional activity to manage water resources and to abstract, treat and distribute more water from rivers to reduce our draw on reservoir stocks. This activity continued during the summer and will continue into autumn and winter until the water resources position recovers. We have used our grid system to move water up to 70 miles from river sources to areas in the south and west of the region which are usually supplied by local reservoirs. Throughout this period, we have been managing reservoir levels to ensure, as far as possible, that stocks are drawn down evenly across all areas.

We will continue to closely monitor the water resources position and alter our operational activities to preserve stocks across the region. We have taken mitigating actions in line with our drought plan, with actions undertaken to date listed in section 4.  We will continue to operate in accordance with our drought plan and expect to apply for additional drought permits and orders as listed in Table 6.1.

Table 6.1. lists all the permit applications we have discussed with the Environment Agency and plan to submit in 2022.

| Permit application | Drought Action |
| --- | --- |
| River Ouse at Moor Monkton | Increase permitted abstraction at lower flows. |
| North West Area | Reduce compensation releases |
| River Ure at Kilgram | Allow abstraction below HOF |
| River Wharfe at Lobwood | Reduce regulating release from Grimwith in the lowest flow band |
| South Area | Reduce compensation releases |
| North Area | Reduce compensation releases |
| River Derwent at Loftsome Bridge | Transfer abstraction licence permissions from Elvington abstraction point on the River Derwent to Loftsome Bridge abstraction point downstream. |
| South West | Reduce compensation releases |
| River Wharfe | Increase annual licence (if licence increase application not received) |
| River Hull | Alter hands off flow requirements |

Table 5: Drought permit applications

If the Environment Agency grant the drought permits, we are applying for in 2022, they will be valid for up to the end of March 2023. We may not implement the drought permits if we receive sufficient rainfall.

If we do not receive sufficient reservoir refill for our region to be no longer in drought by 1st April 2023 further drought actions may need to be implemented. We would consider the situation to have returned to “normal” if regional reservoir stocks are above the normal control line and none of our area reservoir groups are below control line 4 (the Environment Agency Early Warning Trigger line). We will continue to maximise use of river resources until the situation recovers and our communications to customers will continue to target water conservation.

To mitigate the impact of the drought, we will continue to promote the need for water saving to our customers throughout the Yorkshire region. This will be delivered through press releases, public engagement, and collaborations with third parties. By collaborating with others, we will be able to provide a stronger message that reaches a wider audience.

We will seek to work with other water companies, the Environment Agency, Natural England, Consumer Council for Water (CCW), local authorities, health authorities, emergency services, other organisations such as NFU, CBI and trades unions. We recently began publishing our water situation report monthly as part of our ‘open data’ initiative.

If the water resources situation continues during the winter, we will deliver a “winter campaign”. Customer water use is lower during winter months compared to summer. However, we can still experience peaks in demand due to leaking pipes, which freeze in the cold weather then burst when temperatures increase again. Our winter campaign will look to provide advice to customers on how to protect their home when temperatures drop, which will reduce the risk of pipes leaking or bursting.

The winter campaign will focus on raising awareness of the key messages across Yorkshire through media relations, stakeholder relations and bought on and offline media, including digital advertising, radio and potentially print. The advertising will be geo-targeted to relevant areas, and we will have the ability to upscale activity should the weather take a turn for the worse. As part of the campaign, we will offer a limited number of free items to customers, such as outdoor tap covers, which will be available to order via our website.

Alongside our campaign, we will be promoting our Priority Services Register to ensure we know about customers who need an extra bit of help. Media activity and campaign messaging will be targeted on the relevant channels to have maximum impact.

We will continually monitor the situation, making decisions about applying for winter drought permits or whether we need further spring/summer permits in line with our Drought Plan.

Should a severe shortage of rainfall continue this year, it is possible that permit applications beyond those listed in Table 6.1 will be required. The decision to apply for additional permits will depend on reservoir stocks and forecasts, which we will be monitoring closely.

# Operational changes we will make to avoid future drought-related problems

Our Drought Plan includes long term options that we will consider if the drought continues into 2023. These options will provide additional resources for public supply and will only be implemented if there is a risk that our current available resources will not be able to meet demand if the drought continues.

The decision to implement long term options will be dependent on the severity of the situation and scenario modelling to assess the potential risk. The trigger in our drought plan is to review the need for long term options if we are six weeks away from our regional drought control line in the second year of a drought. We are currently reviewing the scope of the long-term options and the timescales for delivery. If we were approaching the trigger for implementing long term options, this information will help determine which long-term options we should implement if required.

In line with our drought planning process, once the situation recovers, we will carry out a full review of our drought triggers and actions and their impacts. We will produce a “lessons learnt report” within six months of the situation returning to normal. This will include a review of operations and any opportunities to operate differently to improve our resilience to future droughts. For example, we will review drought triggers and reservoir control lines incorporating 2022 data. If this review leads to material changes to our current Drought Plan, it will be revised and resubmitted to Defra.

# Notices and advertisements relation to application

Written notice of the North West Area Drought Permit applications will be sent to third parties with an interest in the sites. These include;

Local authorities responsible for areas affected by the permit;

Embsay and Grimwith Reservoirs are within Craven Distict Council Local Authority.

Silsden, Reva, Weecher, Eldwick, Hewenden, Doe Park, Leeming, and Leeshaw Reservoirs are within Bradford City Council Local Authority.

Other abstractors operating in the areas affected by the permit.

Local rivers trusts and wildlife groups.

Local angling clubs in the areas affected by the permits if granted.

Local wildlife sites – predominantly owned by Sheffield Local Authority and Barnsley Local Authority.

Fish farms in the area affected by the permits if granted.

The notice provides information on where the full application can be inspected free of charge for a period of eight days from the date the notice is served. A copy of the notice is provided in Appendix 2.

The notice will be advertised on 15th September 2022 in the Bradford Telegraph & Argus, Ilkley Gazette, and Wharedale Observer, which are circulated in the area potentially affected if the permit is granted, and in the London Gazette, in accordance with Environment Agency guidance. If the application is successful, we will provide notice the permit has been granted in the same newspapers.

A Yorkshire Water webpage has been created to provide information on drought permit applications, including copies of all supporting documents. Further permit application notices will be added on the dates we apply. The webpage includes information to explain why we are making the applications and a list of frequently asked questions.

# Public inspection arrangements

Documents relating to the North West Area drought permit applications have been made available, free of charge, for inspection by any interested parties from the date the notices are advertised in the Bradford Telegraph & Argus, Ilkley Gazette and Wharfedale Observer, and the London Gazette. The documents include a copy of the drought permit application and supporting information including environmental reports and were made available at the following locations for eight days staring on [DATE]:

Yorkshire Water, Western House, Halifax Road, Bradford, BD6 2SZ.

Environment Agency, Lateral, 8 City Walk, Leeds, LS11 9AT.

Haworth Post Office, 98 Main Street, Haworth, Keighley, BD22 8DP. (Leeming reservoir, Leeshaw Reservoir, Springhead Weir)

Denholme Post Office, 54 Main Road, Denholme, Bradford, BD13 4BL. (Doe Park Reservoir, Hewenden Reservoir)

Eldwick Post Office, 90 Otley Road, Eldwick, Bingley, BD16 3EE. (Eldwick Reservoir, Weecher Reservoir)

Menston Post Office, 52 Cleasby Road, Menston, Ilkley, LS29 6JA. (Reva Reservoir, Carr Bottom Reservoir)

Silsden Post Office, 39 Kirkgate, Silsden, Keighley, BD20 0AJ. (Silsden Reservoir)

Skipton Post Office, 11 Swadford Street, Skipton, BD23 1RD. (Embsay Reservoir)

Grassington Post Office, 15 Main Street, Grassington, Skipton, BD23 5AD (Grimwith Reservoir)

The post offices selected are within eight kilometres of the reservoirs impacted by the drought permit applications, named in brackets. The supporting documents are available at the Yorkshire Water Head Office in Bradford. The Environment Agency guidelines state drought permits must be advertised at the water company’s head office and the office most local to the relevant area. We have a number of water treatment works nearby the permit application sites however, they are not suitable for public access, and we are therefore only able to provide the information at our head office in Bradford, which can be accessed by the public.

# Environment Agency

We initiated the formal dry-weather governance meetings with our local Environment Agency in May following reservoirs stocks crossing the Environment Agency early warning trigger line. We have continued to consult and engage weekly with the Environment Agency on the drought situation as it has escalated. We will continue to meet regularly until the situation recovers.

# Natural England

Natural England were consulted throughout the process of writing our Drought Plan 2022 and we have notified them of our intention to submit drought permit applications for the late summer of 2022. If there is potential for a proposed drought permit to impact on a designated area, we are required to consult Natural England prior to submitting the application. The environmental assessment of these drought options confirmed there would be no impacts on any designated sites by any of the drought options in the North West area. The results of the assessment can be found in the accompanying EAR.

# Local rivers trusts and wildlife trusts

The environmental assessment of these drought options confirmed there would be no impacts on any Local Wildlife Sites by any of the drought options in the North West area. The results of the assessment can be found in the accompanying EAR.

# Navigation Authority

We do not require navigation authority’s consent for most of the North West Area drought permit applications. The only consent required is in relation to the Embsay Reservoir Drought Permit which, if implemented, would result in a reduction in compensation flows into Embsay Beck and consequently Eller Beck which feeds the Leeds and Liverpool Canal at Skipton. The Canal and Rivers Trust (CRT) has confirmed that they are happy for us to apply for the Embsay Reservoir Drought Permit. A copy of their email confirmation is included with this application.

# Internal Drainage Board

We will have notified the relevant Internal Drainage Boards of our intention to submit drought permit applications.

# Retailers

Since retail separation in April 2017 commercial water users are now customers of retail companies. The Yorkshire Water Non-Household Management Team will ensure retailers operating in the Yorkshire Water supply area are notified of the permit applications in advance of public notices being published in newspapers.  Notification will be provided by email and will include a copy of the frequently asked questions. We will highlight to the retailers that the drought permits we are applying for will not impact on customers’ supplies and we are providing the information in case they get any calls or queries from their non-household customers. We will also provide retailers with contact details for raising questions relating to the permits.

# Appendices

# Appendix 1: Summary of water saving communications

The table below summarises the communication activity we have carried out to raise awareness of the dry weather situation and encourage demand reduction.

| Water Saving Customer Communications |  | W/C 20th June | W/C 27th June | W/C 4th July | W/C 11th July | W/C 18th July | W/C 25th July | W/C 1st August | W/C 8th August | W/C 15th August |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| MEDIUM | PLATFORM | REACH / IMPRESSIONS | REACH / IMPRESSIONS | REACH / IMPRESSIONS | REACH / IMPRESSIONS | REACH / IMPRESSIONS | REACH / IMPRESSIONS | REACH / IMPRESSIONS | REACH / IMPRESSIONS | REACH / IMPRESSIONS |
| ONLINE | Facebook ‘paid for’ Adverts | Impressions: 1,406,328 | Impressions: 895,032 | Impressions: 1,144,058 | Impressions: 1,021,400 | Impressions 1,261,645 | Impressions: 1,354,586 | Impressions 1,552,557 | Impressions TBC | Impressions TBC |
|  | Programmatic/ Digital Display Advertising | Impressions: 271,828 | Impressions: 252,118 | Impressions: 503,115 | Impressions: 1,212,554 | Impressions: 714,940 | Impressions: 478,719 | Impressions: 505,055 | Impressions: TBC | Impressions: TBC |
| RADIO ADS | Traditional Radio | Impressions: 3,234,500 | Impressions: 3,234,500 | Impressions: 4,737,500 | Impressions: 4,737,500 | Impressions: 4,737,500 | Impressions: 4,737,500 | Impressions: 3,182,395 | Impressions: 3,931,375 | Impressions: 3,931,375 |
|  | Digital Audio ‘Instream’ | Impressions: 130,000 | Impressions: 130,000 | Impressions: 312,500 | Impressions: 312,500 | Impressions: 312,500 | Impressions: 312,500 | Impressions: 312,500 | Impressions: 312,500 | Impressions: 312,500 |
| LOCAL NEWSP-APERS | Metro Yorkshire | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 98,889 | 98,889 |
|  | Yorkshire Post | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 49,229 | 49,229 |
| OUT-DOOR | Digital 6 Sheet Bus | Impressions: 9,260 N/A | Impressions: 41,372 N/A | Impressions: 120,064 N/A | Impressions: 116,284 N/A | Impressions: 44,839 N/A | Impressions: 67,877 Impressions: 1,083,333 | Impressions: 145,967 Impressions: 1,083,333 | TBC Impressions: 1,083,333 | TBC TBC |
| TV / YouTube | All 4 Sky Go YouTube | N/A N/A N/A | N/A N/A N/A | N/A N/A N/A | N/A N/A N/A | N/A N/A N/A | Impressions: 52,102 Impressions: 43,215 Impressions: 55,138 | Impressions: 52,102 Impressions: 43,215 Impressions: 80,856 | Impressions: 122,237 Impressions: 47,907 Impressions: 47,907 | TBC TBC TBC |
| MEDIA | Media reach | Reach: 407,112 | Reach: 8,169 | Reach: 20,650,458 | Reach: 370,117,387 | Reach: 80,600,000 | Reach: 19,300,000 | Reach: 104,000,000 | Reach: 1,100,000,000 | TBC |
| IN HOUSE | Customer Emails | N/A | N/A | N/A | N/A | Impressions: 29,755 | N/A | N/A | N/A | Impressions: 51,000 |
|  | YW Website: Save water page | Hits: 815 | Hits: 678 | Hits: 794 | Hits: 1,802 | Hits: 2,612 | Hits: 1,515 | Hits: 2,465 | Hits: 4,103 | Hits: TBC |
|  | YW Website: Hosepipe page | Hits: 25 | Hits: 11 | Hits: 70 | Hits: 657 | Hits: 761 | Hits: 422 | Hits: 2,858 | Hits: 38,431 | Hits: TBC |
|  | Organic Social Channels: Facebook, Instagram & Twitter | Reach: 19,982 | Reach: 16,628 | Reach: 33,758 | Reach: 45,070 | Reach: 75,688 | Reach: 42,000 | Reach: 41,846 | Reach: 47,452 | Reach: TBC |

Samples of creative used during the campaign are provided below

# Appendix 2: Notice relating to the North West reservoir group drought permit application

YORKSHIRE WATER SERVICES LIMITED

NOTICE OF APPLICATION FOR DROUGHT PERMITS

North West Area Catchments

TAKE NOTICE that due to the threat of a serious water shortage in the Yorkshire area caused by an exceptional shortage of rain, YORKSHIRE WATER SERVICES LIMITED (company number 02366682) whose registered office is at Western House, Halifax Road, Bradford, BD6 2SZ is applying to the Environment Agency for [twelve] drought permits in the North West Area catchment under section 79a of the Water Resources Act 1991 (as amended).

The drought permits are intended to apply until 31st March 2023 inclusive and propose to reduce the compensation releases from reservoirs in the Wharfe, Aire, and Worth river valleys.

Leeming Reservoir (SE 03 34)

Yorkshire Water releases water from Leeming Reservoir under conditions defined by the Leeming Reservoir impoundment licence (NE/027/0014/010) to compensate the downstream receiving watercourse, Leeming Water. The volume released is dependent on the stock levels in Leeming Reservoir and in Leeshaw Reservoir, which is operated under the terms of the Leeshaw Reservoir impoundment licence (NE/027/0014/011). Under the Leeming Reservoir impoundment licence conditions, not less than 4.00 megalitres per a day (Ml/d) must be continuously discharged when Leeming reservoir level is either above or below the control lines and Leeshaw reservoir level is above the control lines defined in the respective licences, or 5.250 Ml/d when the Leeming reservoir level is above its control line and Leeshaw reservoir level is below its control line, or 3.250 Ml/d when both the Leeshaw and Leeming reservoir levels are below their control lines.

The drought permit application for Leeming Reservoir is to reduce the compensation release required when Leeming reservoir level is above or below the control line and Leeshaw reservoir level is above the control line to 2.00 Ml/d, to reduce the compensation release when Leeming reservoir level is above the control line and Leeshaw reservoir level is below the control line to 2.63 Ml/d and to reduce further when the reservoirs are both below the control lines to 1.625 Ml/d. There would then be a further reduction to 1.33 Ml/d when Leeming reservoir level is above or below the control line and Leeshaw reservoir level is above the control line, and to 1.75 Ml/d when the Leeming reservoir level is above or below the control line and Leeshaw reservoir level is below the control line or 1.083 Ml/d when both the Leeshaw and Leeming reservoir levels are below the control lines, if regional reservoir stocks were below the regional Drought Control Line for four consecutive weeks or more, as defined in the Yorkshire Water Drought Plan.

Leeshaw Reservoir (SE 01 35)

Yorkshire Water releases water from Leeshaw Reservoir under conditions defined by the Leeshaw Reservoir impoundment licence (NE/027/0014/011) to compensate the downstream receiving watercourse, Dunkirk Beck. Under the licence conditions, we must continuously discharge not less than 4.00 Ml/d when the reservoir level is above the control line defined in the licence, or 2.750 Ml/d when the reservoir level is below the control line.

The drought permit application for Leeshaw Reservoir is to reduce the compensation release required when the reservoir stocks are above the control line to 2.00 Ml/d, or when the reservoir stocks are below the control line to 1.375 Ml/d. There would then be a further reduction to 1.33Ml/d when the reservoir level is above the control line or 0.92 Ml/d if below the reservoir control line, if regional reservoir stocks were below the regional Drought Control Line for four consecutive weeks or more, as defined in the Yorkshire Water Drought Plan.

Springhead Weir Maintained Flow (SE 02 37)

Yorkshire Water is licensed to abstract water from Ponden Reservoir for supply to customers under the terms of abstraction licence number 2/27/14/058 (the “Ponden licence”). The terms of the Ponden licence state Yorkshire Water must release flow from Ponden Reservoir to compensate the downstream receiving watercourse, the River Worth. Yorkshire Water is licensed to abstract water from Lower Laithe Reservoir for supply to customers under the terms of abstraction licence number 2/27/14/009 (the “Lower Laithe licence”). The terms of the Lower Laithe licence state Yorkshire Water must release flow from Lower Laithe Reservoir to compensate the downstream receiving watercourse, Sladen Beck. Under the terms of both Ponden and Lower Laithe licence conditions, Yorkshire Water must ensure the flow of water at Springhead Weir, which is below the confluence of the two watercourses, shall not fall below 6.00 Ml/d, when the combined compensation flow from Leeming and Leeshaw reservoirs is 8.00 Ml/d, or 8.00 Ml/d when the combined compensation flow from Leeming and Leeshaw reservoirs reduces to 6.00 Ml/d.

The drought permit application for the Springhead Weir Maintained Flow is to reduce the maintained flow at Springhead Weir when regional stocks are at or approaching the drought control line. The maintained flow would reduce to 3.00 Ml/d if either Leeshaw and Leeming reservoirs are above the control lines and to 4.00 Ml/d if both Leeshaw and Leeming are below the control lines. There would then be a further reduction further to 2.00 Ml/d if either Leeshaw and Leeming reservoirs are above the control lines and to 2.67 Ml/d if both Leeshaw or Leeming are below the control lines, if regional reservoir stocks are below the regional Drought Control Line for four consecutive weeks or more, as defined in the Yorkshire Water Drought Plan.

Doe Park Reservoir (SE 07 34)

Under the terms of abstraction licence NE/027/0016/021, we must release water from Doe Park Reservoir to compensate the downstream water course. The licence states that we must release flow from Doe Park Reservoir to the Denholme Beck so as to maintain a flow of no less than 3.6 Ml/d in Denholme Beck.

The drought permit application for Doe Park Reservoir is to provide a release of 1.8 Ml/d at all stock levels, which could be reduced to 1.2 Ml/d if regional reservoir stocks were below the regional Drought Control Line for four consecutive weeks or more, as defined in the Yorkshire Water Drought Plan.

Hewenden Reservoir (SE 07 35)

Under the terms of the Bradford Waterworks Act 1854, Yorkshire Water must release water from Hewenden Reservoir to compensate the downstream water course, the Hewenden Beck. The Act states Yorkshire Water must release flow from Hewenden Reservoir at mill owners’ discretion. Yorkshire Water currently operates the compensation flow under the terms of a flow trial agreement held with the Environment Agency, whereby a continuous discharge is made of not less than 6.30 Ml/d.

The drought permit application for Hewenden Reservoir is to provide a continuous release of 3.15 Ml/d, which could be reduced to 2.10 Ml/d if regional reservoir stocks were below the regional Drought Control Line for four consecutive weeks or more, as defined in the Yorkshire Water Drought Plan.

Eldwick Reservoir (SE 12 41)

Under the terms of Shipley Waterworks and Police Act 1854, Yorkshire Water must release water from Eldwick Reservoir to compensate the downstream water course, the Eldwick Beck. The Act states Yorkshire Water must release two fifths of the average daily inflow to the reservoir between 05:00 hours and 20:00 hours every day (barring Sunday, Christmas Day, and Good Friday). Yorkshire Water currently operates the compensation flow under the terms of a flow trial agreement held with the Environment Agency, whereby we continuously discharge not less than 1.00 Ml/d.

The drought permit application for Eldwick Reservoir is to provide a compensation continuous release of 0.50 Ml/d, which could be reduced to 0.33 Ml/d if regional reservoir stocks were below the regional Drought Control Line for four consecutive weeks or more, as defined in the Yorkshire Water Drought Plan.

Reva Reservoir (SE 15 42)

Yorkshire Water is licensed to abstract water from Reva Reservoir for supply to customers under the Yeadon Waterworks Act 1916. The terms of the Act state Yorkshire Water must release not less than 0.791 Ml/d (174,000 gallons per day) to compensate the downstream water course, the Hawksworth Beck.

The drought permit application for Reva reservoir is to reduce the compensation release required to 0.396 Ml/d. There would be a further reduction to 0.264 Ml/d if regional reservoir stocks were below the regional Drought Control Line for four consecutive weeks or more, as defined in the Yorkshire Water Drought Plan.

Weecher Reservoir (SE 13 42)

Yorkshire Water is licensed to abstract water from Weecher Reservoir for supply to customers under the Baildon Local Water Act 1890. The terms of the Act state Yorkshire Water must release not less than 110,273 gallons (0.501 Ml) per a working day Monday to Saturday to compensate the downstream water course, the Weecher Brow Beck. Yorkshire Water currently operates the compensation release under an agreement held with the Environment Agency to discharge 0.43 Ml/d.

The drought permit application for Weecher Reservoir is to reduce the compensation release required to 0.215 Ml/d. There would be a further reduction to 0.143 Ml/d if regional reservoir stocks were below the regional Drought Control Line for four consecutive weeks or more, as defined in the Yorkshire Water Drought Plan.

Silsden Reservoir (SE 04 47)

Yorkshire Water is licensed to abstract water from Silsden Reservoir for supply to customers under abstraction licence number 2/27/15/149. The terms of the licence include a prescribed flow condition of 2.409 Ml/d to be discharged to Silsden Beck, whereby no water can be abstracted if the flow exiting the reservoir is below this level.

The drought permit application is to reduce the Silsden Reservoir prescribed flow requirement to 1.20 Ml/d. There would be a further reduction to 0.80 Ml/d if regional reservoir stocks were below the regional Drought Control Line for four consecutive weeks or more, as defined in the Yorkshire Water Drought Plan.

Embsay Reservoir (SD 99 54)

Yorkshire Water is licensed to abstract water from Embsay Reservoir for supply to customers under the Skipton Water and Improvement Act 1904 and abstraction licence number 2/27/15/45 (the “Embsay licence”). The terms of the Act state that Yorkshire Water must release not less than 1.186 Ml/d (261,000 gallons per day) to compensate the downstream water course, the Embsay Beck. The Embsay licence states a flow of not less than 0.273 Ml/d (60,000 gallons per day) must remain in Mill Beck, immediately downstream of the abstraction point, when abstraction takes place.

The drought permit application for Embsay Reservoir is to reduce the compensation release required to 0.593 Ml/d. There would be a further reduction to 0.395 Ml/d if regional reservoir stocks were below the regional Drought Control Line for four consecutive weeks or more, as defined in the Yorkshire Water Drought Plan. All releases would be greater than 0.273 Ml/d, therefore consistent with the Embsay licence condition.

Grimwith Reservoir (SE 06 64)

Under the terms of licence (NE/027/0019/011) Yorkshire Water must release flow from Grimwith Reservoir to compensate the downstream water course, the River Dibb, a tributary to the River Wharfe. The volume released changes throughout the year. From 1st January to 19th April we must release no less than 15.1 Ml/d; from 20th April to 10th May no less than 7.9 Ml/d; from 11th May to 11th October no less than 3.8 Ml/d; from 12th to 31st October no less than 7.8 Ml/d; from 1st November to 31st December no less than 15.1 Ml/d.

The drought permit application for Grimwith Reservoir is to reduce the compensation release requirement to: 7.55 Ml/d from 1st January to 19th April; 3.90 Ml/d from 20th April to the 10th May; 1.90 Ml/d from 11th May to 11th October; 3.90 Ml/d from 12th to 31st October; 7.55 Ml/d from 1st November to 31st December. There would be a further reduction to: 5.03 Ml/d Ml/d from 1st January to 19th April; 2.60 Ml/d from 20th April to the 10th May; 1.27 Ml/d from 11th May to 11th October; 2.60 Ml/d from 12th to 31st October; 5.03 Ml/d from 1st November to 31st December if regional reservoir stocks were below the regional Drought Control Line for four consecutive weeks or more, as defined in the Yorkshire Water Drought Plan.

Carr Bottom Reservoir (SE 15 45)

Yorkshire Water is licensed to impound water at Carr Bottom Reservoir for supply to customers under the Burley-in-Wharfedale Water Act 1899. The terms of the Act state that no less than 0.085 Ml/d (18,600 gallons per day) must be released into the downstream watercourse, the Carr Beck. The drought permit application for Carr Bottom Reservoir is to reduce the compensation release required to 0.0425 Ml/d. There would be a further reduction to 0.028 Ml/d if regional reservoir stocks were below the regional Drought Control Line for four consecutive weeks or more, as defined in the Yorkshire Water Drought Plan.

The anticipated effect of the proposed drought permits, if granted, will be to reduce the rate of draw down on reservoirs in the Wharfe, Aire and Worth Valley area catchments This will aid winter refill and conserve stocks for public water supply. It will result in a reduction in flow in the downstream receiving watercourses. However, it will mean compensation flow from the reservoirs to the watercourses can be provided for longer than if the compensation releases continued at the current rates.

Yorkshire Water, in consultation with the Environment Agency, has carried out an assessment of the potential environmental impacts resulting from each of the drought permits. This includes an environmental monitoring plan and mitigation measures to reduce the impacts on the downstream ecology.

Anyone may inspect the proposals at the following locations, free of charge, during normal working hours for a period of seven days from the publication of this notice:

- Yorkshire Water, Western House, Halifax Road, Bradford, BD6 2SZ.

- Environment Agency, Lateral, 8 City Walk, Leeds, LS11 9AT. By appointment, telephone 03708 506 506.

- Haworth Post Office, 98 Main Street, Haworth, Keighley, BD22 8DP.
Open 9:00-17:30 Monday to Friday. 9:00-12:30 Saturday. Closed Sunday.

- Denholme Post Office, 54 Main Road, Denholme, Bradford, BD13 4BL. 
Open 9:00-13:00 and 14:-17:30 Mon, Tues, Thurs, and Fri. 9:00-12:00 Wednesday. 9:00-12:00 Saturday. Closed Sunday.

- Eldwick Post Office, 90 Otley Road, Eldwick, Bingley, BD16 3EE. 
Open 9:00-17:30 Monday-Firday. 9:00-12:30 Saturday. Closed Sunday.

- Menston Post Office, 52 Cleasby Road, Menston, Ilkley, LS29 6JA. 
Open 7:00-20:00 Monday to Saturday. 7:00-19:00 Sunday.

- Silsden Post Office, 39 Kirkgate, Silsden, Keighley, BD20 0AJ. 
Open 6:00-17:30 Monday to Friday. 6:00-14:00 Saturday. 5:30-11:30 Sunday.

- Skipton Post Office, 11 Swadford Street, Skipton, BD23 1RD. 
Open 9:00-17:30 Monday to Saturday. Closed on Sunday.

- Grassington Post Office, 15 Main Street, Grassington, Skipton, BD23 5AD
Open 10:00-17:00 Monday to Sunday.

- Copies of the proposals are also available to view on the Yorkshire Water website https://www.yorkshirewater.com/drought-permits

Objections may be made in writing to the Environment Agency at:

Water Resources Permitting Support Centre, Environment Agency, Quadrant 2, 99 Parkway Avenue, Parkway Business Park, Sheffield, S9 4WF or psc-waterresources@environment-agency.gov.uk

Objections should be made immediately and in any event by 5pm on 22nd September 2022. Objectors may send a copy of their objection to the address below.

Objectors may also send a copy of their objection to:

Western House, Halifax Road, Bradford, BD6 2SZ or publicaffairs@yorkshirewater.co.uk.

Dated: 	15th September 2022

Signed:	Neil Dewis	Perminder Kaur

Director of Water Service Delivery	Head of Legal Services

Yorkshire Water, Western House, Halifax Road, Bradford, BD6 2SZ